## Disclaimer
TasNetworks – Annual Planning Report 2024 – Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2024.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Overview
Updates to APR Substation Capacity and Maximum Demand Forecasts | Tx-Dx connection points | Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Appendix A.3.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix C of this APR.
T-D as well as Zone data have been split into data and info sheets. This allows a more clean and user friendly experience with data on one sheet and all supporting and/or linked information in another.
Both T-D and Zone data tabs now have been automated using VBA Macros (see VBA Codes). This addition reduces risk of human error and/or using a multitude of individual links. It fully automates the calculation of raw forecast data into usable data for graphs.
All offset formulas have been removed and replaced as they are difficult to trace back to raw data and do not minimise human risk of errors.
| Distribution line max. demand |  | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Appendix A.3.2 of this APR.
ForecastData
raw forecast data
(Updated annually)
FORECAST
Automatically re-formats from ForecastData sheet
T-D
Zone
T-D Data
Uses VBA macros to automatically calculate formulas
T-D Info
Supporting T-D information and data which has been referenced and linked to
Zone Data
Uses VBA macros to automatically calculate formulas
Zone info
Supporting Zone information and data which has been referenced and linked to
Substation DER
Raw Sub DER data
(Updated annually)
DERdataMax
Raw Maxiumum Sub DER data
(Updated annually)
Feeder DER
Raw Feeder DER data
(Updated annually)
Tx-Dx Connection Points
Connection point summary and forecast graphs
Zone subs & sub-trans lines
Zone and sub-trans summary and forecast graphs
Distribution feeder max. demand
Feeder max demand for Summer and Winter
VBA Macros
Main Output #1
Main Output #2
Main Output #3
VBA MACROS

## Assumptions + methodology
Tx-Dx connection points | Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Appendix A.3.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix C of this APR.
Distribution line max. demand |  | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Appendix A.3.2 of this APR.
Updated 3 December 2024

## ForecastData (hidden)
Ref. Embedded Generation NMIs 230621.xlsx in 2021 APR Chapter 4 folder, http://collaborationzone.tnad.tasnetworks.com.au/business-functions/network-planning/APR15/Annual%20Planning%20Report%20Creation/Chapter%204%20-%20Area%20planning
|  |  |  | Summer (MVA) | [13 empty] | Winter (MVA) | [14 empty] | Embedded generation
|  |  | Non-peaking season | 2021 (Actual) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | PF | Regional DF | 2021 (Actuals) | 2022 (Actuals) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | PF | Regional DF |  | less than 100 kVA | Over 100 kVA
TRUE | AL | Arthurs Lake (DL) | Summer | 0.52501 | 0.54367 | 0.54367 | 0.55195 | 0.57158 | 0.58532 | 0.58831 | 0.59143 | 0.59612 | 0.61509 | 0.65457 | 0.69408 | 0.98881 | 0.80435 | 0.022543 | 0.2009 | 0.2009 | 0.20715 | 0.2112 | 0.21504 | 0.21642 | 0.21811 | 0.22053 | 0.22493 | 0.23601 | 0.24605 | 0.66721 | 0.5974 | TR | 20.6073 | 2
TRUE | AV | Avoca | Summer | 13.2985 | 10.5902 | 10.5902 | 10.7515 | 11.1337 | 11.4015 | 11.4597 | 11.5205 | 11.6119 | 11.9814 | 12.7503 | 13.52 | 0.98493 | 0.43165 | 8.2335 | 6.4502 | 6.4502 | 6.6511 | 6.781 | 6.9043 | 6.9487 | 7.003 | 7.0805 | 7.222 | 7.5776 | 7.9 | 1 | 0.73008 | GT | 7.5015 | 0.30292
TRUE | BEZ | Zs-Bellerive | Summer | 7.558 | 9.8484 | 9.8484 | 9.9984 | 10.3539 | 10.6029 | 10.657 | 10.7135 | 10.7986 | 11.1421 | 11.8572 | 12.573 | 0.99994 |  | 10.3203 | 10.5204 | 10.5204 | 10.8481 | 11.0599 | 11.2609 | 11.3334 | 11.4219 | 11.5483 | 11.7792 | 12.3591 | 12.885 | 0.99982 |  | SH | 1.1198 | 0
TRUE | BU | Burnie | Summer | 41.8144 | 43.7936 | 44.4027 | 44.4606 | 46.0414 | 47.1486 | 47.3891 | 47.6406 | 48.0188 | 49.5466 | 52.7264 | 55.9091 | 0.99845 | 0.93437 | 58.1268 | 59.8407 | 60.3765 | 61.7047 | 62.9095 | 64.0533 | 64.4652 | 64.9687 | 65.6878 | 67.0009 | 70.2998 | 73.2909 | 0.99835 | 0.92899 | TU | 0.0657 | 0
TRUE | BW | Bridgewater | Summer | 19.096 | 24.486 | 24.3338 | 24.828 | 24.9425 | 25.5422 | 25.6726 | 25.8088 | 26.0137 | 26.8414 | 28.564 | 30.2882 | 0.99985 | 0.86038 | 34.895 | 35.4617 | 35.3278 | 36.5387 | 36.5763 | 37.2413 | 37.4808 | 37.7735 | 38.1916 | 38.9551 | 40.8731 | 42.6121 | 0.99976 | 0.93665 | DP | 11.2123 | 0.95333
TRUE | CAZ | Cambridge-Total | Summer | 12.5347 | 16.3127 | 16.3127 | 16.5611 | 17.15 | 17.5624 | 17.652 | 17.7457 | 17.8865 | 18.4556 | 19.6401 | 20.8256 | 0.98311 |  | 16.9885 | 18.8922 | 18.8922 | 19.4807 | 19.8611 | 20.2221 | 20.3522 | 20.5112 | 20.7382 | 21.1527 | 22.1942 | 23.1385 | 0.99488 |  | WA | 0 | 0
TRUE | CLZ | Zs-Claremont | Summer | 12.6915 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 | 0.99857 |  | 22.118 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 | 0.99941
TRUE | CR | Creek Road | Summer | 51.9611 | 64.5253 | 66.6569 | 65.5081 | 67.8372 | 69.4685 | 69.8229 | 70.1935 | 70.7507 | 73.0018 | 77.6869 | 82.3763 | 0.99501 | 0.8873 | 89.0875 | 92.548 | 94.423 | 95.4308 | 97.2941 | 99.063 | 99.7001 | 100.4788 | 101.591 | 103.6217 | 108.7237 | 113.3496 | 0.99089 | 0.9452 | AL | 0.36324 | 1.6
TRUE | CS | Chapel Street | Summer | 20.2013 | 24.2412 | 24.2412 | 24.6104 | 25.4854 | 26.0983 | 26.2314 | 26.3706 | 26.58 | 27.4257 | 29.1858 | 30.9475 | 0.99997 | 0.92902 | 38.759 | 40.3611 | 40.3611 | 41.6183 | 42.4309 | 43.2024 | 43.4802 | 43.8198 | 44.3048 | 45.1905 | 47.4155 | 49.4329 | 0.99999 | 0.90185
TRUE | DB | Derwent Bridge | Summer | 0.28717 | 0.33268 | 0.33268 | 0.33774 | 0.34975 | 0.35816 | 0.35999 | 0.3619 | 0.36477 | 0.37638 | 0.40053 | 0.42471 | 0.98969 | 0.76923 | 0.33494 | 0.33628 | 0.33628 | 0.34676 | 0.35353 | 0.35996 | 0.36227 | 0.3651 | 0.36914 | 0.37652 | 0.39506 | 0.41187 | 1 | 0.71875 | DB | 0 | 0
TRUE | DE | Derby | Winter | 7.8275 | 6.8909 | 6.8909 | 6.9959 | 7.2446 | 7.4188 | 7.4567 | 7.4963 | 7.5558 | 7.7962 | 8.2965 | 8.7973 | 0.99287 | 0.71111 | 7.0036 | 5.8108 | 5.8108 | 5.9918 | 6.1088 | 6.2198 | 6.2598 | 6.3087 | 6.3786 | 6.5061 | 6.8264 | 7.1169 | 0.96015 | 0.32805 | KR | 6.9122 | 0.1992
TRUE | DP | Devonport | Summer | 36.0101 | 36.5976 | 36.9782 | 41.0194 | 37.6757 | 38.5816 | 38.7785 | 38.9843 | 39.2938 | 40.544 | 43.146 | 45.7504 | 0.99065 | 0.86328 | 52.515 | 53.2265 | 53.5613 | 58.337 | 55.2521 | 56.2566 | 56.6184 | 57.0607 | 57.6922 | 58.8455 | 61.7428 | 64.3698 | 0.99697 | 0.95374 | HR | 0.01525 | 0
TRUE | DPZ | Zs-Derwent Park | Summer | 12.9504 | 18.1439 | 18.1439 | 18.4202 | 19.0752 | 19.5339 | 19.6335 | 19.7377 | 19.8944 | 20.5274 | 21.8448 | 23.1634 | 0.97772 |  | 19.1852 | 18.729 | 18.729 | 19.3124 | 19.6894 | 20.0474 | 20.1763 | 20.3339 | 20.559 | 20.97 | 22.0025 | 22.9386 | 0.98066
TRUE | EB | Emu Bay (RT) | Summer | 7.8282 | 7.6238 | 7.6238 | 7.7399 | 8.0151 | 8.2078 | 8.2497 | 8.2935 | 8.3593 | 8.6253 | 9.1789 | 9.7329 | 0.96247 | 0.76111 | 9.0691 | 8.8576 | 8.8576 | 9.1335 | 9.3118 | 9.4811 | 9.5421 | 9.6166 | 9.7231 | 9.9174 | 10.4057 | 10.8484 | 0.97442 | 0.8838 | UL | 10.809 | 8.805
TRUE | EHZ | Zs-East Hobart | Summer | 23.8662 | 26.0751 | 26.0751 | 26.4722 | 27.4134 | 28.0726 | 28.2159 | 28.3656 | 28.5908 | 29.5005 | 31.3937 | 33.2888 | 0.97267 |  | 29.2574 | 27.121 | 27.121 | 27.9658 | 28.5118 | 29.0302 | 29.2169 | 29.4451 | 29.771 | 30.3662 | 31.8613 | 33.2169 | 0.97304
TRUE | EL | Electrona | Summer | 10.0694 | 12.3126 | 12.3126 | 12.5001 | 12.9446 | 13.2558 | 13.3235 | 13.3942 | 13.5005 | 13.9301 | 14.8241 | 15.7189 | 0.99951 | 0.78257 | 16.2935 | 16.2531 | 16.2531 | 16.7594 | 17.0866 | 17.3972 | 17.5091 | 17.6459 | 17.8412 | 18.1978 | 19.0938 | 19.9062 | 0.99914 | 0.88141 | NT | 0 | 0
TRUE | GBZ | Zs-Geilston Bay | Summer | 10.354 | 18.3822 | 18.3822 | 18.6622 | 19.3257 | 19.7904 | 19.8914 | 19.997 | 20.1557 | 20.797 | 22.1317 | 23.4677 | 0.99983 |  | 19.0827 | 18.8139 | 18.8139 | 19.4 | 19.7787 | 20.1383 | 20.2678 | 20.4262 | 20.6522 | 21.0651 | 22.1022 | 23.0426 | 0.9995
TRUE | GRZ | Zs-Gretna | Winter | 1.9864 | 1.0903 | 1.0903 | 1.1069 | 1.1463 | 1.1739 | 1.1799 | 1.1861 | 1.1955 | 1.2336 | 1.3127 | 1.392 | 0.90942 |  | 0.31302 | 0.27031 | 0.27031 | 0.27873 | 0.28417 | 0.28934 | 0.2912 | 0.29347 | 0.29672 | 0.30265 | 0.31756 | 0.33107 | 0.98037
TRUE | GT | George Town | Summer | 12.9473 | 15.7618 | 18.1979 | 14.6107 | 15.1302 | 15.494 | 15.5731 | 15.6557 | 15.78 | 16.282 | 17.327 | 18.3729 | 0.99855 | 0.91086 | 19.5416 | 19.8436 | 21.9865 | 19.2187 | 19.594 | 19.9502 | 20.0785 | 20.2354 | 20.4593 | 20.8683 | 21.8958 | 22.8274 | 0.99895 | 0.77669 | NW | 7.5109 | 0.58708
TRUE | HA | Hadspen | Summer | 40.4237 | 37.995 | 37.386 | 38.7283 | 39.3049 | 40.2501 | 40.4554 | 40.6701 | 40.993 | 42.2973 | 45.0118 | 47.7289 | 0.99865 | 0.93747 | 54.9768 | 55.2719 | 54.7361 | 57.1316 | 57.5431 | 58.5893 | 58.9661 | 59.4267 | 60.0845 | 61.2855 | 64.303 | 67.0389 | 0.99902 | 0.93765 | PM | 1.026 | 0
TRUE | HOZ | Zs-Howrah | Summer | 12.0396 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 | 0.99857 |  | 21.2816 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 | 0.99921
TRUE | HR | Huon River | Winter | 0.55446 | 0.62466 | 0.62466 | 0.63418 | 0.65672 | 0.67252 | 0.67595 | 0.67953 | 0.68493 | 0.70672 | 0.75208 | 0.79748 | 0.55938 | 0.83333 | 0.92276 | 0.57863 | 0.57863 | 0.59665 | 0.6083 | 0.61936 | 0.62334 | 0.62821 | 0.63517 | 0.64786 | 0.67976 | 0.70868 | 0.56163 | 0.81818 | NH | 5.5279 | 0
TRUE | KE | Kermandie | Summer | 6.2488 | 7.0843 | 7.0843 | 7.1922 | 7.4479 | 7.627 | 7.6659 | 7.7066 | 7.7678 | 8.0149 | 8.5293 | 9.0441 | 0.98581 | 0.86854 | 8.6874 | 8.5363 | 8.5363 | 8.8022 | 8.974 | 9.1372 | 9.1959 | 9.2678 | 9.3703 | 9.5576 | 10.0282 | 10.4549 | 0.98708 | 0.91347 | MY | 6.4748 | 2.2
TRUE | KI11 | Kingston 11kV | Summer | 16.2318 | 19.3602 | 19.3602 | 19.655 | 20.3539 | 20.8433 | 20.9497 | 21.0608 | 21.228 | 21.9035 | 23.3092 | 24.7162 | 0.9997 | 0.7452 | 27.5402 | 27.6208 | 27.6208 | 28.4811 | 29.0372 | 29.5651 | 29.7553 | 29.9877 | 30.3196 | 30.9257 | 32.4484 | 33.829 | 0.99979 | 0.9059 | BU | 13.9754 | 4.1353
TRUE | KI33 | Kingston 33kV | Summer | 5.6704 | 7.4365 | 7.4365 | 7.5498 | 7.8182 | 8.0062 | 8.047 | 8.0897 | 8.154 | 8.4134 | 8.9534 | 9.4938 | 0.99992 | 0.85913 | 11.1262 | 11.0615 | 11.0615 | 11.406 | 11.6287 | 11.8401 | 11.9163 | 12.0094 | 12.1423 | 12.385 | 12.9948 | 13.5477 | 0.99724 | 0.94338 | CS | 7.4504 | 1.69
TRUE | KR | Knights Road | Summer | 15.0454 | 15.4095 | 16.3992 | 16.6489 | 17.2409 | 17.6555 | 17.7456 | 17.8397 | 17.9814 | 18.5535 | 19.7442 | 20.936 | 0.98727 | 0.90798 | 20.0543 | 18.7877 | 19.6583 | 20.2706 | 20.6664 | 21.0421 | 21.1775 | 21.3429 | 21.5791 | 22.0105 | 23.0942 | 24.0768 | 0.98922 | 0.96199 | NN | 4.4486 | 0.56
TRUE | LF | Lindisfarne | Summer | 20.1035 | 25.692 | 25.692 | 26.0833 | 27.0106 | 27.6602 | 27.8013 | 27.9488 | 28.1707 | 29.067 | 30.9325 | 32.7997 | 1 | 0.81658 | 35.7593 | 36.1898 | 36.1898 | 37.3171 | 38.0457 | 38.7374 | 38.9866 | 39.2911 | 39.726 | 40.5201 | 42.5152 | 44.3241 | 0.99787 | 0.92622
TRUE | MB | Meadowbank | Winter | 8.3046 | 8.4548 | 8.4548 | 8.5835 | 8.8887 | 9.1025 | 9.1489 | 9.1975 | 9.2705 | 9.5654 | 10.1793 | 10.7938 | 0.95908 | 0.71486 | 4.6221 | 5.236 | 5.236 | 5.399 | 5.5045 | 5.6045 | 5.6406 | 5.6846 | 5.7476 | 5.8625 | 6.1511 | 6.4128 | 1 | 0.69937 | EL | 8.7161 | 0.1298
TRUE | MT | Mornington | Summer | 22.6309 | 29.0785 | 29.0785 | 29.5214 | 30.571 | 31.3061 | 31.4659 | 31.6329 | 31.884 | 32.8984 | 35.0098 | 37.1231 | 0.99982 | 0.82309 | 38.7639 | 41.1453 | 41.1453 | 42.4269 | 43.2553 | 44.0417 | 44.3249 | 44.6711 | 45.1656 | 46.0684 | 48.3367 | 50.3933 | 0.99854 | 0.94757
TRUE | MY | Mowbray | Summer | 22.4062 | 22.0811 | 22.6902 | 22.4174 | 23.2145 | 23.7727 | 23.894 | 24.0208 | 24.2115 | 24.9818 | 26.5851 | 28.1899 | 0.99846 | 0.73585 | 38.721 | 35.3881 | 35.9239 | 36.4904 | 37.2029 | 37.8793 | 38.1229 | 38.4207 | 38.8459 | 39.6225 | 41.5733 | 43.3422 | 0.9944 | 0.93917 | PL | 2.3477 | 0.45
TRUE | NH | North Hobart | Summer | 19.9398 | 25.096 | 25.096 | 25.4782 | 26.3841 | 27.0186 | 27.1564 | 27.3006 | 27.5173 | 28.3928 | 30.215 | 32.0389 | 0.9987 | 0.82122 | 35.6257 | 34.7894 | 34.7894 | 35.873 | 36.5734 | 37.2384 | 37.4779 | 37.7706 | 38.1887 | 38.952 | 40.8699 | 42.6088 | 0.99767 | 0.94864 | AV | 1.2114 | 5
TRUE | NN | New Norfolk | Winter | 14.95 | 13.7569 | 13.7569 | 13.9665 | 14.463 | 14.8108 | 14.8864 | 14.9654 | 15.0842 | 15.5641 | 16.563 | 17.5628 | 0.99134 | 0.89365 | 20.854 | 18.1369 | 18.1369 | 18.7019 | 19.067 | 19.4137 | 19.5385 | 19.6911 | 19.9091 | 20.3071 | 21.3069 | 22.2135 | 0.99676 | 0.85865 | EB | 0.70338 | 0
TRUE | NT | Newton (Henty Goldmine) | Summer | 4.0472 | 4.3959 | 4.3959 | 4.4628 | 4.6215 | 4.7326 | 4.7568 | 4.782 | 4.82 | 4.9733 | 5.2925 | 5.612 | 0.99985 | 0.89037 | 3.8815 | 3.9408 | 3.9408 | 4.0636 | 4.1429 | 4.2182 | 4.2454 | 4.2785 | 4.3259 | 4.4124 | 4.6296 | 4.8266 | 0.99991 | 0.875 | RK | 7.1907 | 0
TRUE | NTZ | Zs-New Town | Summer | 17.1169 | 22.5695 | 22.5695 | 22.9132 | 25.4887 | 26.1016 | 26.2348 | 26.374 | 26.5834 | 27.4292 | 29.1895 | 30.9515 | 0.98946 |  | 22.067 | 21.6125 | 21.6125 | 22.2857 | 24.2697 | 24.7109 | 24.8698 | 25.0641 | 25.3415 | 25.8481 | 27.1207 | 28.2747 | 0.99063
TRUE | NW | Norwood | Summer | 16.7155 | 18.4659 | 18.4659 | 18.7472 | 19.4137 | 19.8806 | 19.982 | 20.088 | 20.2475 | 20.8917 | 22.2325 | 23.5745 | 0.9999 | 0.87602 | 29.396 | 28.5123 | 28.5123 | 29.4004 | 29.9745 | 30.5194 | 30.7157 | 30.9556 | 31.2983 | 31.9239 | 33.4957 | 34.9209 | 0.99986 | 0.90014 | QT | 0.88118 | 0
TRUE | PL | Port Latta (RT) | Winter | 22.6255 | 11.7582 | 12.5195 | 11.9372 | 12.3617 | 12.6589 | 12.7235 | 12.791 | 12.8926 | 13.3028 | 14.1565 | 15.0111 | 0.93701 | 0.6205 | 21.4055 | 6.7645 | 7.4341 | 6.9752 | 7.1114 | 7.2407 | 7.2872 | 7.3442 | 7.4255 | 7.5739 | 7.9468 | 8.2849 | 0.99897 | 0.86096 | MB | 0.91829 | 0.2
TRUE | PM | Palmerston | Winter | 15.0674 | 14.2197 | 14.4481 | 13.1224 | 13.589 | 13.9157 | 13.9867 | 14.061 | 14.1726 | 14.6235 | 15.562 | 16.5014 | 0.94916 | 0.69309 | 7.1856 | 10.2606 | 10.4615 | 9.4064 | 9.59 | 9.7644 | 9.8272 | 9.9039 | 10.0136 | 10.2137 | 10.7166 | 11.1726 | 0.98535 | 0.56731 | GO | 0 | 0
TRUE | QT | Queenstown | Summer | 3.7277 | 5.2756 | 5.2756 | 5.3559 | 5.5464 | 5.6797 | 5.7087 | 5.739 | 5.7846 | 5.9686 | 6.3517 | 6.7351 | 0.99981 | 0.84143 | 6.1594 | 6.0756 | 6.0756 | 6.2649 | 6.3872 | 6.5033 | 6.5451 | 6.5962 | 6.6693 | 6.8026 | 7.1375 | 7.4412 | 0.99994 | 0.88151 | RB22 | 0 | 0
TRUE | RA | Railton | Summer | 50.3439 | 47.0618 | 48.5844 | 47.7786 | 49.4773 | 50.6671 | 50.9256 | 51.1959 | 51.6023 | 53.2441 | 56.6612 | 60.0815 | 0.94147 | 0.76883 | 49.2087 | 46.2414 | 47.5807 | 47.6818 | 48.6128 | 49.4966 | 49.8149 | 50.204 | 50.7597 | 51.7744 | 54.3235 | 56.6349 | 0.98001 | 0.95984 | KE | 3.2869 | 0
TRUE | RB22 | Rosebery 22kV | Winter | 2.2636 | 2.1547 | 2.1547 | 2.1875 | 2.2653 | 2.3197 | 2.3316 | 2.3439 | 2.3626 | 2.4377 | 2.5942 | 2.7508 | 1 | 0.64286 | 5.6267 | 2.3149 | 2.3149 | 2.387 | 2.4336 | 2.4778 | 2.4938 | 2.5132 | 2.5411 | 2.5918 | 2.7195 | 2.8352 | 0.99705 |  | SR | 0.19812 | 0
TRUE | RB44 | Rosebery 44kV | Summer | 42.0001 | 24.2237 | 22.7773 | 24.5926 | 25.467 | 26.0794 | 26.2125 | 26.3516 | 26.5608 | 27.4059 | 29.1647 | 30.9252 | 0.94227 | 0.88287 | 42.8784 | 31.0724 | 29.8 | 32.0402 | 32.6658 | 33.2597 | 33.4736 | 33.7351 | 34.1085 | 34.7903 | 36.5032 | 38.0563 | 0.92948 | 0.86062 | RB44 | 0.57149 | 0
TRUE | RI | Risdon 33kV | Summer | 45.7255 | 51.9616 | 51.9616 | 52.7529 | 56.3893 | 57.7453 | 58.04 | 58.348 | 58.8112 | 60.6824 | 64.5768 | 68.4749 | 0.98618 | 0.79104 | 67.9417 | 66.5925 | 66.5925 | 68.6668 | 71.5563 | 72.8573 | 73.3258 | 73.8986 | 74.7165 | 76.2101 | 79.9624 | 83.3646 | 0.98264 | 0.90684 | BW | 10.2075 | 0.32
TRUE | RIZ | Zs-Richmond | Winter | 2.3693 | 2.9973 | 4.9005 | 3.0429 | 3.1511 | 3.2269 | 3.2434 | 3.2606 | 3.2865 | 3.391 | 3.6087 | 3.8265 | 0.98547 |  | 3.8639 | 3.6172 | 5.2913 | 3.7298 | 3.8027 | 3.8718 | 3.8967 | 3.9271 | 3.9706 | 4.05 | 4.2494 | 4.4302 | 0.9952
TRUE | RK | Rokeby | Summer | 13.4039 | 17.3402 | 17.3402 | 17.6043 | 18.2302 | 18.6686 | 18.7638 | 18.8634 | 19.0132 | 19.6181 | 20.8771 | 22.1373 | 0.99952 | 0.81879 | 22.8645 | 24.6628 | 24.6628 | 25.4311 | 25.9276 | 26.399 | 26.5688 | 26.7763 | 27.0727 | 27.6139 | 28.9735 | 30.2062 | 0.99995 | 0.8624 | CR | 15.6436 | 1.065
TRUE | RPZ | Zs-Rosny Park | Summer | 9.8715 | 11.3639 | 11.3639 | 11.537 | 11.9472 | 12.2345 | 12.2969 | 12.3622 | 12.4603 | 12.8568 | 13.6819 | 14.5078 | 0.99992 |  | 15.1503 | 15.0204 | 15.0204 | 15.4882 | 15.7906 | 16.0777 | 16.1811 | 16.3075 | 16.488 | 16.8176 | 17.6457 | 18.3964 | 0.99905
TRUE | SBZ | Zs-Sandy Bay | Summer | 18.7989 | 36.1425 | 38.2741 | 36.6929 | 37.9975 | 38.9113 | 39.1098 | 39.3174 | 39.6295 | 40.8904 | 43.5146 | 46.1413 | 0.99611 |  | 39.248 | 37.7031 | 39.5781 | 38.8775 | 39.6366 | 40.3572 | 40.6168 | 40.934 | 41.3871 | 42.2144 | 44.2929 | 46.1774 | 0.99933
TRUE | SD | Scottsdale | Summer | 12.5948 | 11.9955 | 11.9955 | 12.1782 | 12.6112 | 12.9144 | 12.9803 | 13.0492 | 13.1528 | 13.5713 | 14.4422 | 15.314 | 0.98743 | 0.76872 | 11.7572 | 11.8369 | 11.8369 | 12.2056 | 12.4439 | 12.6702 | 12.7516 | 12.8512 | 12.9935 | 13.2532 | 13.9058 | 14.4974 | 0.99964 | 1 | LF | 5.6014 | 0
TRUE | SL | St Leonards | Summer | 36.3243 | 16.6205 | 16.6205 | 16.8736 | 17.4736 | 17.8938 | 17.9851 | 18.0805 | 18.224 | 18.8039 | 20.0106 | 21.2186 | 1 | 0.65982 | 31.1972 | 29.5835 | 29.5835 | 30.505 | 31.1006 | 31.666 | 31.8697 | 32.1186 | 32.4741 | 33.1233 | 34.7541 | 36.2328 | 0.9998 | 0.9316 | RI | 5.8486 | 0.59998
TRUE | SM | St Marys | Summer | 11.1371 | 12.8837 | 12.8837 | 13.08 | 13.545 | 13.8707 | 13.9415 | 14.0155 | 14.1268 | 14.5762 | 15.5117 | 16.448 | 0.99939 | 0.63105 | 17.1811 | 16.0318 | 16.0318 | 16.5311 | 16.8539 | 17.1603 | 17.2707 | 17.4056 | 17.5982 | 17.95 | 18.8338 | 19.6351 | 0.99922 | 0.75654 | TB | 2.9445 | 0
TRUE | SO | Sorell | Summer | 23.7 | 26.7211 | 28.6243 | 27.128 | 28.0926 | 28.7681 | 28.9149 | 29.0683 | 29.2991 | 30.2313 | 32.1715 | 34.1135 | 0.99627 | 0.77083 | 37.4986 | 35.84 | 37.5142 | 36.9564 | 37.678 | 38.363 | 38.6097 | 38.9113 | 39.342 | 40.1284 | 42.1042 | 43.8957 | 0.99909 | 0.92281 | SM | 6.2124 | 0
TRUE | SR | Savage River DL | Summer | 23.1001 | 0.99811 | 0.99811 | 1.0133 | 1.0493 | 1.0746 | 1.0801 | 1.0858 | 1.0944 | 1.1292 | 1.2017 | 1.2742 | 1 | 0.79167 | 23.3432 | 1.099 | 1.099 | 1.1333 | 1.1554 | 1.1764 | 1.184 | 1.1932 | 1.2064 | 1.2305 | 1.2911 | 1.3461 | 0.99964 | 0.17 | SD | 4.8918 | 1.89
TRUE | ST | Smithton | Summer | 25.3099 | 24.1733 | 24.1733 | 24.5415 | 25.414 | 26.0252 | 26.1579 | 26.2968 | 26.5055 | 27.3488 | 29.104 | 30.8608 | 0.95114 | 0.87291 | 21.8625 | 21.3308 | 21.3308 | 21.9952 | 22.4247 | 22.8324 | 22.9792 | 23.1587 | 23.415 | 23.8831 | 25.059 | 26.1252 | 0.98096 | 0.79216 | MT | 11.4925 | 0
TRUE | SUZ | Zs-Summerleas | Summer | 5.7946 | 7.5904 | 7.5904 | 7.706 | 7.98 | 8.1719 | 8.2136 | 8.2572 | 8.3228 | 8.5876 | 9.1387 | 9.6903 | 0.99911 |  | 12.055 | 11.2897 | 11.2897 | 11.6414 | 11.8687 | 12.0844 | 12.1622 | 12.2572 | 12.3928 | 12.6406 | 13.2629 | 13.8272 | 0.99956
TRUE | TB | Triabunna (RT) | Summer | 5.8378 | 6.2666 | 6.2666 | 6.3621 | 6.5883 | 6.7467 | 6.7811 | 6.8171 | 6.8712 | 7.0899 | 7.5449 | 8.0003 | 0.99495 | 0.662 | 9.0762 | 9.3239 | 9.3239 | 9.6144 | 9.8021 | 9.9803 | 10.0445 | 10.1229 | 10.235 | 10.4396 | 10.9536 | 11.4196 | 0.92612 | 0.82309 | HA | 15.1834 | 1.0487
TRUE | THZ | Zs-Trial Harbour | Summer | 2.2437 | 7.5744 | 6.128 | 7.6898 | 7.9632 | 8.1547 | 8.1963 | 8.2398 | 8.3052 | 8.5695 | 9.1194 | 9.6699 | 0.90922 |  | 3.1466 | 2.5009 | 1.2286 | 2.5788 | 2.6292 | 2.677 | 2.6942 | 2.7152 | 2.7453 | 2.8002 | 2.938 | 3.0631 | 0.75751
TRUE | TR | Trevallyn | Summer | 38.6613 | 42.7373 | 43.3463 | 46.2478 | 44.9308 | 46.0113 | 46.2461 | 46.4915 | 46.8606 | 48.3515 | 51.4546 | 54.5606 | 0.99913 | 0.88594 | 71.3244 | 68.786 | 69.3218 | 73.4836 | 72.3135 | 73.6283 | 74.1018 | 74.6806 | 75.5072 | 77.0166 | 80.8086 | 84.2468 | 0.9998 | 0.92367 | RA | 11.638 | 3.2592
TRUE | TU | Tungatinah | Summer | 0.74973 | 0.92972 | 0.92972 | 0.94388 | 0.97744 | 1.0009 | 1.006 | 1.0114 | 1.0194 | 1.0519 | 1.1194 | 1.1869 | 0.98394 | 0.61017 | 1.0265 | 1.0921 | 1.0921 | 1.1261 | 1.1481 | 1.169 | 1.1765 | 1.1857 | 1.1988 | 1.2228 | 1.283 | 1.3376 | 0.99846 | 0.83333 | ST | 3.3141 | 1.1333
TRUE | UL | Ulverstone | Summer | 19.0966 | 22.3624 | 22.3624 | 22.703 | 23.5102 | 24.0756 | 24.1984 | 24.3268 | 24.52 | 25.3001 | 26.9238 | 28.549 | 0.99829 | 0.67998 | 31.413 | 29.1115 | 29.1115 | 30.0183 | 30.6044 | 31.1608 | 31.3612 | 31.6062 | 31.956 | 32.5948 | 34.1996 | 35.6547 | 0.99998 | 0.84857 | KI11 | 9.0801 | 0.30004
TRUE | WA | Waddamana | Summer | 0.14344 | 0.49896 | 0.49896 | 0.50656 | 0.52457 | 0.53718 | 0.53992 | 0.54279 | 0.5471 | 0.5645 | 0.60073 | 0.63699 | 0.98608 |  | 0.90555 | 0.65002 | 0.65002 | 0.67026 | 0.68335 | 0.69578 | 0.70025 | 0.70572 | 0.71353 | 0.72779 | 0.76363 | 0.79612 | 1 |  | DE | 1.3562 | 2.02
TRUE | WHZ | Zs-West Hobart | Summer | 26.2904 | 27.7002 | 27.7002 | 28.1221 | 29.1219 | 29.8222 | 29.9744 | 30.1335 | 30.3727 | 31.339 | 33.3503 | 35.3634 | 0.99855 |  | 37.7186 | 37.243 | 37.243 | 38.4031 | 39.1529 | 39.8647 | 40.1211 | 40.4345 | 40.8821 | 41.6993 | 43.7524 | 45.6139 | 0.99782
TRUE | WV | Wesley Vale | Summer | 8.8731 | 8.5858 | 9.3471 | 8.7166 | 9.0265 | 9.2435 | 9.2907 | 9.34 | 9.4142 | 9.7137 | 10.3371 | 10.9611 | 0.99678 | 0.77692 | 11.4381 | 11.109 | 11.7787 | 11.4551 | 11.6787 | 11.891 | 11.9675 | 12.061 | 12.1945 | 12.4383 | 13.0507 | 13.6059 | 0.9997 | 0.8574 | KI33 | 2.8651 | 0
TRUE | WYZ | Wayatinah | Winter | 1.2223 | 1.6743 | 1.6743 | 1.6998 | 1.7602 | 1.8025 | 1.8117 | 1.8213 | 1.8358 | 1.8942 | 2.0158 | 2.1374 | 0.96549 | 0.7972 | 1.1687 | 1.2821 | 1.2821 | 1.322 | 1.3479 | 1.3724 | 1.3812 | 1.392 | 1.4074 | 1.4355 | 1.5062 | 1.5703 | 0.95562 | 0.10569 | SL | 5.9534 | 0
TRUE |  | Zs-CambridgeMT | Winter
TRUE |  | Zs-CambridgeLF | Summer
TRUE | GO | Gordon | Summer | 0.33193 | 0.47355 | 0.47355 | 0.48076 | 0.49786 | 0.50983 | 0.51243 | 0.51515 | 0.51924 | 0.53576 | 0.57015 | 0.60456 | 0.92097 | 0.63415 | 0.2693 | 2.6038 | 2.6038 | 2.6849 | 2.7373 | 2.7871 | 2.805 | 2.8269 | 2.8582 | 2.9153 | 3.0589 | 3.189 | 0.82896 | 0.73585 | SO | 12.6619 | 1.067
TRUE | SH | Sheffield | Summer |  | 1.7425 | 1.7425 | 1.769 | 1.8319 | 1.876 | 1.8855 | 1.8955 | 1.9106 | 1.9714 | 2.0979 | 2.2245 | 0.99185 |  |  | 1.9766 | 1.9766 | 2.0382 | 2.078 | 2.1158 | 2.1294 | 2.146 | 2.1698 | 2.2131 | 2.3221 | 2.4209 | 0.99598 |  | WV | 4.0988 | 0.265
[32 empty] | WY | 0.00304 | 0.9

## Tx-Dx connection points
[5 empty] | Planning area |  |  |  | Greater Hobart
| Transmission-distribution connection point: |  |  |  | Supplying |  |  |  | Distribution lines
| Bridgewater |  |  |  | Voltage |  |  |  | 110/11 kV
[5 empty] | Number of transformers |  |  |  | 2
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | BWSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| Firm delivery | Substation capacity (winter and summer) (MVA) | BWSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | BWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
[6 empty] | 7.4365 | 7.5498 | 7.8182 |  | 8.047 | 8.0897 | 8.154 | 8.4134 | 8.9534 | 9.4938
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(peak season) | BWMaximum demand forecast(peak season)Maximum demand (MW) | 34.8864 | 35.4531 | 35.3192 | 36.5298 | 36.5673 | 37.2322 | 37.4716 | 37.7643 | 38.1823 | 38.9456 | 40.8631 | 42.6017
| Reactive power (coincident) (MVAr) | Maximum demand forecast(peak season) | BWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.77139 | 0.78392 | 0.78096 | 0.80773 | 0.80856 | 0.82326 | 0.82855 | 0.83503 | 0.84427 | 0.86115 | 0.90355 | 0.94199
(Winter peak) | Maximum demand (MVA) | Maximum demand forecast(peak season) | BWMaximum demand forecast(peak season)Maximum demand (MVA) | 34.895 | 35.4617 | 35.3278 | 36.5387 | 36.5763 | 37.2413 | 37.4808 | 37.7735 | 38.1916 | 38.9551 | 40.8731 | 42.6121
| Power factor (coincident) | Maximum demand forecast(peak season) | BWMaximum demand forecast(peak season)Power factor (coincident) | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976
BW
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(non-peak season) | BWMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.0931 | 24.4824 | 24.3301 | 24.8243 | 24.9387 | 25.5384 | 25.6687 | 25.8049 | 26.0098 | 26.8373 | 28.5597 | 30.2837
(Summer) | Reactive power (coincident) (MVAr) | Maximum demand forecast(non-peak season) | BWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.33109 | 0.42455 | 0.42191 | 0.43048 | 0.43246 | 0.44286 | 0.44512 | 0.44748 | 0.45104 | 0.46539 | 0.49525 | 0.52515
|  |  |  | 5.6704 |  | 7.4365 | 7.5498 |  | 8.0062 | 8.047 |  | 8.154 |  |  | 9.4938
Hours exceeding | 95% of maximum demand | Hours exceeding | BWHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
[6 empty] | 7.4365 | 7.5498 | 7.8182 | 8.0062 | 8.047 | 8.0897 | 8.154 |  | 8.9534 | 9.4938
Regional diversity factor | Summer | Regional diversity factor | BWRegional diversity factorSummer | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038
| Winter | Regional diversity factor | BWRegional diversity factorWinter | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665
|  |  |  | 5.6704 | 7.4365 |  | 7.5498 | 7.8182 | 8.0062 | 8.047 | 8.0897 | 8.154 |  | 8.9534 | 9.4938
Load transfer capacity (MVA) | Claremont | Load transfer capacity (MVA)1 | BWLoad transfer capacity (MVA)1 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Derwent Park | Load transfer capacity (MVA)2 | BWLoad transfer capacity (MVA)2 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Norfolk | Load transfer capacity (MVA)3 | BWLoad transfer capacity (MVA)3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Load transfer capacity (MVA)4 | BWLoad transfer capacity (MVA)4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Load transfer capacity (MVA)5 | BWLoad transfer capacity (MVA)5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.6704
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | BWEmbedded generation capacity (MVA)Units less than 100 kVA | 10.2075
| Units greater than 100 kVA | Embedded generation capacity (MVA) | BWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.32
| Forecast average day DER generation contribution | Embedded generation forecast capacity (MVA) | BWEmbedded generation forecast capacity (MVA) |  |  | 2.9745 | 3.3001 | 3.5562 | 3.8088 | 4.058 | 4.2957 | 4.5241 | 4.7445 | 4.9565 | 5.1614
| Forecast average day max generation impact | Embedded generation forecast capacity (MVA) | ALEmbedded generation forecast capacity (MVA) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes
[14 empty] | 2032 | 2033
[14 empty] | 35 | 35
[14 empty] | 42 | 42
[14 empty] | 40.8731 | 42.6121

## Zone subs & sub-trans lines
[5 empty] | Planning area |  |  |  | West Coast | [5 empty] | Sub-transmission lines |  | Source substation
| Zone substation: |  |  |  | Supplying |  |  |  | Distribution lines | [5 empty] | 97013 | Trial Harbour1 | 50[1]
| Trial Harbour |  |  |  | Voltage |  |  |  | 44/22 kV | [6 empty] | Trial Harbour2
[5 empty] | Number of transformers |  |  |  | 2 | [6 empty] | Trial Harbour3
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | THZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Firm delivery | Substation capacity (winter and summer) (MVA) | THZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | THZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Sub-transmission line capacity (MVA) | Total (winter) | Sub-transmission lines capacity | THZSub-transmission lines capacityTotal (winter) | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
| Firm delivery (winter) | Sub-transmission lines capacity | THZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total (summer) | Sub-transmission lines capacity | THZSub-transmission lines capacityTotal (summer) | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
| Firm delivery (summer) | Sub-transmission lines capacity | THZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(peak season) | THZMaximum demand forecast(peak season)Maximum demand (MVA) | 3.1466 | 2.5009 | 1.2286 | 2.5788 | 2.6292 | 2.677 | 2.6942 | 2.7152 | 2.7453 | 2.8002 | 2.938 | 3.0631
(Winter) | Power factor (coincident) | Maximum demand forecast(peak season) | THZMaximum demand forecast(peak season)Power factor (coincident) | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751
THZ
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(non-peak season) | THZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 2.2437 | 7.5744 | 6.128 | 7.6898 | 7.9632 | 8.1547 | 8.1963 | 8.2398 | 8.3052 | 8.5695 | 9.1194 | 9.6699
(Summer) | Power factor (coincident) | Maximum demand forecast(non-peak season) | THZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922
Hours exceeding | 95% of maximum demand | Hours exceeding | THZHours exceeding95% of maximum demand | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load transfer capacity (MVA) |  | Load transfer capacity (MVA)1 | THZLoad transfer capacity (MVA)1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Load transfer capacity (MVA)2 | THZLoad transfer capacity (MVA)2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Load transfer capacity (MVA)3 | THZLoad transfer capacity (MVA)3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Load transfer capacity (MVA)4 | THZLoad transfer capacity (MVA)4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | THZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Units greater than 100 kVA | Embedded generation capacity (MVA) | THZEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER Maximum | PV
EV
Battery
| Notes |  |  | [1] Load forecast step increase in 2018 from point load increase.

## Distribution feeder max. demand
Distribution feeder maximum demand, (Amps) 2021 50% POE forecast.
|  | Summer | [11 empty] | Winter | [11 empty] | NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [9 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Substation | Feeder | 2022 (Actual) | 2023 (Actual) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2022 (Actual) | 2023 (Actual) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Arthurs Lake | 49101 | 37.2354 | 38.0643 | 38.0643 | 38.644 | 40.018 | 40.9803 | 41.1894 | 41.408 | 41.7367 | 43.0646 | 45.8284 | 48.5948 | 37.1425 | 33.4827 | 33.4827 | 34.5257 | 35.1998 | 35.8398 | 36.0703 | 36.352 | 36.7544 | 37.4891 | 39.3349 | 41.0085 | 0.02752 | 0.057228 | 0.093249 | 0.136 | 0.18235 | 0.23622 | 0.29865 | 0.43851 | 0.55622 | 0.66858 | -0.26961 | -0.33479 | -0.40584 | -0.47416 | -0.53303 | -0.58423 | -0.63045 | -0.66926 | -0.71349 | -0.75089
Avoca | 56001 | 8.2083 | 10.9692 | 10.9692 | 11.1363 | 11.5322 | 11.8096 | 11.8698 | 11.9328 | 12.0275 | 12.4102 | 13.2067 | 14.0039 | 11.932 | 7.6532 | 7.6532 | 7.8916 | 8.0457 | 8.1919 | 8.2446 | 8.309 | 8.401 | 8.5689 | 8.9908 | 9.3734 | 0.0030425 | 0.0062843 | 0.010317 | 0.015415 | 0.021261 | 0.02843 | 0.037041 | 0.057223 | 0.073976 | 0.090166 | -0.027829 | -0.034256 | -0.041011 | -0.047021 | -0.051665 | -0.055005 | -0.05729 | -0.055758 | -0.055503 | -0.054566
Avoca | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018896 | 0.0039029 | 0.0064074 | 0.0095733 | 0.013204 | 0.017656 | 0.023004 | 0.035538 | 0.045943 | 0.055998 | -0.017283 | -0.021275 | -0.02547 | -0.029203 | -0.032086 | -0.034161 | -0.03558 | -0.034628 | -0.03447 | -0.033888
Avoca | 56003 | 52 | 58.8488 | 58.8488 | 59.745 | 61.8692 | 63.357 | 63.6803 | 64.0182 | 64.5265 | 66.5795 | 70.8524 | 75.1293 | 51.7053 | 52.7114 | 52.7114 | 54.3533 | 55.4145 | 56.422 | 56.7849 | 57.2284 | 57.8618 | 59.0185 | 61.9243 | 64.5591 | 0.017449 | 0.03618 | 0.059557 | 0.0891 | 0.12292 | 0.16429 | 0.21385 | 0.32961 | 0.4258 | 0.51863 | -0.13569 | -0.17345 | -0.21357 | -0.24989 | -0.27865 | -0.30025 | -0.31617 | -0.31193 | -0.31524 | -0.31417
Avoca | 56004 | 208.6083 | 243.1561 | 243.1561 | 246.8593 | 255.6363 | 261.7837 | 263.1194 | 264.5157 | 266.6157 | 275.0985 | 292.7537 | 310.4253 | 122.5278 | 129.1477 | 129.1477 | 133.1705 | 135.7706 | 138.2391 | 139.1281 | 140.2148 | 141.7668 | 144.6007 | 151.7203 | 158.1756 | 0.053737 | 0.10641 | 0.17426 | 0.26459 | 0.37207 | 0.50761 | 0.67313 | 1.0679 | 1.394 | 1.7102 | -0.42686 | -0.52749 | -0.63378 | -0.72731 | -0.79777 | -0.84482 | -0.8724 | -0.8165 | -0.78953 | -0.7512
Bellerive Zone | 27171 | 102.5759 | 124.2483 | 124.2483 | 126.1406 | 130.6255 | 133.7667 | 134.4492 | 135.1627 | 136.2357 | 140.5703 | 149.5917 | 158.6216 | 201.203 | 161.0075 | 161.0075 | 166.0227 | 169.2643 | 172.3417 | 173.4501 | 174.8048 | 176.7397 | 180.2726 | 189.1486 | 197.1964 | 0.037939 | 0.079921 | 0.12956 | 0.18525 | 0.2424 | 0.30517 | 0.37543 | 0.52619 | 0.65389 | 0.77345 | -0.37011 | -0.4674 | -0.5748 | -0.68119 | -0.77654 | -0.86453 | -0.94921 | -1.0481 | -1.1481 | -1.2372
Bellerive Zone | 27172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bellerive Zone | 27173 | 27.124 | 32.0169 | 32.0169 | 32.5045 | 33.6602 | 34.4696 | 34.6455 | 34.8294 | 35.1059 | 36.2228 | 38.5475 | 40.8744 | 40.6991 | 41.9895 | 41.9895 | 43.2974 | 44.1428 | 44.9453 | 45.2344 | 45.5877 | 46.0923 | 47.0137 | 49.3284 | 51.4272 | 0.011523 | 0.023477 | 0.037398 | 0.052826 | 0.068544 | 0.085781 | 0.10494 | 0.14583 | 0.18062 | 0.21323 | -0.14094 | -0.16755 | -0.19625 | -0.22389 | -0.24791 | -0.26939 | -0.28942 | -0.31146 | -0.33351 | -0.35275
Bellerive Zone | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bellerive Zone | 27175 | 77.3536 | 110.7853 | 110.7853 | 112.4726 | 116.4715 | 119.2723 | 119.8809 | 120.5171 | 121.4738 | 125.3387 | 133.3827 | 141.4341 | 162.1053 | 148.6773 | 148.6773 | 153.3085 | 156.3018 | 159.1435 | 160.167 | 161.418 | 163.2047 | 166.4671 | 174.6633 | 182.0948 | 0.032047 | 0.067515 | 0.10946 | 0.15651 | 0.20479 | 0.25782 | 0.31719 | 0.44456 | 0.55246 | 0.65348 | -0.31248 | -0.39468 | -0.48542 | -0.57532 | -0.65589 | -0.73024 | -0.80181 | -0.8854 | -0.96988 | -1.0452
Bellerive Zone | 27176 | 163.7486 | 66.3406 | 66.3406 | 67.351 | 69.7456 | 71.4228 | 71.7872 | 72.1682 | 72.7411 | 75.0555 | 79.8724 | 84.6937 | 170.3345 | 81.7649 | 81.7649 | 84.3118 | 85.958 | 87.5208 | 88.0837 | 88.7717 | 89.7542 | 91.5484 | 96.0559 | 100.1428 | 0.010132 | 0.021359 | 0.034635 | 0.049529 | 0.064814 | 0.081604 | 0.1004 | 0.14073 | 0.17489 | 0.20687 | -0.098867 | -0.12488 | -0.1536 | -0.18205 | -0.20755 | -0.23107 | -0.25371 | -0.28014 | -0.30686 | -0.33069
Bellerive Zone | 27178 | 93.9838 | 141.0191 | 141.0191 | 143.1668 | 148.2571 | 151.8223 | 152.5969 | 153.4067 | 154.6246 | 159.5442 | 169.7834 | 180.0321 | 123.5162 | 139.9497 | 139.9497 | 144.3091 | 147.1266 | 149.8016 | 150.765 | 151.9426 | 153.6244 | 156.6953 | 164.4103 | 171.4056 | 0.023769 | 0.050075 | 0.081182 | 0.11608 | 0.15189 | 0.19122 | 0.23525 | 0.32972 | 0.40975 | 0.48467 | -0.23176 | -0.29273 | -0.36003 | -0.42671 | -0.48647 | -0.54161 | -0.59469 | -0.65669 | -0.71935 | -0.77525
Bridgewater | 48180 | 133.5006 | 135.1826 | 135.1826 | 137.2414 | 142.121 | 145.5386 | 146.2812 | 147.0575 | 148.2249 | 152.941 | 162.7563 | 172.5809 | 319.3467 | 197.2811 | 197.2811 | 203.4262 | 207.398 | 211.1688 | 212.5268 | 214.1868 | 216.5576 | 220.8865 | 231.7621 | 241.623 | 0.046707 | 0.09636 | 0.15488 | 0.22113 | 0.29001 | 0.36705 | 0.45397 | 0.64248 | 0.8019 | 0.9524 | -0.47298 | -0.58295 | -0.70192 | -0.81642 | -0.9157 | -1.0037 | -1.0851 | -1.1686 | -1.2554 | -1.3305
Bridgewater | 48181 | 168.0727 | 178.0266 | 178.0266 | 180.7379 | 187.164 | 191.6647 | 192.6427 | 193.665 | 195.2025 | 201.4132 | 214.3394 | 227.2776 | 185.2675 | 174.0184 | 174.0184 | 179.4389 | 182.9424 | 186.2685 | 187.4664 | 188.9307 | 191.0219 | 194.8404 | 204.4336 | 213.1317 | 0.0029944 | 0.0062268 | 0.010146 | 0.014798 | 0.019841 | 0.025703 | 0.032496 | 0.047713 | 0.060522 | 0.072747 | -0.029336 | -0.036428 | -0.044158 | -0.051592 | -0.057998 | -0.063569 | -0.068598 | -0.072821 | -0.077634 | -0.081703
Bridgewater | 48182 | 181.4135 | 258.2723 | 220.3131 | 223.6684 | 231.6209 | 237.1907 | 238.401 | 239.6661 | 241.5687 | 249.2547 | 265.2512 | 281.2627 | 274.7805 | 303.4734 | 270.0831 | 278.4959 | 283.9335 | 289.0957 | 290.9549 | 293.2275 | 296.4731 | 302.3995 | 317.2885 | 330.7884 | 0.057998 | 0.12061 | 0.19652 | 0.28663 | 0.38431 | 0.49783 | 0.62942 | 0.92416 | 1.1722 | 1.409 | -0.5682 | -0.70557 | -0.85531 | -0.99929 | -1.1234 | -1.2313 | -1.3287 | -1.4105 | -1.5037 | -1.5825
Bridgewater | 48183 | 166.1118 | 202.2094 | 202.2094 | 242.2849 | 212.588 | 217.7002 | 218.811 | 219.9721 | 221.7184 | 228.7728 | 243.4549 | 258.1506 | 234.149 | 185.1116 | 185.1116 | 223.9309 | 194.6045 | 198.1427 | 199.417 | 200.9746 | 203.1991 | 207.261 | 217.4657 | 226.7183 | 0.055927 | 0.11491 | 0.18449 | 0.26376 | 0.34675 | 0.44039 | 0.54674 | 0.77954 | 0.9762 | 1.1626 | -0.58692 | -0.71559 | -0.85388 | -0.98559 | -1.0983 | -1.1965 | -1.2856 | -1.3701 | -1.4599 | -1.5366
Bridgewater | 48184 | 147.8078 | 158.4562 | 158.4562 | 160.8694 | 166.5891 | 170.5951 | 171.4656 | 172.3755 | 173.7439 | 179.2719 | 190.7771 | 202.2931 | 236.666 | 221.6421 | 221.6421 | 228.546 | 233.0083 | 237.2447 | 238.7705 | 240.6354 | 243.2989 | 248.1624 | 260.381 | 271.4596 | 0.04431 | 0.092142 | 0.15014 | 0.21898 | 0.2936 | 0.38034 | 0.48086 | 0.70604 | 0.89557 | 1.0765 | -0.4341 | -0.53904 | -0.65344 | -0.76344 | -0.85823 | -0.94068 | -1.0151 | -1.0776 | -1.1488 | -1.209
Bridgewater | 48185 | 129.3696 | 161.2838 | 161.2838 | 163.7401 | 169.5619 | 173.6394 | 174.5254 | 175.4515 | 176.8444 | 182.471 | 194.1815 | 205.903 | 215.9486 | 189.0347 | 189.0347 | 194.923 | 198.7288 | 202.3419 | 203.6432 | 205.2338 | 207.5054 | 211.6534 | 222.0744 | 231.5231 | 0.044656 | 0.092796 | 0.15121 | 0.22066 | 0.29604 | 0.38377 | 0.48555 | 0.71377 | 0.90582 | 1.0892 | -0.43599 | -0.54148 | -0.65644 | -0.76693 | -0.86204 | -0.94466 | -1.0191 | -1.0809 | -1.1517 | -1.2113
Bridgewater | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgewater | 48188 | 68.8158 | 108.7551 | 139.1225 | 110.4114 | 114.3371 | 117.0866 | 117.684 | 118.3085 | 119.2477 | 123.0418 | 130.9383 | 138.8422 | 117.704 | 107.0627 | 133.775 | 110.3976 | 112.5531 | 114.5994 | 115.3364 | 116.2373 | 117.5239 | 119.8732 | 125.7753 | 131.1267 | 0.023991 | 0.049889 | 0.081291 | 0.11856 | 0.15897 | 0.20593 | 0.26035 | 0.38227 | 0.48489 | 0.58285 | -0.23503 | -0.29186 | -0.35379 | -0.41335 | -0.46467 | -0.50931 | -0.5496 | -0.58343 | -0.622 | -0.6546
Bridgewater | 48189 | 68.2112 | 70.3646 | 70.3646 | 71.4362 | 73.9761 | 75.755 | 76.1415 | 76.5456 | 77.1533 | 79.6081 | 84.7171 | 89.8309 | 113.142 | 103.0704 | 103.0704 | 106.2809 | 108.356 | 110.3261 | 111.0356 | 111.9029 | 113.1415 | 115.4032 | 121.0852 | 126.2371 | 0.020141 | 0.041883 | 0.068245 | 0.099537 | 0.13346 | 0.17288 | 0.21857 | 0.32093 | 0.40708 | 0.48931 | -0.19732 | -0.24502 | -0.29702 | -0.34702 | -0.3901 | -0.42758 | -0.46141 | -0.48981 | -0.52218 | -0.54955
Bridgewater | 48190 | 117.0775 | 134.6388 | 134.6388 | 136.6893 | 141.5493 | 144.9532 | 145.6928 | 146.4659 | 147.6287 | 152.3258 | 162.1017 | 171.8867 | 186.0119 | 191.2168 | 191.2168 | 197.1731 | 201.0228 | 204.6776 | 205.994 | 207.6029 | 209.9008 | 214.0966 | 224.6379 | 234.1958 | 0.039141 | 0.081394 | 0.13263 | 0.19344 | 0.25935 | 0.33597 | 0.42477 | 0.62368 | 0.7911 | 0.95091 | -0.38346 | -0.47616 | -0.57721 | -0.67438 | -0.75811 | -0.83094 | -0.89668 | -0.95187 | -1.0148 | -1.068
Bridgewater | 48191 | 42.1157 | 58.0752 | 58.0752 | 58.9597 | 61.056 | 62.5242 | 62.8433 | 63.1767 | 63.6783 | 65.7043 | 69.9211 | 74.1417 | 68.1981 | 66.1334 | 66.1334 | 68.1934 | 69.5249 | 70.7889 | 71.2442 | 71.8006 | 72.5954 | 74.0465 | 77.6923 | 80.9979 | 0.017263 | 0.035704 | 0.057802 | 0.08358 | 0.11112 | 0.14275 | 0.17911 | 0.25981 | 0.32783 | 0.39258 | -0.17432 | -0.21469 | -0.25844 | -0.30035 | -0.33637 | -0.36774 | -0.39612 | -0.42133 | -0.44915 | -0.4728
Bridgewater | 48192 | 141.4602 | 153.1272 | 153.1272 | 155.4593 | 160.9866 | 164.8579 | 165.6991 | 166.5784 | 167.9008 | 173.2429 | 184.3612 | 195.4898 | 252.8428 | 225.2853 | 225.2853 | 232.3028 | 236.8384 | 241.1444 | 242.6952 | 244.5909 | 247.2982 | 252.2416 | 264.661 | 275.9217 | 0.072647 | 0.14788 | 0.23458 | 0.32959 | 0.42558 | 0.53029 | 0.64637 | 0.89302 | 1.1024 | 1.2989 | -0.7952 | -0.95929 | -1.134 | -1.2995 | -1.441 | -1.5653 | -1.6789 | -1.8005 | -1.9223 | -2.0278
Burnie | 91001 | 134.5759 | 176.4125 | 191.5963 | 179.0993 | 185.4671 | 189.9271 | 190.8962 | 191.9092 | 193.4327 | 199.5871 | 212.3961 | 225.2171 | 152.6801 | 143.4974 | 156.8535 | 147.9672 | 150.8562 | 153.599 | 154.5868 | 155.7942 | 157.5187 | 160.6674 | 168.5781 | 175.7507 | 0.032916 | 0.062423 | 0.09986 | 0.14826 | 0.20458 | 0.27425 | 0.35831 | 0.55603 | 0.7199 | 0.87832 | -0.26212 | -0.32107 | -0.38415 | -0.44151 | -0.48709 | -0.52122 | -0.54626 | -0.53621 | -0.53929 | -0.53602
Burnie | 91002 | 76.5109 | 57.2777 | 57.2777 | 58.15 | 60.2175 | 61.6656 | 61.9802 | 62.3091 | 62.8038 | 64.802 | 68.9609 | 73.1236 | 57.1215 | 56.8181 | 56.8181 | 58.5879 | 59.7318 | 60.8178 | 61.209 | 61.6871 | 62.3698 | 63.6166 | 66.7488 | 69.5888 | 0.034701 | 0.065675 | 0.10447 | 0.15364 | 0.21003 | 0.27901 | 0.36165 | 0.55457 | 0.71473 | 0.86925 | -0.28074 | -0.34349 | -0.41051 | -0.47165 | -0.5206 | -0.558 | -0.58634 | -0.58246 | -0.59055 | -0.59191
Burnie | 91003 | 155.683 | 168.1387 | 168.1387 | 170.6995 | 176.7686 | 181.0194 | 181.9431 | 182.9086 | 184.3607 | 190.2264 | 202.4347 | 214.6543 | 191.9684 | 217.0713 | 217.0713 | 223.8329 | 228.2032 | 232.3521 | 233.8465 | 235.673 | 238.2816 | 243.0447 | 255.0113 | 265.8614 | 0.03257 | 0.062894 | 0.099574 | 0.14222 | 0.18736 | 0.23828 | 0.29651 | 0.42351 | 0.52966 | 0.62901 | -0.3076 | -0.3771 | -0.45453 | -0.53156 | -0.60091 | -0.66481 | -0.72625 | -0.7944 | -0.86461 | -0.92736
Burnie | 91004 | 132.3971 | 166.0328 | 166.0328 | 168.5614 | 174.5546 | 178.7522 | 179.6642 | 180.6176 | 182.0515 | 187.8438 | 199.8992 | 211.9658 | 141.8489 | 146.0485 | 146.0485 | 150.5978 | 153.5381 | 156.3296 | 157.335 | 158.5639 | 160.319 | 163.5237 | 171.575 | 178.8751 | 0.032183 | 0.064582 | 0.1031 | 0.14704 | 0.19293 | 0.24432 | 0.30222 | 0.4274 | 0.53311 | 0.63261 | -0.3173 | -0.39039 | -0.47021 | -0.54762 | -0.61532 | -0.67571 | -0.73176 | -0.78924 | -0.84888 | -0.90093
Burnie | 91005 | 64.049 | 69.1955 | 69.1955 | 70.2494 | 72.7471 | 74.4964 | 74.8765 | 75.2739 | 75.8715 | 78.2855 | 83.3096 | 88.3385 | 108.4818 | 106.7944 | 106.7944 | 110.1209 | 112.271 | 114.3122 | 115.0474 | 115.946 | 117.2294 | 119.5728 | 125.4601 | 130.7981 | 0.053021 | 0.10679 | 0.17047 | 0.2426 | 0.31746 | 0.40078 | 0.49424 | 0.69517 | 0.86513 | 1.0249 | -0.52773 | -0.64936 | -0.78208 | -0.91077 | -1.0233 | -1.1239 | -1.2174 | -1.3151 | -1.4155 | -1.5034
Burnie | 91006 | 144.807 | 176.6551 | 176.6551 | 179.3455 | 185.7221 | 190.1882 | 191.1587 | 192.1731 | 193.6987 | 199.8616 | 212.6882 | 225.5268 | 227.4849 | 233.9185 | 233.9185 | 241.2048 | 245.9143 | 250.3853 | 251.9956 | 253.9638 | 256.7749 | 261.9077 | 274.8031 | 286.4953 | 0.077791 | 0.15659 | 0.24999 | 0.35583 | 0.46569 | 0.58789 | 0.7249 | 1.0192 | 1.268 | 1.5018 | -0.77482 | -0.9535 | -1.1488 | -1.3387 | -1.5054 | -1.6548 | -1.7943 | -1.9417 | -2.0931 | -2.2259
Burnie | 91007 | 60.6885 | 62.9418 | 62.9418 | 63.9004 | 66.1723 | 67.7636 | 68.1093 | 68.4708 | 69.0144 | 71.2102 | 75.7803 | 80.3546 | 100.7315 | 142.4863 | 142.4863 | 146.9247 | 149.7933 | 152.5167 | 153.4976 | 154.6965 | 156.4088 | 159.5354 | 167.3903 | 174.5123 | 0.039863 | 0.077006 | 0.1219 | 0.17398 | 0.229 | 0.29096 | 0.36181 | 0.51584 | 0.64462 | 0.76504 | -0.37759 | -0.46292 | -0.55803 | -0.6528 | -0.73824 | -0.81716 | -0.8932 | -0.97841 | -1.0659 | -1.1442
Burnie | 91008 | 153.015 | 142.1311 | 142.1311 | 144.2958 | 149.4262 | 153.0195 | 153.8002 | 154.6164 | 155.8439 | 160.8023 | 171.1222 | 181.4517 | 281.351 | 229.526 | 229.526 | 236.6755 | 241.2965 | 245.6836 | 247.2636 | 249.1949 | 251.9532 | 256.9896 | 269.6428 | 281.1155 | 0.089155 | 0.17223 | 0.27263 | 0.38912 | 0.51216 | 0.65074 | 0.80919 | 1.1537 | 1.4417 | 1.711 | -0.84449 | -1.0353 | -1.2481 | -1.46 | -1.6511 | -1.8276 | -1.9977 | -2.1883 | -2.3839 | -2.5591
Burnie | 91009 | 89.8122 | 104.8429 | 104.8429 | 106.4396 | 110.224 | 112.8746 | 113.4506 | 114.0526 | 114.958 | 118.6156 | 126.2281 | 133.8476 | 159.8709 | 171.7012 | 171.7012 | 177.0496 | 180.5064 | 183.7882 | 184.9702 | 186.415 | 188.4783 | 192.246 | 201.7114 | 210.2938 | 0.079978 | 0.15951 | 0.25413 | 0.36136 | 0.47243 | 0.59541 | 0.73265 | 1.0293 | 1.2792 | 1.5126 | -0.79517 | -0.97796 | -1.1796 | -1.3784 | -1.5557 | -1.7178 | -1.8724 | -2.0463 | -2.2225 | -2.3794
Burnie | 91010 | 92.0676 | 136.3358 | 136.3358 | 138.4122 | 143.3334 | 146.7802 | 147.5291 | 148.312 | 149.4895 | 154.2457 | 164.1448 | 174.0532 | 161.0992 | 203.0777 | 203.0777 | 209.4034 | 213.4919 | 217.3735 | 218.7714 | 220.4802 | 222.9206 | 227.3767 | 238.5719 | 248.7226 | 0.047502 | 0.091762 | 0.14525 | 0.20732 | 0.27288 | 0.34672 | 0.43114 | 0.61468 | 0.76814 | 0.91163 | -0.44994 | -0.55162 | -0.66496 | -0.77788 | -0.87969 | -0.97374 | -1.0644 | -1.1659 | -1.2701 | -1.3635
Burnie | 91011 | 100.7948 | 104.4049 | 104.4049 | 105.995 | 109.7636 | 112.4031 | 112.9766 | 113.5762 | 114.4778 | 118.1201 | 125.7008 | 133.2885 | 86.9902 | 77.4886 | 77.4886 | 79.9023 | 81.4624 | 82.9434 | 83.4769 | 84.1289 | 85.0601 | 86.7604 | 91.0322 | 94.9054 | 0.064024 | 0.12135 | 0.18852 | 0.26343 | 0.34012 | 0.42446 | 0.51825 | 0.71797 | 0.88678 | 1.0448 | -0.58688 | -0.71606 | -0.85596 | -0.99062 | -1.1076 | -1.2115 | -1.3076 | -1.4095 | -1.5125 | -1.6019
Burnie | 91012 | 112.7704 | 106.2175 | 106.2175 | 107.8351 | 111.6692 | 114.3545 | 114.938 | 115.548 | 116.4653 | 120.1708 | 127.8831 | 135.6026 | 64.5286 | 64.462 | 64.462 | 66.4699 | 67.7677 | 68.9998 | 69.4436 | 69.986 | 70.7607 | 72.1751 | 75.7288 | 78.9508 | 0.046068 | 0.091432 | 0.1461 | 0.21036 | 0.27944 | 0.3591 | 0.45083 | 0.65484 | 0.82611 | 0.98891 | -0.43326 | -0.53263 | -0.6404 | -0.74318 | -0.83103 | -0.90668 | -0.9741 | -1.0294 | -1.0918 | -1.1438
Cambridge Zone | 29481 | 37.7735 | 49.7166 | 49.7166 | 50.4738 | 52.2684 | 53.5253 | 53.7984 | 54.0839 | 54.5133 | 56.2477 | 59.8576 | 63.4708 | 77.969 | 70.2522 | 70.2522 | 72.4405 | 73.8549 | 75.1976 | 75.6812 | 76.2724 | 77.1166 | 78.6581 | 82.531 | 86.0425 | 0.015277 | 0.031392 | 0.050233 | 0.071183 | 0.092567 | 0.11603 | 0.14211 | 0.198 | 0.24546 | 0.28993 | -0.17736 | -0.21361 | -0.25297 | -0.29117 | -0.32467 | -0.3549 | -0.38334 | -0.41523 | -0.44709 | -0.47535
Cambridge Zone | 29482 | 42.567 | 44.6863 | 44.6863 | 45.3668 | 46.9799 | 48.1096 | 48.3551 | 48.6117 | 48.9976 | 50.5565 | 53.8011 | 57.0487 | 41.6207 | 41.448 | 41.448 | 42.739 | 43.5735 | 44.3657 | 44.651 | 44.9998 | 45.4979 | 46.4074 | 48.6923 | 50.764 | 0.0068795 | 0.013748 | 0.021669 | 0.030379 | 0.03921 | 0.048885 | 0.059643 | 0.082615 | 0.10201 | 0.12024 | -0.093774 | -0.10867 | -0.12448 | -0.1394 | -0.15209 | -0.16314 | -0.17318 | -0.18364 | -0.19413 | -0.20285
Cambridge Zone | 29483 | 84.6276 | 109.3632 | 109.3632 | 111.0287 | 114.9763 | 117.7412 | 118.342 | 118.97 | 119.9145 | 123.7297 | 131.6704 | 139.6185 | 170.125 | 161.5962 | 161.5962 | 166.6298 | 169.8832 | 172.9719 | 174.0843 | 175.444 | 177.386 | 180.9318 | 189.8402 | 197.9175 | 0.039033 | 0.078004 | 0.12295 | 0.17236 | 0.22247 | 0.27736 | 0.3384 | 0.46874 | 0.5788 | 0.6822 | -0.53205 | -0.61656 | -0.70628 | -0.79094 | -0.8629 | -0.92563 | -0.98257 | -1.0419 | -1.1015 | -1.1509
Cambridge Zone | 29485 | 98.1639 | 116.4042 | 116.4042 | 118.177 | 122.3788 | 125.3217 | 125.9611 | 126.6295 | 127.6348 | 131.6958 | 140.1477 | 148.6074 | 103.021 | 100.5195 | 100.5195 | 103.6506 | 105.6743 | 107.5956 | 108.2876 | 109.1334 | 110.3413 | 112.547 | 118.0884 | 123.1128 | 4.8791e-05 | 9.7505e-05 | 0.00015368 | 0.00021546 | 0.00027809 | 0.0003467 | 0.000423 | 0.00058592 | 0.0007235 | 0.00085275 | -0.00066506 | -0.0007707 | -0.00088285 | -0.00098868 | -0.0010786 | -0.001157 | -0.0012282 | -0.0013024 | -0.0013768 | -0.0014387
Cambridge Zone | 29486 | 44.3773 | 51.0831 | 51.0831 | 51.861 | 53.705 | 54.9964 | 55.277 | 55.5704 | 56.0115 | 57.7936 | 61.5027 | 65.2152 | 49.1231 | 46.4388 | 46.4388 | 47.8853 | 48.8203 | 49.7079 | 50.0276 | 50.4183 | 50.9764 | 51.9954 | 54.5554 | 56.8766 | 0.0022932 | 0.0045827 | 0.0072231 | 0.010126 | 0.01307 | 0.016295 | 0.019881 | 0.027538 | 0.034004 | 0.040079 | -0.031258 | -0.036223 | -0.041494 | -0.046468 | -0.050695 | -0.054381 | -0.057726 | -0.061212 | -0.064711 | -0.067617
Cambridge Zone | 29488 | 223.9236 | 221.2516 | 221.2516 | 224.6212 | 232.6076 | 238.2011 | 239.4165 | 240.687 | 242.5978 | 250.3165 | 266.3812 | 282.4609 | 242.7551 | 221.7913 | 221.7913 | 228.6999 | 233.1652 | 237.4044 | 238.9312 | 240.7974 | 243.4627 | 248.3294 | 260.5562 | 271.6423 | 0.02399 | 0.047128 | 0.073834 | 0.10326 | 0.13315 | 0.16597 | 0.20252 | 0.28074 | 0.34681 | 0.40893 | -0.30199 | -0.35211 | -0.4053 | -0.45545 | -0.49803 | -0.53507 | -0.56862 | -0.6032 | -0.63805 | -0.6671
Cambridge Zone | 29489 | 87.9018 | 106.5471 | 106.5471 | 108.1698 | 112.0158 | 114.7094 | 115.2947 | 115.9066 | 116.8267 | 120.5438 | 128.28 | 136.0234 | 112.4401 | 112.1984 | 112.1984 | 115.6933 | 117.9522 | 120.0967 | 120.8691 | 121.8132 | 123.1615 | 125.6234 | 131.8086 | 137.4168 | 0.010588 | 0.021159 | 0.033349 | 0.046754 | 0.060345 | 0.075235 | 0.09179 | 0.12714 | 0.157 | 0.18505 | -0.14432 | -0.16724 | -0.19158 | -0.21454 | -0.23406 | -0.25108 | -0.26652 | -0.28262 | -0.29877 | -0.31219
Cambridge Zone | 29490 | 45.0057 | 52.0869 | 52.0869 | 52.8802 | 54.7603 | 56.0772 | 56.3633 | 56.6624 | 57.1122 | 58.9294 | 62.7113 | 66.4968 | 84.5196 | 74.6825 | 74.6825 | 77.0088 | 78.5124 | 79.9398 | 80.454 | 81.0824 | 81.9798 | 83.6186 | 87.7356 | 91.4686 | 0.01693 | 0.033834 | 0.053328 | 0.074763 | 0.096497 | 0.12031 | 0.14678 | 0.20331 | 0.25105 | 0.2959 | -0.23078 | -0.26743 | -0.30635 | -0.34307 | -0.37428 | -0.40149 | -0.42619 | -0.45193 | -0.47776 | -0.49921
Cambridge Zone | 29491 | 73.6366 | 71.5355 | 71.5355 | 72.625 | 75.2071 | 77.0157 | 77.4086 | 77.8194 | 78.4372 | 80.9328 | 86.1269 | 91.3258 | 81.5088 | 74.5759 | 74.5759 | 76.8988 | 78.4003 | 79.8257 | 80.3391 | 80.9666 | 81.8627 | 83.4992 | 87.6103 | 91.3379 | 0.0027323 | 0.0054603 | 0.0086063 | 0.012066 | 0.015573 | 0.019415 | 0.023688 | 0.032811 | 0.040516 | 0.047754 | -0.037243 | -0.043159 | -0.049439 | -0.055366 | -0.060403 | -0.064794 | -0.06878 | -0.072933 | -0.077103 | -0.080565
Cambridge Zone | 29492 | 2.9803 | 3.3428 | 3.3428 | 3.3937 | 3.5144 | 3.5989 | 3.6172 | 3.6364 | 3.6653 | 3.7819 | 4.0246 | 4.2676 | 2.756 | 2.9379 | 2.9379 | 3.0295 | 3.0886 | 3.1448 | 3.165 | 3.1897 | 3.225 | 3.2895 | 3.4514 | 3.5983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | 20534 | 32.4855 | 64.3681 | 64.3681 | 65.3484 | 67.6718 | 69.2992 | 69.6528 | 70.0224 | 70.5783 | 72.8239 | 77.4975 | 82.1755 | 68.5532 | 58.8222 | 58.8222 | 60.6545 | 61.8387 | 62.963 | 63.368 | 63.8629 | 64.5698 | 65.8605 | 69.1032 | 72.0434 | 0.0094116 | 0.019668 | 0.03199 | 0.046165 | 0.061035 | 0.07783 | 0.096934 | 0.13846 | 0.1735 | 0.20645 | -0.089878 | -0.11358 | -0.13996 | -0.1663 | -0.19009 | -0.21216 | -0.23353 | -0.25809 | -0.28317 | -0.30547
Chapel Street | 20535 | 117.8285 | 93.0629 | 93.0629 | 94.4803 | 97.8395 | 100.1923 | 100.7035 | 101.2379 | 102.0416 | 105.2882 | 112.0454 | 118.8088 | 258.1471 | 271.1673 | 271.1673 | 279.6139 | 285.0733 | 290.2562 | 292.1229 | 294.4046 | 297.6633 | 303.6135 | 318.5622 | 332.1163 | 0.028899 | 0.060803 | 0.099113 | 0.14313 | 0.18926 | 0.24128 | 0.30042 | 0.4288 | 0.53718 | 0.63916 | -0.2774 | -0.35121 | -0.43339 | -0.5155 | -0.58969 | -0.65858 | -0.72533 | -0.8023 | -0.88091 | -0.9509
Chapel Street | 20536 | 72.6436 | 97.3741 | 97.3741 | 98.8571 | 102.3719 | 104.8337 | 105.3686 | 105.9278 | 106.7687 | 110.1657 | 117.2359 | 124.3127 | 155.2169 | 153.0919 | 153.0919 | 157.8606 | 160.9427 | 163.8688 | 164.9227 | 166.2109 | 168.0506 | 171.4099 | 179.8495 | 187.5016 | 0.028328 | 0.059147 | 0.096173 | 0.13878 | 0.18347 | 0.23397 | 0.29141 | 0.41627 | 0.52164 | 0.62072 | -0.27034 | -0.34155 | -0.4208 | -0.49993 | -0.57139 | -0.63768 | -0.70185 | -0.77556 | -0.85085 | -0.91777
Chapel Street | 20537 | 64.5402 | 79.2539 | 79.2539 | 80.4609 | 83.3216 | 85.3253 | 85.7607 | 86.2158 | 86.9002 | 89.6651 | 95.4196 | 101.1794 | 139.6027 | 121.5644 | 121.5644 | 125.351 | 127.7984 | 130.1219 | 130.9588 | 131.9817 | 133.4425 | 136.11 | 142.8115 | 148.8878 | 0.022733 | 0.046966 | 0.076103 | 0.10969 | 0.145 | 0.18497 | 0.23048 | 0.32961 | 0.41321 | 0.49175 | -0.21522 | -0.2711 | -0.33327 | -0.3953 | -0.45126 | -0.50309 | -0.5532 | -0.61044 | -0.66893 | -0.72078
Chapel Street | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | 20539 | 24.7721 | 32.6245 | 32.6245 | 33.1214 | 34.299 | 35.1238 | 35.303 | 35.4904 | 35.7721 | 36.9103 | 39.2791 | 41.6501 | 36.8468 | 35.1327 | 35.1327 | 36.2271 | 36.9344 | 37.6059 | 37.8478 | 38.1434 | 38.5656 | 39.3365 | 41.2733 | 43.0294 | 0.0048871 | 0.010096 | 0.01636 | 0.023581 | 0.031171 | 0.039764 | 0.049547 | 0.070858 | 0.08883 | 0.10571 | -0.046268 | -0.05828 | -0.071645 | -0.08498 | -0.097009 | -0.10815 | -0.11893 | -0.13123 | -0.1438 | -0.15495
Chapel Street | 20540 | 117.9686 | 124.6258 | 124.6258 | 126.5239 | 131.0224 | 134.1731 | 134.8577 | 135.5734 | 136.6497 | 140.9974 | 150.0463 | 159.1036 | 135.5535 | 114.634 | 114.634 | 118.2048 | 120.5127 | 122.7037 | 123.4929 | 124.4574 | 125.835 | 128.3504 | 134.6699 | 140.3998 | 0.0049695 | 0.010267 | 0.016636 | 0.023978 | 0.031696 | 0.040434 | 0.050382 | 0.072052 | 0.090327 | 0.1075 | -0.047047 | -0.059263 | -0.072853 | -0.086412 | -0.098644 | -0.10998 | -0.12093 | -0.13344 | -0.14623 | -0.15756
Chapel Street | 20541 | 152.3482 | 232.6364 | 232.6364 | 236.1795 | 244.5768 | 250.4582 | 251.7361 | 253.072 | 255.0811 | 263.1969 | 280.0883 | 296.9953 | 266.0662 | 215.7589 | 215.7589 | 222.4796 | 226.8235 | 230.9474 | 232.4327 | 234.2481 | 236.8409 | 241.5753 | 253.4696 | 264.2541 | 0.022167 | 0.046059 | 0.07464 | 0.10734 | 0.1415 | 0.17979 | 0.22335 | 0.31781 | 0.39713 | 0.47193 | -0.20511 | -0.26019 | -0.32127 | -0.38199 | -0.43658 | -0.48701 | -0.5356 | -0.59121 | -0.64793 | -0.69809
Chapel Street | 20544 | 98.8439 | 112.7117 | 112.7117 | 114.4283 | 118.4968 | 121.3463 | 121.9655 | 122.6127 | 123.5861 | 127.5182 | 135.702 | 143.8935 | 157.0133 | 138.8646 | 138.8646 | 143.1901 | 145.9859 | 148.64 | 149.596 | 150.7644 | 152.4332 | 155.4803 | 163.1355 | 170.0766 | 0.02353 | 0.048611 | 0.078768 | 0.11353 | 0.15007 | 0.19145 | 0.23855 | 0.34115 | 0.42768 | 0.50897 | -0.22276 | -0.2806 | -0.34494 | -0.40915 | -0.46706 | -0.52071 | -0.57258 | -0.63182 | -0.69236 | -0.74603
Chapel Street | 20545 | 30.8312 | 36.4563 | 36.4563 | 37.0115 | 38.3274 | 39.2491 | 39.4494 | 39.6587 | 39.9736 | 41.2454 | 43.8924 | 46.5419 | 61.5134 | 59.1125 | 59.1125 | 60.9538 | 62.1439 | 63.2738 | 63.6807 | 64.1781 | 64.8885 | 66.1856 | 69.4443 | 72.399 | 0.011696 | 0.024164 | 0.039154 | 0.056435 | 0.0746 | 0.095164 | 0.11858 | 0.16958 | 0.21259 | 0.253 | -0.11073 | -0.13948 | -0.17147 | -0.20338 | -0.23217 | -0.25884 | -0.28462 | -0.31407 | -0.34416 | -0.37084
Chapel Street | 20547 | 20.6077 | 184.9524 | 184.9524 | 187.7692 | 194.4453 | 199.1212 | 200.1372 | 201.1992 | 202.7965 | 209.2489 | 222.6779 | 236.1195 | 46.6566 | 139.7182 | 139.7182 | 144.0703 | 146.8833 | 149.5537 | 150.5156 | 151.6912 | 153.3702 | 156.436 | 164.1384 | 171.1221 | 0.042967 | 0.090027 | 0.14652 | 0.21144 | 0.27948 | 0.35625 | 0.44352 | 0.63307 | 0.793 | 0.94341 | -0.40996 | -0.51872 | -0.63974 | -0.76056 | -0.86964 | -0.97083 | -1.0688 | -1.1815 | -1.2966 | -1.3988
Chapel Street | 20548 | 135.3892 | 118.1896 | 118.1896 | 119.9896 | 124.2558 | 127.2438 | 127.8931 | 128.5717 | 129.5925 | 133.7157 | 142.2972 | 150.8867 | 329.562 | 216.1284 | 216.1284 | 222.8606 | 227.2119 | 231.3429 | 232.8307 | 234.6493 | 237.2465 | 241.989 | 253.9036 | 264.7066 | 0.037051 | 0.077036 | 0.12473 | 0.17912 | 0.23576 | 0.29932 | 0.37136 | 0.52739 | 0.65855 | 0.78148 | -0.33767 | -0.42959 | -0.53122 | -0.63196 | -0.72224 | -0.80539 | -0.8853 | -0.97693 | -1.0697 | -1.151
Chapel Street | 20549 | 87.8404 | 110.7928 | 110.7928 | 112.4801 | 116.4793 | 119.2804 | 119.889 | 120.5252 | 121.482 | 125.3472 | 133.3917 | 141.4436 | 166.8713 | 164.1892 | 164.1892 | 169.3036 | 172.6092 | 175.7474 | 176.8777 | 178.2592 | 180.2323 | 183.8351 | 192.8864 | 201.0933 | 0.030319 | 0.063246 | 0.1025 | 0.14718 | 0.19364 | 0.24537 | 0.3042 | 0.43132 | 0.53825 | 0.63839 | -0.27609 | -0.35198 | -0.43595 | -0.51924 | -0.59393 | -0.66279 | -0.72901 | -0.80487 | -0.88216 | -0.9504
Chapel Street | 20551 | 60.0501 | 45.6771 | 45.6771 | 46.3728 | 48.0216 | 49.1764 | 49.4273 | 49.6896 | 50.084 | 51.6776 | 54.9941 | 58.3137 | 59.1483 | 38.7443 | 38.7443 | 39.9511 | 40.7312 | 41.4717 | 41.7384 | 42.0644 | 42.53 | 43.3802 | 45.5161 | 47.4527 | 0.0059305 | 0.012252 | 0.019853 | 0.028615 | 0.037825 | 0.048252 | 0.060125 | 0.085985 | 0.10779 | 0.12828 | -0.056145 | -0.070722 | -0.086941 | -0.10312 | -0.11772 | -0.13124 | -0.14431 | -0.15925 | -0.1745 | -0.18803
Chapel Street | 20552 | 86.334 | 97.984 | 97.984 | 99.4763 | 103.0132 | 105.4903 | 106.0286 | 106.5912 | 107.4375 | 110.8558 | 117.9702 | 125.0913 | 196.7397 | 173.4856 | 173.4856 | 178.8895 | 182.3822 | 185.6982 | 186.8924 | 188.3522 | 190.437 | 194.2438 | 203.8076 | 212.4791 | 0.028527 | 0.058934 | 0.095496 | 0.13764 | 0.18195 | 0.2321 | 0.28921 | 0.41361 | 0.51851 | 0.61706 | -0.27007 | -0.34019 | -0.4182 | -0.49604 | -0.56625 | -0.6313 | -0.69417 | -0.766 | -0.83939 | -0.90446
Chapel Street | 20553 | 92.4249 | 106.7054 | 106.7054 | 108.3305 | 112.1822 | 114.8798 | 115.466 | 116.0787 | 117.0003 | 120.7228 | 128.4705 | 136.2255 | 173.4824 | 161.6328 | 161.6328 | 166.6675 | 169.9216 | 173.011 | 174.1237 | 175.4837 | 177.4261 | 180.9728 | 189.8832 | 197.9623 | 0.041629 | 0.082456 | 0.13 | 0.18223 | 0.23487 | 0.29176 | 0.35445 | 0.48784 | 0.60105 | 0.70654 | -0.3846 | -0.47799 | -0.57987 | -0.67963 | -0.76807 | -0.84903 | -0.92639 | -1.018 | -1.1092 | -1.1901
Chapel Street | 20554 | 97.314 | 98.7233 | 98.7233 | 100.2269 | 103.7904 | 106.2863 | 106.8286 | 107.3955 | 108.2481 | 111.6922 | 118.8603 | 126.0352 | 144.4567 | 142.86 | 142.86 | 147.31 | 150.1862 | 152.9167 | 153.9002 | 155.1023 | 156.819 | 159.9538 | 167.8293 | 174.9701 | 0.011422 | 0.023596 | 0.038235 | 0.055111 | 0.072848 | 0.092931 | 0.1158 | 0.1656 | 0.2076 | 0.24706 | -0.10813 | -0.13621 | -0.16744 | -0.19861 | -0.22672 | -0.25276 | -0.27794 | -0.3067 | -0.33608 | -0.36213
Claremont Zone | 21081 | 102.0486 | 116.6369 | 116.6369 | 118.4133 | 122.6234 | 125.5722 | 126.2129 | 126.8827 | 127.89 | 131.959 | 140.4278 | 148.9045 | 186.4731 | 163.4918 | 163.4918 | 168.5845 | 171.876 | 175.0009 | 176.1264 | 177.5021 | 179.4668 | 183.0543 | 192.0672 | 200.2392 | 0.033206 | 0.069658 | 0.1129 | 0.16176 | 0.21224 | 0.2681 | 0.33114 | 0.46712 | 0.58175 | 0.68898 | -0.29539 | -0.37938 | -0.47201 | -0.56359 | -0.64545 | -0.72069 | -0.79282 | -0.8756 | -0.95979 | -1.0339
Claremont Zone | 21082 | 30.1127 | 29.8144 | 29.8144 | 30.2685 | 31.3447 | 32.0984 | 32.2622 | 32.4334 | 32.6909 | 33.731 | 35.8958 | 38.0626 | 50.8419 | 43.6737 | 43.6737 | 45.0341 | 45.9134 | 46.7481 | 47.0488 | 47.4162 | 47.9411 | 48.8994 | 51.307 | 53.49 | 0.0078271 | 0.016419 | 0.026612 | 0.038129 | 0.050029 | 0.063194 | 0.078054 | 0.11011 | 0.13713 | 0.1624 | -0.069627 | -0.089424 | -0.11126 | -0.13285 | -0.15214 | -0.16988 | -0.18688 | -0.20639 | -0.22624 | -0.24372
Claremont Zone | 21083 | 169.635 | 193.0252 | 193.0252 | 195.965 | 202.9325 | 207.8124 | 208.8728 | 209.9812 | 211.6482 | 218.3822 | 232.3974 | 246.4257 | 200.561 | 182.2939 | 182.2939 | 187.9722 | 191.6423 | 195.1265 | 196.3814 | 197.9153 | 200.106 | 204.106 | 214.1554 | 223.2672 | 0.010673 | 0.02239 | 0.036289 | 0.051994 | 0.068222 | 0.086174 | 0.10644 | 0.15014 | 0.18699 | 0.22146 | -0.094945 | -0.12194 | -0.15172 | -0.18116 | -0.20747 | -0.23165 | -0.25483 | -0.28144 | -0.3085 | -0.33234
Claremont Zone | 21084 | 149.5598 | 162.5805 | 162.5805 | 165.0565 | 170.9251 | 175.0354 | 175.9285 | 176.862 | 178.2661 | 183.938 | 195.7427 | 207.5583 | 178.5449 | 173.0803 | 173.0803 | 178.4716 | 181.9562 | 185.2644 | 186.4559 | 187.9123 | 189.9922 | 193.7901 | 203.3315 | 211.9828 | 0.0038627 | 0.0081031 | 0.013133 | 0.018817 | 0.02469 | 0.031187 | 0.03852 | 0.054338 | 0.067673 | 0.080147 | -0.034361 | -0.044132 | -0.054907 | -0.065561 | -0.075083 | -0.083835 | -0.092226 | -0.10185 | -0.11165 | -0.12028
Claremont Zone | 21085 | 135.8418 | 150.2229 | 150.2229 | 152.5107 | 157.9332 | 161.7311 | 162.5563 | 163.4189 | 164.7163 | 169.957 | 180.8644 | 191.782 | 281.9641 | 253.2283 | 253.2283 | 261.1162 | 266.2144 | 271.0544 | 272.7977 | 274.9284 | 277.9715 | 283.5281 | 297.4879 | 310.1453 | 0.049786 | 0.1044 | 0.16925 | 0.24269 | 0.31876 | 0.40312 | 0.49828 | 0.70436 | 0.87804 | 1.0407 | -0.44493 | -0.57049 | -0.70891 | -0.84559 | -0.96758 | -1.0795 | -1.1865 | -1.3081 | -1.4322 | -1.5414
Claremont Zone | 21086 | 74.3401 | 142.0168 | 142.0168 | 144.1797 | 149.306 | 152.8964 | 153.6765 | 154.492 | 155.7185 | 160.673 | 170.9846 | 181.3058 | 150.3033 | 134.8123 | 134.8123 | 139.0116 | 141.7257 | 144.3025 | 145.2305 | 146.3649 | 147.9849 | 150.9431 | 158.375 | 165.1134 | 0.024193 | 0.050751 | 0.082256 | 0.11785 | 0.15464 | 0.19533 | 0.24126 | 0.34033 | 0.42384 | 0.50197 | -0.21521 | -0.2764 | -0.34389 | -0.41062 | -0.47026 | -0.52507 | -0.57763 | -0.63793 | -0.69927 | -0.7533
Claremont Zone | 21087 | 52.1954 | 77.199 | 77.199 | 78.3747 | 81.1613 | 83.113 | 83.5371 | 83.9804 | 84.6471 | 87.3403 | 92.9456 | 98.5561 | 105.3043 | 95.8556 | 95.8556 | 98.8414 | 100.7712 | 102.6034 | 103.2632 | 104.0698 | 105.2217 | 107.325 | 112.6093 | 117.4006 | 0.021381 | 0.044851 | 0.072694 | 0.10415 | 0.13666 | 0.17262 | 0.21321 | 0.30077 | 0.37457 | 0.44362 | -0.19019 | -0.24427 | -0.30392 | -0.36289 | -0.41559 | -0.46404 | -0.51048 | -0.56378 | -0.61799 | -0.66573
Claremont Zone | 21088 | 31.7856 | 35.0235 | 35.0235 | 35.5569 | 36.8211 | 37.7066 | 37.899 | 38.1001 | 38.4026 | 39.6244 | 42.1674 | 44.7128 | 65.0712 | 54.5458 | 54.5458 | 56.2449 | 57.343 | 58.3856 | 58.7611 | 59.2201 | 59.8755 | 61.0724 | 64.0794 | 66.8058 | 0.012469 | 0.026157 | 0.042395 | 0.060742 | 0.0797 | 0.10067 | 0.12435 | 0.17541 | 0.21845 | 0.25872 | -0.11092 | -0.14246 | -0.17724 | -0.21164 | -0.24237 | -0.27063 | -0.29771 | -0.32879 | -0.36041 | -0.38826
Claremont Zone | 21089 | 76.6201 | 94.4608 | 94.4608 | 95.8995 | 99.3092 | 101.6973 | 102.2162 | 102.7586 | 103.5744 | 106.8698 | 113.7284 | 120.5935 | 168.3732 | 139.1446 | 139.1446 | 143.4788 | 146.2802 | 148.9397 | 149.8976 | 151.0684 | 152.7405 | 155.7938 | 163.4645 | 170.4195 | 0.029142 | 0.061132 | 0.099081 | 0.14196 | 0.18628 | 0.2353 | 0.29064 | 0.41 | 0.51064 | 0.60477 | -0.25926 | -0.33297 | -0.41426 | -0.49462 | -0.56645 | -0.63246 | -0.69575 | -0.76835 | -0.84221 | -0.90726
Derby | 55001 | 114.6452 | 75.0812 | 75.0812 | 76.2246 | 78.9348 | 80.833 | 81.2454 | 81.6765 | 82.325 | 84.9443 | 90.3958 | 95.8524 | 40.0949 | 74.4056 | 74.4056 | 76.7232 | 78.2212 | 79.6434 | 80.1556 | 80.7817 | 81.6758 | 83.3085 | 87.4103 | 91.1294 | 0.075699 | 0.10439 | 0.1393 | 0.18147 | 0.228 | 0.28311 | 0.34779 | 0.49524 | 0.61831 | 0.73615 | -0.33029 | -0.3903 | -0.45438 | -0.5137 | -0.56246 | -0.60196 | -0.63458 | -0.64918 | -0.67169 | -0.68703
Derby | 55002 | 37.2707 | 53.6525 | 53.6525 | 54.4696 | 56.4063 | 57.7627 | 58.0574 | 58.3655 | 58.8289 | 60.7006 | 64.5962 | 68.4955 | 35.2053 | 38.7037 | 38.7037 | 39.9092 | 40.6885 | 41.4282 | 41.6947 | 42.0203 | 42.4854 | 43.3347 | 45.4683 | 47.4029 | 0.18711 | 0.2175 | 0.2578 | 0.31383 | 0.38252 | 0.47111 | 0.58076 | 0.84596 | 1.0648 | 1.2783 | -0.42976 | -0.48498 | -0.54311 | -0.59294 | -0.62865 | -0.6493 | -0.65706 | -0.60332 | -0.57113 | -0.53241
Derby | 55003 | 36.426 | 34.8016 | 34.8016 | 35.3317 | 36.5879 | 37.4677 | 37.6589 | 37.8587 | 38.1593 | 39.3734 | 41.9003 | 44.4295 | 16.5439 | 16.1971 | 16.1971 | 16.7016 | 17.0277 | 17.3373 | 17.4488 | 17.5851 | 17.7797 | 18.1351 | 19.0281 | 19.8377 | 0.023242 | 0.031009 | 0.040822 | 0.0534 | 0.06794 | 0.085828 | 0.10734 | 0.15772 | 0.19968 | 0.24024 | -0.083519 | -0.099242 | -0.11613 | -0.13163 | -0.14411 | -0.1537 | -0.16102 | -0.16002 | -0.16247 | -0.16309
Derwent Bridge | 49621 | 7.4313 | 0.38971 | 0.38971 | 0.39565 | 0.40971 | 0.41957 | 0.42171 | 0.42394 | 0.42731 | 0.44091 | 0.4692 | 0.49752 | 9.6281 | 0.38188 | 0.38188 | 0.39377 | 0.40146 | 0.40876 | 0.41139 | 0.4146 | 0.41919 | 0.42757 | 0.44862 | 0.46771 | 0.0015391 | 0.0030695 | 0.0050262 | 0.0075858 | 0.010591 | 0.014338 | 0.018887 | 0.029646 | 0.038599 | 0.047291 | -0.012944 | -0.015987 | -0.019253 | -0.022232 | -0.024601 | -0.026373 | -0.02767 | -0.027035 | -0.027165 | -0.02698
Derwent Park Zone | 17100 | 106.0972 | 109.5554 | 109.5554 | 111.2239 | 115.1785 | 117.9482 | 118.55 | 119.1791 | 120.1253 | 123.9473 | 131.9019 | 139.8639 | 133.2592 | 123.3127 | 123.3127 | 127.1538 | 129.6364 | 131.9933 | 132.8422 | 133.8798 | 135.3617 | 138.0675 | 144.8654 | 151.0291 | 0.0015731 | 0.0033115 | 0.0053988 | 0.007797 | 0.01031 | 0.013144 | 0.016365 | 0.023357 | 0.02926 | 0.034814 | -0.015106 | -0.019128 | -0.023607 | -0.028081 | -0.032124 | -0.035879 | -0.039517 | -0.043714 | -0.048 | -0.051816
Derwent Park Zone | 17101 | 119.0265 | 99.9933 | 99.9933 | 101.5162 | 105.1255 | 107.6535 | 108.2028 | 108.777 | 109.6406 | 113.129 | 120.3893 | 127.6564 | 122.7455 | 116.203 | 116.203 | 119.8226 | 122.1621 | 124.3831 | 125.1831 | 126.1608 | 127.5573 | 130.1071 | 136.5131 | 142.3214 | 0.016834 | 0.034283 | 0.05449 | 0.076759 | 0.099354 | 0.12407 | 0.15152 | 0.20991 | 0.25954 | 0.30617 | -0.18208 | -0.22042 | -0.26149 | -0.30072 | -0.33454 | -0.36452 | -0.39225 | -0.42243 | -0.45271 | -0.47909
Derwent Park Zone | 17102 | 15.9385 | 18.9916 | 18.9916 | 19.2809 | 19.9664 | 20.4465 | 20.5509 | 20.6599 | 20.8239 | 21.4865 | 22.8654 | 24.2457 | 18.2654 | 17.614 | 17.614 | 18.1626 | 18.5173 | 18.8539 | 18.9752 | 19.1234 | 19.3351 | 19.7216 | 20.6926 | 21.573 | 2.6255e-05 | 5.5822e-05 | 9.1298e-05 | 0.00013199 | 0.00017455 | 0.00022245 | 0.00027686 | 0.00039475 | 0.00049433 | 0.00058811 | -0.00025403 | -0.00032256 | -0.00039888 | -0.0004752 | -0.00054422 | -0.00060839 | -0.00067064 | -0.00074279 | -0.00081647 | -0.0008822
Derwent Park Zone | 17103 | 81.9232 | 106.2913 | 106.2913 | 107.9101 | 111.7468 | 114.434 | 115.0179 | 115.6283 | 116.5462 | 120.2544 | 127.972 | 135.6968 | 142.9671 | 177.7965 | 177.7965 | 183.3347 | 186.9143 | 190.3126 | 191.5365 | 193.0326 | 195.1692 | 199.0706 | 208.872 | 217.759 | 0.016663 | 0.034428 | 0.055789 | 0.080413 | 0.10629 | 0.1356 | 0.16896 | 0.24163 | 0.30291 | 0.36049 | -0.15777 | -0.19873 | -0.24431 | -0.28979 | -0.33081 | -0.36882 | -0.40555 | -0.44752 | -0.4904 | -0.52842
Derwent Park Zone | 17104 | 105.2256 | 127.983 | 127.983 | 129.9322 | 134.5519 | 137.7875 | 138.4906 | 139.2255 | 140.3308 | 144.7957 | 154.0883 | 163.3896 | 118.7696 | 124.6537 | 124.6537 | 128.5365 | 131.0462 | 133.4287 | 134.2868 | 135.3357 | 136.8337 | 139.569 | 146.4408 | 152.6715 | 0.0035707 | 0.0075918 | 0.012416 | 0.01795 | 0.023739 | 0.030254 | 0.037653 | 0.053686 | 0.067229 | 0.079983 | -0.034548 | -0.043868 | -0.054248 | -0.064627 | -0.074013 | -0.082741 | -0.091207 | -0.10102 | -0.11104 | -0.11998
Derwent Park Zone | 17105 | 133.579 | 168.818 | 168.818 | 171.3891 | 177.4828 | 181.7508 | 182.6781 | 183.6475 | 185.1055 | 190.9949 | 203.2525 | 215.5215 | 224.9652 | 207.8511 | 207.8511 | 214.3254 | 218.5101 | 222.4828 | 223.9137 | 225.6626 | 228.1604 | 232.7212 | 244.1795 | 254.5688 | 0.023908 | 0.049942 | 0.08122 | 0.1172 | 0.15496 | 0.1976 | 0.2461 | 0.35154 | 0.44051 | 0.52418 | -0.22825 | -0.2884 | -0.35536 | -0.42222 | -0.48259 | -0.53861 | -0.59283 | -0.65513 | -0.71877 | -0.77534
Derwent Park Zone | 17106 | 156.4598 | 181.5686 | 181.5686 | 184.3339 | 190.8878 | 195.4781 | 196.4755 | 197.5182 | 199.0862 | 205.4205 | 218.6039 | 231.7996 | 196.3534 | 181.0964 | 181.0964 | 186.7374 | 190.3833 | 193.8447 | 195.0914 | 196.6152 | 198.7915 | 202.7652 | 212.7486 | 221.8006 | 0.012813 | 0.027241 | 0.044553 | 0.064409 | 0.085181 | 0.10856 | 0.13511 | 0.19264 | 0.24123 | 0.287 | -0.12397 | -0.15741 | -0.19466 | -0.2319 | -0.26558 | -0.29689 | -0.32727 | -0.36248 | -0.39844 | -0.43051
Derwent Park Zone | 17107 | 89.9812 | 98.1629 | 98.1629 | 99.6579 | 103.2012 | 105.6829 | 106.2221 | 106.7858 | 107.6336 | 111.0581 | 118.1856 | 125.3196 | 129.7645 | 111.9158 | 111.9158 | 115.4019 | 117.6551 | 119.7942 | 120.5646 | 121.5063 | 122.8512 | 125.3069 | 131.4766 | 137.0706 | 0.0046664 | 0.0098949 | 0.01617 | 0.023369 | 0.030905 | 0.039389 | 0.049028 | 0.069924 | 0.087572 | 0.10419 | -0.045058 | -0.057171 | -0.07066 | -0.084145 | -0.096339 | -0.10767 | -0.11866 | -0.13139 | -0.14438 | -0.15596
Derwent Park Zone | 17108 | 28.2405 | 36.2679 | 36.2679 | 36.8203 | 38.1294 | 39.0463 | 39.2456 | 39.4538 | 39.7671 | 41.0323 | 43.6657 | 46.3015 | 53.7932 | 66.0162 | 66.0162 | 68.0726 | 69.4017 | 70.6635 | 71.1179 | 71.6734 | 72.4667 | 73.9153 | 77.5546 | 80.8544 | 0.00079382 | 0.0016431 | 0.0026642 | 0.0038409 | 0.0050773 | 0.0064765 | 0.0080693 | 0.011538 | 0.014463 | 0.017212 | -0.0075262 | -0.0094854 | -0.011665 | -0.013841 | -0.015803 | -0.017622 | -0.01938 | -0.021391 | -0.023446 | -0.025268
Derwent Park Zone | 17109 | 57.4541 | 65.6838 | 65.6838 | 66.6842 | 69.0551 | 70.7157 | 71.0765 | 71.4537 | 72.021 | 74.3124 | 79.0816 | 83.8553 | 79.7418 | 74.958 | 74.958 | 77.2928 | 78.802 | 80.2347 | 80.7507 | 81.3814 | 82.2822 | 83.927 | 88.0592 | 91.8059 | 0.0026518 | 0.005638 | 0.0092211 | 0.013331 | 0.01763 | 0.022468 | 0.027963 | 0.03987 | 0.049927 | 0.059399 | -0.025657 | -0.032578 | -0.040287 | -0.047995 | -0.054966 | -0.061447 | -0.067735 | -0.075022 | -0.082464 | -0.089102
Devonport | 80001 | 73.5541 | 83.4502 | 83.4502 | 84.7211 | 87.7334 | 89.8431 | 90.3015 | 90.7807 | 91.5014 | 94.4127 | 100.4719 | 106.5367 | 114.2846 | 104.3554 | 104.3554 | 107.606 | 109.707 | 111.7016 | 112.4199 | 113.298 | 114.5521 | 116.8419 | 122.5948 | 127.8109 | 0.019822 | 0.041208 | 0.066562 | 0.095094 | 0.12444 | 0.1567 | 0.19252 | 0.26948 | 0.33445 | 0.39503 | -0.20361 | -0.25304 | -0.3076 | -0.36146 | -0.40959 | -0.45376 | -0.49601 | -0.54442 | -0.59323 | -0.63679
Devonport | 80002 | 188.6406 | 167.0263 | 167.0263 | 169.5701 | 175.5991 | 179.8218 | 180.7394 | 181.6985 | 183.141 | 188.9679 | 201.0954 | 213.2342 | 201.8668 | 123.2314 | 123.2314 | 127.07 | 129.551 | 131.9063 | 132.7547 | 133.7916 | 135.2725 | 137.9765 | 144.7699 | 150.9296 | 0.0013748 | 0.002858 | 0.0046164 | 0.0065952 | 0.0086306 | 0.010868 | 0.013352 | 0.01869 | 0.023196 | 0.027397 | -0.014122 | -0.017549 | -0.021333 | -0.025069 | -0.028407 | -0.03147 | -0.034401 | -0.037758 | -0.041143 | -0.044165
Devonport | 80003 | 152.2416 | 184.7137 | 213.1832 | 187.5269 | 194.1944 | 198.8642 | 199.8789 | 200.9396 | 202.5348 | 208.9788 | 222.3906 | 235.8148 | 152.2368 | 173.762 | 198.8047 | 179.1745 | 182.6728 | 185.994 | 187.1902 | 188.6523 | 190.7404 | 194.5533 | 204.1323 | 212.8177 | 0.037471 | 0.077897 | 0.12582 | 0.17976 | 0.23523 | 0.29622 | 0.36392 | 0.5094 | 0.63223 | 0.74673 | -0.38489 | -0.47832 | -0.58146 | -0.68327 | -0.77425 | -0.85775 | -0.93762 | -1.0291 | -1.1214 | -1.2037
Devonport | 80004 | 52.5184 | 61.4667 | 61.4667 | 62.4028 | 64.6215 | 66.1755 | 66.5131 | 66.8661 | 67.3969 | 69.5413 | 74.0043 | 78.4714 | 105.8717 | 95.3529 | 95.3529 | 98.3231 | 100.2428 | 102.0653 | 102.7217 | 103.5241 | 104.6699 | 106.7622 | 112.0188 | 116.7849 | 0.035584 | 0.073976 | 0.11949 | 0.17071 | 0.22339 | 0.28131 | 0.3456 | 0.48376 | 0.6004 | 0.70914 | -0.36552 | -0.45424 | -0.55218 | -0.64888 | -0.73527 | -0.81457 | -0.89042 | -0.97733 | -1.0649 | -1.1431
Devonport | 80005 | 91.9024 | 112.2353 | 112.2353 | 113.9446 | 117.9959 | 120.8333 | 121.4499 | 122.0944 | 123.0637 | 126.9792 | 135.1284 | 143.2852 | 148.56 | 132.0801 | 132.0801 | 136.1942 | 138.8534 | 141.3779 | 142.2871 | 143.3985 | 144.9857 | 147.8839 | 155.1652 | 161.7671 | 0.09119 | 0.18957 | 0.30621 | 0.43746 | 0.57246 | 0.72088 | 0.88563 | 1.2397 | 1.5386 | 1.8172 | -0.93671 | -1.1641 | -1.4151 | -1.6628 | -1.8842 | -2.0874 | -2.2818 | -2.5045 | -2.729 | -2.9294
Devonport | 80006 | 124.5248 | 242.9019 | 223.9223 | 227.3326 | 235.4154 | 241.0765 | 242.3065 | 243.5923 | 245.5262 | 253.3381 | 269.5967 | 285.8704 | 124.9108 | 128.0807 | 111.3855 | 114.8551 | 117.0976 | 119.2266 | 119.9933 | 120.9306 | 122.2691 | 124.7132 | 130.8536 | 136.4211 | 0.027509 | 0.056921 | 0.091724 | 0.13079 | 0.17089 | 0.21489 | 0.26368 | 0.36823 | 0.45661 | 0.53898 | -0.28366 | -0.35157 | -0.42642 | -0.50019 | -0.566 | -0.62629 | -0.68387 | -0.74981 | -0.81613 | -0.87529
Devonport | 80007 | 85.9623 | 99.4259 | 99.4259 | 216.5524 | 104.5291 | 107.0427 | 107.5889 | 108.1598 | 109.0185 | 112.4871 | 119.7063 | 126.9321 | 220.176 | 151.0948 | 151.0948 | 259.0926 | 158.8432 | 161.7312 | 162.7713 | 164.0427 | 165.8584 | 169.1739 | 177.5034 | 185.0557 | 0.051826 | 0.10774 | 0.17403 | 0.24862 | 0.32535 | 0.40971 | 0.50334 | 0.70456 | 0.87444 | 1.0328 | -0.53235 | -0.66157 | -0.80421 | -0.94504 | -1.0709 | -1.1864 | -1.2968 | -1.4234 | -1.551 | -1.6649
Devonport | 80008 | 73.5098 | 177.7976 | 177.7976 | 180.5054 | 186.9232 | 191.4182 | 192.3949 | 193.4159 | 194.9514 | 201.1541 | 214.0637 | 226.9853 | 154.6886 | 226.4262 | 226.4262 | 233.4792 | 238.0378 | 242.3655 | 243.9243 | 245.8295 | 248.5505 | 253.5189 | 266.0012 | 277.319 | 0.083158 | 0.17288 | 0.27924 | 0.39893 | 0.52205 | 0.6574 | 0.80764 | 1.1305 | 1.4031 | 1.6572 | -0.85419 | -1.0615 | -1.2904 | -1.5164 | -1.7183 | -1.9036 | -2.0808 | -2.2839 | -2.4887 | -2.6714
Devonport | 80009 | 77.5267 | 109.1334 | 109.1334 | 110.7955 | 114.7348 | 117.4939 | 118.0934 | 118.72 | 119.6626 | 123.4698 | 131.3938 | 139.3252 | 159.7063 | 143.6219 | 143.6219 | 148.0956 | 150.9871 | 153.7322 | 154.7209 | 155.9294 | 157.6553 | 160.8068 | 168.7243 | 175.9031 | 0.051186 | 0.10641 | 0.17188 | 0.24556 | 0.32134 | 0.40465 | 0.49713 | 0.69587 | 0.86365 | 1.0201 | -0.52578 | -0.65341 | -0.79429 | -0.93338 | -1.0577 | -1.1717 | -1.2808 | -1.4058 | -1.5319 | -1.6444
Devonport | 80010 | 91.0049 | 114.4389 | 114.4389 | 116.1817 | 120.3126 | 123.2058 | 123.8344 | 124.4915 | 125.4799 | 129.4722 | 137.7814 | 146.0984 | 200.234 | 174.1102 | 174.1102 | 179.5336 | 183.0389 | 186.3667 | 187.5653 | 189.0303 | 191.1226 | 194.9431 | 204.5414 | 213.2441 | 0.0068419 | 0.014224 | 0.022975 | 0.032823 | 0.042952 | 0.054088 | 0.06645 | 0.093014 | 0.11544 | 0.13635 | -0.070279 | -0.087339 | -0.10617 | -0.12476 | -0.14137 | -0.15662 | -0.1712 | -0.18791 | -0.20476 | -0.2198
Devonport | 80011 | 99.3401 | 100.1275 | 100.1275 | 101.6524 | 105.2666 | 107.798 | 108.3481 | 108.923 | 109.7877 | 113.2808 | 120.5509 | 127.8278 | 141.2099 | 149.2893 | 149.2893 | 153.9395 | 156.9452 | 159.7986 | 160.8263 | 162.0825 | 163.8765 | 167.1523 | 175.3823 | 182.8444 | 0.045821 | 0.095596 | 0.15421 | 0.21984 | 0.28717 | 0.3612 | 0.44345 | 0.61851 | 0.7672 | 0.90602 | -0.49828 | -0.61169 | -0.73556 | -0.85615 | -0.96227 | -1.058 | -1.1479 | -1.2471 | -1.3468 | -1.4348
East Hobart Zone | 14060 | 82.2589 | 110.411 | 110.411 | 112.0925 | 116.0779 | 118.8693 | 119.4758 | 120.1098 | 121.0634 | 124.9152 | 132.9319 | 140.9562 | 84.4013 | 111.8664 | 111.8664 | 115.3509 | 117.6031 | 119.7413 | 120.5113 | 121.4526 | 122.7969 | 125.2516 | 131.4185 | 137.0101 | 0.002976 | 0.0058417 | 0.0092903 | 0.013326 | 0.017632 | 0.022631 | 0.028354 | 0.041182 | 0.051705 | 0.061487 | -0.030635 | -0.036995 | -0.043949 | -0.050721 | -0.056658 | -0.061972 | -0.066928 | -0.072021 | -0.077121 | -0.081349
East Hobart Zone | 14061 | 62.4496 | 73.8384 | 73.8384 | 74.963 | 77.6283 | 79.495 | 79.9006 | 80.3246 | 80.9623 | 83.5383 | 88.8996 | 94.2658 | 89.5773 | 77.3007 | 77.3007 | 79.7086 | 81.2649 | 82.7423 | 83.2745 | 83.9249 | 84.8539 | 86.5501 | 90.8114 | 94.6753 | 0.0012555 | 0.0024645 | 0.0039193 | 0.0056219 | 0.0074385 | 0.0095475 | 0.011962 | 0.017374 | 0.021813 | 0.02594 | -0.012924 | -0.015607 | -0.018541 | -0.021398 | -0.023903 | -0.026145 | -0.028235 | -0.030384 | -0.032536 | -0.034319
East Hobart Zone | 14062 | 26.8601 | 37.3393 | 37.3393 | 37.9079 | 39.2557 | 40.1997 | 40.4048 | 40.6192 | 40.9417 | 42.2444 | 44.9555 | 47.6692 | 28.8534 | 33.7434 | 33.7434 | 34.7945 | 35.4738 | 36.1188 | 36.3511 | 36.635 | 37.0405 | 37.7809 | 39.6411 | 41.3278 | 0.00025575 | 0.00050202 | 0.00079839 | 0.0011452 | 0.0015152 | 0.0019449 | 0.0024367 | 0.0035391 | 0.0044434 | 0.005284 | -0.0026327 | -0.0031792 | -0.0037769 | -0.0043588 | -0.004869 | -0.0053257 | -0.0057517 | -0.0061893 | -0.0066276 | -0.006991
East Hobart Zone | 14063 | 94.6817 | 101.3077 | 101.3077 | 102.8506 | 106.5075 | 109.0687 | 109.6252 | 110.2069 | 111.0819 | 114.6161 | 121.9719 | 129.3345 | 158.819 | 121.8983 | 121.8983 | 125.6953 | 128.1495 | 130.4794 | 131.3185 | 132.3442 | 133.8091 | 136.4839 | 143.2038 | 149.2968 | 0.0058358 | 0.011455 | 0.018218 | 0.026131 | 0.034575 | 0.044378 | 0.055601 | 0.080756 | 0.10139 | 0.12057 | -0.060073 | -0.072545 | -0.086182 | -0.09946 | -0.1111 | -0.12152 | -0.13124 | -0.14123 | -0.15123 | -0.15952
East Hobart Zone | 14064 | 72.2852 | 9.788 | 9.788 | 9.937 | 10.2903 | 10.5378 | 10.5916 | 10.6478 | 10.7323 | 11.0738 | 11.7844 | 12.4958 | 63.3558 | 25.041 | 25.041 | 25.821 | 26.3251 | 26.8038 | 26.9762 | 27.1869 | 27.4878 | 28.0372 | 29.4177 | 30.6693 | 0.001302 | 0.0025557 | 0.0040645 | 0.0058301 | 0.007714 | 0.0099011 | 0.012405 | 0.018017 | 0.022621 | 0.026901 | -0.013403 | -0.016185 | -0.019228 | -0.02219 | -0.024788 | -0.027113 | -0.029281 | -0.031509 | -0.033741 | -0.03559
East Hobart Zone | 14065 | 200.4432 | 215.5313 | 215.5313 | 218.8138 | 226.5937 | 232.0427 | 233.2267 | 234.4643 | 236.3257 | 243.8448 | 259.4942 | 275.1581 | 220.2679 | 195.0136 | 195.0136 | 201.0881 | 205.0143 | 208.7416 | 210.0841 | 211.725 | 214.0685 | 218.3477 | 229.0983 | 238.8459 | 0.0071146 | 0.013965 | 0.02221 | 0.031857 | 0.042151 | 0.054103 | 0.067785 | 0.098452 | 0.12361 | 0.14699 | -0.073237 | -0.088441 | -0.10507 | -0.12125 | -0.13545 | -0.14815 | -0.16 | -0.17218 | -0.18437 | -0.19448
East Hobart Zone | 14066 | 86.6237 | 85.7374 | 85.7374 | 87.0432 | 90.138 | 92.3056 | 92.7765 | 93.2689 | 94.0093 | 97.0004 | 103.2256 | 109.4567 | 98.4881 | 96.5432 | 96.5432 | 99.5504 | 101.4941 | 103.3394 | 104.004 | 104.8163 | 105.9765 | 108.0949 | 113.4171 | 118.2427 | 0.0018135 | 0.0035598 | 0.0056613 | 0.0081205 | 0.010744 | 0.013791 | 0.017278 | 0.025096 | 0.031508 | 0.037469 | -0.018668 | -0.022544 | -0.026782 | -0.030908 | -0.034526 | -0.037764 | -0.040784 | -0.043888 | -0.046996 | -0.049572
East Hobart Zone | 14067 | 55.4274 | 65.7705 | 65.7705 | 66.7722 | 69.1463 | 70.809 | 71.1703 | 71.548 | 72.116 | 74.4105 | 79.186 | 83.9659 | 82.1797 | 92.9839 | 92.9839 | 95.8803 | 97.7523 | 99.5296 | 100.1697 | 100.9521 | 102.0695 | 104.1098 | 109.2358 | 113.8835 | 0.002697 | 0.005294 | 0.0084193 | 0.012077 | 0.015979 | 0.020509 | 0.025696 | 0.037322 | 0.046858 | 0.055723 | -0.027763 | -0.033527 | -0.039829 | -0.045966 | -0.051346 | -0.056162 | -0.060654 | -0.065269 | -0.069891 | -0.073723
East Hobart Zone | 14068 | 131.6843 | 136.3959 | 136.3959 | 138.4732 | 143.3966 | 146.8449 | 147.5942 | 148.3774 | 149.5553 | 154.3137 | 164.2172 | 174.1299 | 153.4465 | 169.0099 | 169.0099 | 174.2744 | 177.677 | 180.9074 | 182.0709 | 183.493 | 185.524 | 189.2326 | 198.5497 | 206.9975 | 0.0038595 | 0.0075759 | 0.012048 | 0.017282 | 0.022866 | 0.02935 | 0.036772 | 0.053409 | 0.067055 | 0.079741 | -0.03973 | -0.047978 | -0.056997 | -0.065778 | -0.073478 | -0.08037 | -0.086798 | -0.093403 | -0.10002 | -0.1055
East Hobart Zone | 14069 | 133.6288 | 159.0075 | 159.0075 | 161.4291 | 167.1687 | 171.1886 | 172.0621 | 172.9752 | 174.3484 | 179.8956 | 191.4409 | 202.9969 | 127.708 | 141.0675 | 141.0675 | 145.4616 | 148.3017 | 150.998 | 151.9691 | 153.1561 | 154.8514 | 157.9468 | 165.7235 | 172.7746 | 0.0023837 | 0.0046962 | 0.0074753 | 0.01072 | 0.014174 | 0.018178 | 0.022756 | 0.033002 | 0.041412 | 0.049227 | -0.02429 | -0.029426 | -0.035039 | -0.040503 | -0.045293 | -0.049582 | -0.053584 | -0.057719 | -0.061858 | -0.065289
East Hobart Zone | 14070 | 138.3293 | 161.6694 | 161.6694 | 164.1316 | 169.9673 | 174.0545 | 174.9426 | 175.871 | 177.2672 | 182.9073 | 194.6458 | 206.3953 | 177.2789 | 184.3195 | 184.3195 | 190.0609 | 193.7718 | 197.2948 | 198.5637 | 200.1146 | 202.3296 | 206.3741 | 216.5352 | 225.7482 | 0.003162 | 0.0062068 | 0.0098709 | 0.014159 | 0.018734 | 0.024046 | 0.030127 | 0.043756 | 0.054937 | 0.06533 | -0.03255 | -0.039307 | -0.046696 | -0.053891 | -0.060199 | -0.065845 | -0.071111 | -0.076523 | -0.081942 | -0.086434
East Hobart Zone | 14071 | 165.5251 | 177.1021 | 177.1021 | 179.7993 | 186.1921 | 190.6695 | 191.6424 | 192.6593 | 194.1888 | 200.3673 | 213.2264 | 226.0974 | 167.5116 | 170.6609 | 170.6609 | 175.9768 | 179.4127 | 182.6746 | 183.8494 | 185.2854 | 187.3363 | 191.0811 | 200.4892 | 209.0195 | 2.325e-05 | 4.5638e-05 | 7.2581e-05 | 0.00010411 | 0.00013775 | 0.00017681 | 0.00022152 | 0.00032174 | 0.00040395 | 0.00048037 | -0.00023934 | -0.00028902 | -0.00034335 | -0.00039626 | -0.00044264 | -0.00048416 | -0.00052288 | -0.00056267 | -0.00060251 | -0.00063554
East Hobart Zone | 14072 | 17.1233 | 24.1313 | 24.1313 | 24.4989 | 25.3699 | 25.98 | 26.1126 | 26.2511 | 26.4595 | 27.3014 | 29.0535 | 30.8073 | 19.2251 | 29.2093 | 29.2093 | 30.1192 | 30.7072 | 31.2655 | 31.4666 | 31.7124 | 32.0634 | 32.7043 | 34.3146 | 35.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | 33271 | 115.3507 | 119.5924 | 119.5924 | 121.4137 | 125.7306 | 128.7541 | 129.411 | 130.0977 | 131.1306 | 135.3027 | 143.9861 | 152.6776 | 170.1643 | 168.8418 | 168.8418 | 174.101 | 177.5003 | 180.7274 | 181.8898 | 183.3105 | 185.3394 | 189.0443 | 198.3521 | 206.7916 | 1.2482 | 1.3477 | 1.4653 | 1.6005 | 1.7433 | 1.906 | 2.0921 | 2.5032 | 2.85 | 3.18 | -2.2731 | -2.4886 | -2.7193 | -2.937 | -3.1211 | -3.2788 | -3.4187 | -3.5403 | -3.6737 | -3.782
Electrona | 33272 | 136.2341 | 168.5513 | 168.5513 | 171.1183 | 177.2024 | 181.4636 | 182.3895 | 183.3574 | 184.813 | 190.6932 | 202.9314 | 215.181 | 267.0092 | 235.3199 | 235.3199 | 242.6499 | 247.3876 | 251.8854 | 253.5053 | 255.4854 | 258.3133 | 263.4769 | 276.4495 | 288.2117 | 0.5084 | 0.58839 | 0.68146 | 0.78489 | 0.89072 | 1.0075 | 1.1381 | 1.4184 | 1.6562 | 1.8804 | -1.2832 | -1.4598 | -1.6491 | -1.8294 | -1.9842 | -2.1203 | -2.2448 | -2.375 | -2.5081 | -2.6206
Electrona | 33273 | 9.8872 | 19.6684 | 19.6684 | 19.9679 | 20.6779 | 21.1751 | 21.2832 | 21.3961 | 21.566 | 22.2521 | 23.6802 | 25.1096 | 9.9268 | 15.4103 | 15.4103 | 15.8904 | 16.2006 | 16.4952 | 16.6013 | 16.7309 | 16.9161 | 17.2543 | 18.1038 | 18.8741 | 0.00028553 | 0.00057541 | 0.0009077 | 0.0012658 | 0.001621 | 0.0020002 | 0.0024135 | 0.0032727 | 0.004011 | 0.004699 | -0.0029712 | -0.0036203 | -0.0043163 | -0.0049842 | -0.0055637 | -0.0060831 | -0.006569 | -0.0071327 | -0.0076864 | -0.0081743
Electrona | 33274 | 167.6116 | 195.8357 | 195.8357 | 198.8182 | 205.8872 | 210.8382 | 211.914 | 213.0385 | 214.7298 | 221.5618 | 235.7811 | 250.0136 | 264.6481 | 252.1913 | 252.1913 | 260.0469 | 265.1242 | 269.9445 | 271.6805 | 273.8026 | 276.8332 | 282.367 | 296.2697 | 308.8752 | 0.067958 | 0.13695 | 0.21603 | 0.30128 | 0.38581 | 0.47609 | 0.57448 | 0.77903 | 0.95478 | 1.1186 | -0.70691 | -0.86141 | -1.0271 | -1.1861 | -1.324 | -1.4477 | -1.5634 | -1.6976 | -1.8295 | -1.9457
Electrona | 33275 | 5.9188 | 8.7897 | 8.7897 | 8.9236 | 9.2409 | 9.4631 | 9.5114 | 9.5619 | 9.6378 | 9.9444 | 10.5826 | 11.2214 | 12.452 | 11.6638 | 11.6638 | 12.0271 | 12.2619 | 12.4848 | 12.5651 | 12.6633 | 12.8034 | 13.0594 | 13.7024 | 14.2854 | 0.0047968 | 0.0096669 | 0.015249 | 0.021266 | 0.027232 | 0.033603 | 0.040547 | 0.054981 | 0.067384 | 0.078944 | -0.049916 | -0.060821 | -0.072514 | -0.083734 | -0.09347 | -0.1022 | -0.11036 | -0.11983 | -0.12913 | -0.13733
Electrona | 33276 | 134.4992 | 179.516 | 179.516 | 182.25 | 188.7299 | 193.2683 | 194.2545 | 195.2853 | 196.8357 | 203.0983 | 216.1327 | 229.1792 | 238.0352 | 226.0163 | 226.0163 | 233.0565 | 237.6069 | 241.9268 | 243.4827 | 245.3845 | 248.1006 | 253.06 | 265.5198 | 276.817 | 0.36289 | 0.4649 | 0.58248 | 0.71249 | 0.84534 | 0.9923 | 1.1569 | 1.5123 | 1.8121 | 2.0947 | -1.3899 | -1.6049 | -1.8307 | -2.0398 | -2.2138 | -2.3611 | -2.4903 | -2.612 | -2.7398 | -2.8425
Electrona | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay | 90019 | 389.3928 | 441.2686 | 441.2686 | 447.989 | 463.9171 | 475.0731 | 477.4971 | 480.031 | 483.8419 | 499.2362 | 531.2759 | 563.3455 | 371.7058 | 365.6421 | 365.6421 | 377.0315 | 384.3929 | 391.3816 | 393.8987 | 396.9753 | 401.3693 | 409.3925 | 429.5495 | 447.8258 | 0.00014919 | 0.0002882 | 0.0004562 | 0.00065113 | 0.00085703 | 0.0010889 | 0.0013541 | 0.0019305 | 0.0024125 | 0.0028632 | -0.0014131 | -0.0017325 | -0.0020884 | -0.0024431 | -0.0027629 | -0.0030582 | -0.0033428 | -0.0036617 | -0.0039892 | -0.0042823
Emu Bay | 90020 | 84.8518 | 106.6586 | 106.6586 | 108.283 | 112.1329 | 114.8294 | 115.4153 | 116.0278 | 116.9489 | 120.6699 | 128.4142 | 136.1657 | 113.4966 | 117.5843 | 117.5843 | 121.247 | 123.6143 | 125.8617 | 126.6712 | 127.6606 | 129.0736 | 131.6538 | 138.1359 | 144.0132 | 0.0032822 | 0.0063403 | 0.010036 | 0.014325 | 0.018855 | 0.023956 | 0.02979 | 0.042472 | 0.053075 | 0.06299 | -0.031089 | -0.038114 | -0.045946 | -0.053748 | -0.060783 | -0.067281 | -0.073542 | -0.080558 | -0.087761 | -0.094211
Emu Bay | 90021 | 62.2472 | 73.4844 | 73.4844 | 74.6036 | 77.2561 | 79.1139 | 79.5176 | 79.9395 | 80.5742 | 83.1378 | 88.4733 | 93.8139 | 98.0217 | 81.7817 | 81.7817 | 84.3292 | 85.9757 | 87.5388 | 88.1018 | 88.7899 | 89.7727 | 91.5672 | 96.0757 | 100.1634 | 0.0059377 | 0.01147 | 0.018157 | 0.025915 | 0.03411 | 0.043339 | 0.053892 | 0.076835 | 0.096018 | 0.11395 | -0.056243 | -0.068952 | -0.08312 | -0.097235 | -0.10996 | -0.12172 | -0.13304 | -0.14574 | -0.15877 | -0.17044
Emu Bay | 90023 | 94.1662 | 93.3443 | 93.3443 | 94.7659 | 98.1353 | 100.4952 | 101.008 | 101.544 | 102.3501 | 105.6066 | 112.3841 | 119.168 | 141.2551 | 128.1848 | 128.1848 | 132.1776 | 134.7584 | 137.2084 | 138.0908 | 139.1694 | 140.7098 | 143.5226 | 150.5891 | 156.9963 | 0.01468 | 0.028359 | 0.04489 | 0.064072 | 0.084331 | 0.10715 | 0.13324 | 0.18996 | 0.23739 | 0.28173 | -0.13905 | -0.17048 | -0.2055 | -0.2404 | -0.27187 | -0.30093 | -0.32893 | -0.36031 | -0.39253 | -0.42138
Emu Bay | 90024 | 83.5266 | 85.7867 | 85.7867 | 87.0932 | 90.1898 | 92.3586 | 92.8298 | 93.3225 | 94.0633 | 97.0561 | 103.2849 | 109.5196 | 129.4618 | 115.6713 | 115.6713 | 119.2744 | 121.6032 | 123.814 | 124.6103 | 125.5836 | 126.9737 | 129.5118 | 135.8885 | 141.6702 | 0.0049829 | 0.0096258 | 0.015237 | 0.021748 | 0.028625 | 0.03637 | 0.045226 | 0.06448 | 0.080578 | 0.09563 | -0.047198 | -0.057865 | -0.069754 | -0.081599 | -0.09228 | -0.10214 | -0.11165 | -0.1223 | -0.13324 | -0.14303
Geilston Bay Zone | 26161 | 81.7068 | 141.3816 | 141.3816 | 143.5348 | 148.6382 | 152.2125 | 152.9892 | 153.801 | 155.0221 | 159.9544 | 170.2198 | 180.4949 | 164.6273 | 129.9643 | 129.9643 | 134.0126 | 136.6291 | 139.1132 | 140.0078 | 141.1014 | 142.6632 | 145.515 | 152.6796 | 159.1758 | 0.027715 | 0.059353 | 0.096797 | 0.13893 | 0.18232 | 0.23018 | 0.28372 | 0.3993 | 0.49747 | 0.58967 | -0.27426 | -0.34699 | -0.4272 | -0.50657 | -0.57763 | -0.64315 | -0.70618 | -0.77925 | -0.8538 | -0.92055
Geilston Bay Zone | 26162 | 94.1273 | 95.7478 | 95.7478 | 97.206 | 100.6621 | 103.0828 | 103.6087 | 104.1585 | 104.9855 | 108.3258 | 115.2778 | 122.2364 | 184.9057 | 167.683 | 167.683 | 172.9062 | 176.2822 | 179.4872 | 180.6415 | 182.0524 | 184.0675 | 187.747 | 196.9909 | 205.3724 | 0.030739 | 0.065819 | 0.10729 | 0.15386 | 0.2017 | 0.25433 | 0.31324 | 0.43995 | 0.54711 | 0.64745 | -0.30545 | -0.38649 | -0.47581 | -0.56409 | -0.643 | -0.71559 | -0.78525 | -0.86591 | -0.94751 | -1.02
Geilston Bay Zone | 26163 | 56.7462 | 82.1388 | 82.1388 | 83.3898 | 86.3547 | 88.4313 | 88.8825 | 89.3542 | 90.0636 | 92.9291 | 98.893 | 104.8626 | 116.3975 | 103.9341 | 103.9341 | 107.1716 | 109.2641 | 111.2506 | 111.9661 | 112.8407 | 114.0896 | 116.3703 | 122.0999 | 127.295 | 0.019779 | 0.042353 | 0.069039 | 0.099004 | 0.12979 | 0.16365 | 0.20156 | 0.28309 | 0.35205 | 0.41662 | -0.19655 | -0.24869 | -0.30617 | -0.36297 | -0.41375 | -0.46046 | -0.50528 | -0.55718 | -0.60969 | -0.65637
Geilston Bay Zone | 26164 | 105.4822 | 204.8085 | 204.8085 | 207.9277 | 215.3205 | 220.4984 | 221.6235 | 222.7995 | 224.5683 | 231.7133 | 246.5841 | 261.4688 | 230.6862 | 201.364 | 201.364 | 207.6364 | 211.6904 | 215.5391 | 216.9253 | 218.6197 | 221.0395 | 225.458 | 236.5587 | 246.6237 | 0.045264 | 0.096921 | 0.15799 | 0.22656 | 0.29701 | 0.37451 | 0.46125 | 0.64784 | 0.80564 | 0.95339 | -0.44978 | -0.56912 | -0.70064 | -0.83064 | -0.94683 | -1.0537 | -1.1563 | -1.2751 | -1.3952 | -1.502
Geilston Bay Zone | 26165 | 100.2113 | 129.2221 | 129.2221 | 131.1902 | 135.8546 | 139.1215 | 139.8314 | 140.5734 | 141.6894 | 146.1975 | 155.5801 | 164.9715 | 149.9306 | 133.4638 | 133.4638 | 137.6211 | 140.3081 | 142.8591 | 143.7778 | 144.9008 | 146.5047 | 149.4333 | 156.7908 | 163.4619 | 0.0094159 | 0.020159 | 0.032861 | 0.047122 | 0.061773 | 0.07789 | 0.09593 | 0.13473 | 0.16755 | 0.19828 | -0.093552 | -0.11837 | -0.14573 | -0.17276 | -0.19693 | -0.21917 | -0.2405 | -0.26521 | -0.2902 | -0.31242
Geilston Bay Zone | 26166 | 49.8948 | 59.7658 | 59.7658 | 60.676 | 62.8333 | 64.3443 | 64.6726 | 65.0158 | 65.532 | 67.617 | 71.9565 | 76.3 | 97.0534 | 87.1352 | 87.1352 | 89.8494 | 91.6037 | 93.2692 | 93.869 | 94.6022 | 95.6493 | 97.5613 | 102.3648 | 106.7202 | 0.017527 | 0.037531 | 0.061179 | 0.087732 | 0.11501 | 0.14502 | 0.17861 | 0.25086 | 0.31197 | 0.36918 | -0.17417 | -0.22038 | -0.27131 | -0.32165 | -0.36664 | -0.40804 | -0.44775 | -0.49375 | -0.54028 | -0.58164
Geilston Bay Zone | 26167 | 120.3958 | 152.1594 | 152.1594 | 154.4768 | 159.9692 | 163.816 | 164.6519 | 165.5256 | 166.8397 | 172.148 | 183.196 | 194.2543 | 215.5451 | 216.0378 | 216.0378 | 222.7672 | 227.1166 | 231.2458 | 232.733 | 234.5509 | 237.147 | 241.8875 | 253.7971 | 264.5956 | 0.023093 | 0.050186 | 0.082495 | 0.11913 | 0.15706 | 0.19905 | 0.24651 | 0.34851 | 0.43523 | 0.5167 | -0.22047 | -0.28361 | -0.35385 | -0.42405 | -0.48757 | -0.54671 | -0.60417 | -0.67166 | -0.74078 | -0.803
Geilston Bay Zone | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | 53001 | 88 | 114.5413 | 99.3576 | 100.8707 | 104.4572 | 106.9691 | 107.5149 | 108.0854 | 108.9435 | 112.4097 | 119.6239 | 126.8448 | 0 | 127.476 | 114.1199 | 117.6746 | 119.9722 | 122.1534 | 122.939 | 123.8992 | 125.2706 | 127.7747 | 134.0659 | 139.7701 | 0.053801 | 0.10878 | 0.1715 | 0.23866 | 0.30489 | 0.37522 | 0.45144 | 0.60862 | 0.74247 | 0.86659 | -0.54602 | -0.66845 | -0.79884 | -0.92252 | -1.0286 | -1.1222 | -1.2083 | -1.3055 | -1.4003 | -1.4824
George Town | 53002 | 126 | 157.5899 | 157.5899 | 159.99 | 165.6784 | 169.6625 | 170.5282 | 171.4331 | 172.7941 | 178.2919 | 189.7342 | 201.1872 | 123 | 162.6213 | 162.6213 | 167.6868 | 170.9608 | 174.0691 | 175.1885 | 176.5569 | 178.5111 | 182.0795 | 191.0444 | 199.1729 | 6.4896e-05 | 0.00011941 | 0.00018517 | 0.00026422 | 0.00035132 | 0.00045465 | 0.00057613 | 0.00085426 | 0.0010857 | 0.0013076 | -0.00054485 | -0.0006562 | -0.00077303 | -0.00087848 | -0.0009623 | -0.0010269 | -0.0010767 | -0.001085 | -0.0011068 | -0.0011168
George Town | 53003 | 84.0827 | 96.7199 | 191.6181 | 98.1929 | 101.6842 | 104.1294 | 104.6607 | 105.2161 | 106.0514 | 109.4256 | 116.4483 | 123.4775 | 145.8988 | 143.2128 | 226.6887 | 147.6738 | 150.5571 | 153.2944 | 154.2803 | 155.4853 | 157.2063 | 160.3488 | 168.2438 | 175.4021 | 0.10082 | 0.19315 | 0.3006 | 0.41871 | 0.53791 | 0.66702 | 0.80895 | 1.1064 | 1.3596 | 1.5959 | -1.0155 | -1.2256 | -1.4532 | -1.6732 | -1.8654 | -2.0378 | -2.1988 | -2.3789 | -2.5574 | -2.7135
George Town | 53004 | 37 | 46.7775 | 46.7775 | 47.49 | 49.1784 | 50.3611 | 50.618 | 50.8866 | 51.2906 | 52.9225 | 56.3189 | 59.7185 | 56.1247 | 54.3509 | 54.3509 | 56.0439 | 57.1381 | 58.1769 | 58.5511 | 59.0084 | 59.6616 | 60.8542 | 63.8504 | 66.5671 | 0.034004 | 0.068694 | 0.10829 | 0.1507 | 0.19255 | 0.237 | 0.2852 | 0.38465 | 0.46932 | 0.54786 | -0.34496 | -0.42222 | -0.50452 | -0.5826 | -0.64956 | -0.70869 | -0.76306 | -0.82437 | -0.88419 | -0.93599
George Town | 53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3654e-05 | 0.00017943 | 0.00027924 | 0.00038896 | 0.00049967 | 0.0006196 | 0.00075143 | 0.0010277 | 0.0012629 | 0.0014823 | -0.00094324 | -0.0011383 | -0.0013498 | -0.0015542 | -0.0017327 | -0.0018929 | -0.0020425 | -0.0022098 | -0.0023756 | -0.0025207
George Town | 53007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6098 | 8.6098 | 8.878 | 9.0514 | 9.2159 | 9.2752 | 9.3477 | 9.4511 | 9.64 | 10.1147 | 10.545 | 0.00014048 | 0.00026914 | 0.00041885 | 0.00058343 | 0.00074951 | 0.0009294 | 0.0011271 | 0.0015416 | 0.0018943 | 0.0022235 | -0.0014149 | -0.0017075 | -0.0020247 | -0.0023313 | -0.002599 | -0.0028393 | -0.0030637 | -0.0033147 | -0.0035635 | -0.0037811
George Town | 53008 | 52 | 69.6033 | 69.6033 | 70.6633 | 73.1757 | 74.9354 | 75.3178 | 75.7174 | 76.3186 | 78.7468 | 83.8005 | 88.859 | 74.4246 | 65.7431 | 65.7431 | 67.791 | 69.1146 | 70.3711 | 70.8237 | 71.3769 | 72.1669 | 73.6095 | 77.2338 | 80.5199 | 0.08205 | 0.15146 | 0.23501 | 0.33497 | 0.44463 | 0.57421 | 0.72614 | 1.0729 | 1.3616 | 1.6383 | -0.70184 | -0.84443 | -0.9943 | -1.1301 | -1.2387 | -1.3233 | -1.3895 | -1.4066 | -1.4398 | -1.4577
George Town | 53009 | 61 | 76.7992 | 76.7992 | 77.9688 | 80.741 | 82.6826 | 83.1045 | 83.5455 | 84.2087 | 86.888 | 92.4642 | 98.0457 | 161.3419 | 90.4959 | 90.4959 | 93.3148 | 95.1367 | 96.8664 | 97.4894 | 98.2509 | 99.3384 | 101.3241 | 106.3129 | 110.8363 | 0.087149 | 0.17263 | 0.27087 | 0.37707 | 0.48271 | 0.59573 | 0.71889 | 0.97445 | 1.1919 | 1.3938 | -0.88186 | -1.0737 | -1.2793 | -1.4758 | -1.6454 | -1.796 | -1.9354 | -2.0922 | -2.2459 | -2.3798
George Town | 53010 | 190.0394 | 223.4392 | 204.4596 | 207.5735 | 214.9537 | 220.1227 | 221.2459 | 222.42 | 224.1857 | 231.3186 | 246.1641 | 261.0234 | 248.8726 | 210.472 | 193.7769 | 199.8128 | 203.7141 | 207.4179 | 208.7518 | 210.3823 | 212.711 | 216.963 | 227.6454 | 237.3312 | 0.0020604 | 0.0039474 | 0.0061432 | 0.008557 | 0.010993 | 0.013631 | 0.016531 | 0.022609 | 0.027783 | 0.032612 | -0.020751 | -0.025044 | -0.029696 | -0.034192 | -0.038119 | -0.041643 | -0.044934 | -0.048616 | -0.052264 | -0.055456
Gordon | 49801 | 8.68 | 12.779 | 12.779 | 12.9737 | 13.4349 | 13.758 | 13.8282 | 13.9016 | 14.0119 | 14.4578 | 15.3856 | 16.3143 | 13.6069 | 14.2927 | 14.2927 | 14.7379 | 15.0257 | 15.2989 | 15.3973 | 15.5175 | 15.6893 | 16.0029 | 16.7908 | 17.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna Rural Zone | 37001 | 0 | 85.9165 | 85.9165 | 87.225 | 90.3263 | 92.4984 | 92.9704 | 93.4637 | 94.2057 | 97.203 | 103.4413 | 109.6853 | 3.8066 | 24.1886 | 24.1886 | 24.942 | 25.429 | 25.8914 | 26.0579 | 26.2614 | 26.5521 | 27.0828 | 28.4163 | 29.6253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna Rural Zone | 37002 | 61.6667 | 61.992 | 61.992 | 62.9362 | 65.1738 | 66.7411 | 67.0816 | 67.4376 | 67.973 | 70.1357 | 74.6368 | 79.1421 | 18.9947 | 20.2349 | 20.2349 | 20.8652 | 21.2726 | 21.6594 | 21.7987 | 21.9689 | 22.2121 | 22.6561 | 23.7716 | 24.783 | 0.0068321 | 0.013626 | 0.022311 | 0.033673 | 0.047014 | 0.063648 | 0.083839 | 0.1316 | 0.17134 | 0.20993 | -0.057458 | -0.070968 | -0.085466 | -0.09869 | -0.10921 | -0.11707 | -0.12283 | -0.12001 | -0.12058 | -0.11977
Hadspen | 67081 | 74.2794 | 104.3756 | 104.3756 | 105.9653 | 109.7328 | 112.3716 | 112.945 | 113.5443 | 114.4457 | 118.087 | 125.6656 | 133.2512 | 135.6236 | 126.6093 | 126.6093 | 130.5531 | 133.1021 | 135.522 | 136.3936 | 137.4589 | 138.9804 | 141.7586 | 148.7382 | 155.0667 | 0.038756 | 0.074331 | 0.11606 | 0.16249 | 0.2098 | 0.26145 | 0.31847 | 0.44078 | 0.54309 | 0.63786 | -0.37221 | -0.45333 | -0.54177 | -0.62787 | -0.70364 | -0.77215 | -0.83667 | -0.90956 | -0.98154 | -1.0445
Hadspen | 67082 | 106.4002 | 142.4692 | 142.4692 | 144.639 | 149.7816 | 153.3834 | 154.166 | 154.9841 | 156.2145 | 161.1848 | 171.5292 | 181.8833 | 118.3075 | 125.6634 | 125.6634 | 129.5777 | 132.1077 | 134.5096 | 135.3746 | 136.432 | 137.9421 | 140.6995 | 147.627 | 153.9082 | 0.11368 | 0.19477 | 0.29052 | 0.40031 | 0.5161 | 0.64781 | 0.79817 | 1.13 | 1.4087 | 1.6732 | -0.97511 | -1.1497 | -1.3354 | -1.5089 | -1.6537 | -1.7754 | -1.8809 | -1.9638 | -2.056 | -2.1285
Hadspen | 67083 | 120.6001 | 148.8228 | 148.8228 | 151.0893 | 156.4612 | 160.2237 | 161.0412 | 161.8958 | 163.1811 | 168.373 | 179.1788 | 189.9946 | 130.6712 | 132.8174 | 132.8174 | 136.9545 | 139.6285 | 142.1671 | 143.0814 | 144.199 | 145.7951 | 148.7095 | 156.0314 | 162.6701 | 0.020732 | 0.03939 | 0.061099 | 0.085105 | 0.10951 | 0.1362 | 0.16578 | 0.22853 | 0.28155 | 0.3311 | -0.21177 | -0.25349 | -0.29837 | -0.34123 | -0.37816 | -0.41072 | -0.44058 | -0.4721 | -0.50365 | -0.53061
Hadspen | 67084 | 188.0448 | 193.5421 | 178.3584 | 181.0747 | 187.5128 | 192.022 | 193.0017 | 194.0259 | 195.5663 | 201.7886 | 214.7389 | 227.7012 | 155.7736 | 175.9694 | 162.6132 | 167.6785 | 170.9524 | 174.0605 | 175.1799 | 176.5482 | 178.5023 | 182.0705 | 191.035 | 199.1631 | 0.021012 | 0.037734 | 0.057631 | 0.080697 | 0.10525 | 0.1334 | 0.16571 | 0.23741 | 0.29759 | 0.3548 | -0.19332 | -0.2294 | -0.26798 | -0.30412 | -0.33439 | -0.35985 | -0.38192 | -0.39863 | -0.41763 | -0.43258
Hadspen | 67085 | 68.4323 | 75.9768 | 75.9768 | 77.1339 | 79.8764 | 81.7972 | 82.2145 | 82.6508 | 83.307 | 85.9575 | 91.4741 | 96.9957 | 112.9565 | 114.638 | 114.638 | 118.2089 | 120.5169 | 122.708 | 123.4972 | 124.4618 | 125.8394 | 128.3549 | 134.6746 | 140.4047 | 0.028332 | 0.054425 | 0.085021 | 0.11902 | 0.1536 | 0.19129 | 0.23289 | 0.32194 | 0.39642 | 0.46534 | -0.27028 | -0.3299 | -0.39497 | -0.4584 | -0.51431 | -0.56497 | -0.6128 | -0.66726 | -0.72097 | -0.76799
Hadspen | 67086 | 85.6121 | 105.0687 | 105.0687 | 106.6689 | 110.4615 | 113.1178 | 113.695 | 114.2983 | 115.2057 | 118.8712 | 126.5 | 134.136 | 181.1025 | 162.3636 | 162.3636 | 167.4211 | 170.6899 | 173.7933 | 174.911 | 176.2772 | 178.2283 | 181.791 | 190.7417 | 198.8573 | 0.080619 | 0.15487 | 0.24193 | 0.33866 | 0.43707 | 0.54431 | 0.6627 | 0.91608 | 1.128 | 1.3241 | -0.76907 | -0.93874 | -1.1239 | -1.3044 | -1.4635 | -1.6076 | -1.7437 | -1.8987 | -2.0515 | -2.1853
Hadspen | 67087 | 175.357 | 197.9343 | 197.9343 | 200.9488 | 208.0935 | 213.0976 | 214.1849 | 215.3215 | 217.0309 | 223.9361 | 238.3078 | 252.6928 | 204.7528 | 202.1828 | 202.1828 | 208.4806 | 212.5511 | 216.4155 | 217.8074 | 219.5086 | 221.9383 | 226.3747 | 237.5206 | 247.6265 | 0.097632 | 0.18804 | 0.29434 | 0.41431 | 0.53869 | 0.67745 | 0.8335 | 1.171 | 1.4553 | 1.7227 | -1.055 | -1.2551 | -1.4704 | -1.6754 | -1.851 | -2.0041 | -2.1427 | -2.2774 | -2.4167 | -2.5333
Hadspen | 67088 | 42.3875 | 51.4599 | 51.4599 | 52.2437 | 54.1012 | 55.4021 | 55.6848 | 55.9803 | 56.4248 | 58.22 | 61.9564 | 65.6963 | 89.4732 | 86.2535 | 86.2535 | 88.9402 | 90.6767 | 92.3253 | 92.9191 | 93.6449 | 94.6814 | 96.574 | 101.329 | 105.6403 | 0.64675 | 0.69521 | 0.75179 | 0.81452 | 0.87832 | 0.94802 | 1.025 | 1.188 | 1.3248 | 1.4519 | -1.1999 | -1.3093 | -1.4278 | -1.5419 | -1.6414 | -1.7302 | -1.8129 | -1.9047 | -1.9952 | -2.072
Hadspen | 67089 | 47.6339 | 60.2545 | 60.2545 | 61.1722 | 63.3472 | 64.8705 | 65.2015 | 65.5475 | 66.0679 | 68.1699 | 72.5449 | 76.924 | 141.2943 | 102.5919 | 102.5919 | 105.7875 | 107.853 | 109.8139 | 110.5201 | 111.3833 | 112.6162 | 114.8674 | 120.523 | 125.651 | 0.052368 | 0.1006 | 0.15715 | 0.21999 | 0.28391 | 0.35357 | 0.43047 | 0.59506 | 0.73272 | 0.86012 | -0.49957 | -0.60978 | -0.73005 | -0.84728 | -0.95063 | -1.0443 | -1.1327 | -1.2333 | -1.3326 | -1.4195
Hadspen | 67090 | 166.157 | 180.8122 | 180.8122 | 202.8346 | 190.0925 | 194.6637 | 195.657 | 196.6953 | 198.2568 | 204.5647 | 217.6932 | 230.8338 | 236.1728 | 253.1333 | 253.1333 | 278.2334 | 266.1144 | 270.9527 | 272.6953 | 274.8252 | 277.8672 | 283.4216 | 297.3762 | 310.0289 | 0.098667 | 0.19263 | 0.30437 | 0.43358 | 0.57076 | 0.72749 | 0.90689 | 1.3038 | 1.6366 | 1.9524 | -0.94854 | -1.1523 | -1.3705 | -1.5759 | -1.7489 | -1.8956 | -2.0241 | -2.1272 | -2.2415 | -2.3345
Hadspen | 67091 | 66.7529 | 86.6756 | 86.6756 | 87.9956 | 91.1243 | 93.3156 | 93.7917 | 94.2894 | 95.038 | 98.0618 | 104.3551 | 110.6544 | 135.2339 | 128.1443 | 128.1443 | 132.1359 | 134.7158 | 137.1651 | 138.0472 | 139.1255 | 140.6654 | 143.4773 | 150.5415 | 156.9467 | 0.051173 | 0.10006 | 0.15802 | 0.22328 | 0.29038 | 0.36408 | 0.44702 | 0.62364 | 0.77132 | 0.90812 | -0.56274 | -0.67558 | -0.80012 | -0.92317 | -1.0332 | -1.1345 | -1.2315 | -1.3442 | -1.4552 | -1.5546
Howrah Zone | 22323 | 61.6583 | 74.9383 | 74.9383 | 76.0796 | 78.7846 | 80.6791 | 81.0908 | 81.5211 | 82.1683 | 84.7826 | 90.2238 | 95.67 | 112.484 | 99.0911 | 99.0911 | 102.1777 | 104.1727 | 106.0667 | 106.7488 | 107.5826 | 108.7734 | 110.9478 | 116.4104 | 121.3634 | 0.017677 | 0.037241 | 0.060375 | 0.086327 | 0.11296 | 0.14221 | 0.17496 | 0.24522 | 0.30473 | 0.36045 | -0.17236 | -0.2177 | -0.26776 | -0.31735 | -0.36179 | -0.4028 | -0.44228 | -0.48838 | -0.53498 | -0.57655
Howrah Zone | 22324 | 75.4885 | 107.3126 | 107.3126 | 108.947 | 112.8205 | 115.5336 | 116.1231 | 116.7393 | 117.6661 | 121.4098 | 129.2016 | 137.0006 | 128.7924 | 136.2594 | 136.2594 | 140.5038 | 143.2471 | 145.8514 | 146.7895 | 147.936 | 149.5734 | 152.5634 | 160.075 | 166.8858 | 0.020918 | 0.043569 | 0.070325 | 0.10036 | 0.13122 | 0.1652 | 0.20313 | 0.28498 | 0.35434 | 0.41937 | -0.21441 | -0.26647 | -0.32376 | -0.38032 | -0.43081 | -0.47722 | -0.52173 | -0.57315 | -0.62517 | -0.67169
Howrah Zone | 22325 | 81.792 | 107.388 | 107.388 | 109.0235 | 112.8999 | 115.6148 | 116.2047 | 116.8214 | 117.7488 | 121.4952 | 129.2924 | 137.097 | 175.8893 | 161.3236 | 161.3236 | 166.3487 | 169.5966 | 172.6801 | 173.7906 | 175.148 | 177.0867 | 180.6266 | 189.52 | 197.5836 | 0.031376 | 0.066099 | 0.10716 | 0.15322 | 0.20049 | 0.25241 | 0.31054 | 0.43523 | 0.54087 | 0.63976 | -0.30592 | -0.3864 | -0.47524 | -0.56326 | -0.64213 | -0.71493 | -0.785 | -0.86683 | -0.94954 | -1.0233
Howrah Zone | 22326 | 29.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2934 | 53.2046 | 53.2046 | 54.8619 | 55.933 | 56.9499 | 57.3162 | 57.7639 | 58.4032 | 59.5707 | 62.5037 | 65.1631 | 0.0093532 | 0.019607 | 0.031833 | 0.045685 | 0.06002 | 0.075873 | 0.093784 | 0.13226 | 0.16496 | 0.19566 | -0.085883 | -0.10981 | -0.13644 | -0.16306 | -0.18715 | -0.20958 | -0.23139 | -0.25703 | -0.28324 | -0.30682
Howrah Zone | 22328 | 81.3869 | 151.2502 | 151.2502 | 153.5537 | 159.0133 | 162.8371 | 163.668 | 164.5365 | 165.8428 | 171.1194 | 182.1014 | 193.0936 | 175.4417 | 180.7069 | 180.7069 | 186.3357 | 189.9739 | 193.4278 | 194.6718 | 196.1923 | 198.3639 | 202.3291 | 212.2911 | 221.3235 | 0.030284 | 0.0638 | 0.10343 | 0.14789 | 0.19352 | 0.24363 | 0.29973 | 0.42009 | 0.52205 | 0.6175 | -0.29528 | -0.37296 | -0.45871 | -0.54366 | -0.61979 | -0.69005 | -0.75768 | -0.83667 | -0.9165 | -0.98772
Howrah Zone | 22329 | 105.2865 | 130.5838 | 130.5838 | 132.5726 | 137.2861 | 140.5875 | 141.3048 | 142.0547 | 143.1824 | 147.738 | 157.2195 | 166.7098 | 226.2499 | 255.9809 | 255.9809 | 263.9545 | 269.1081 | 274.0008 | 275.763 | 277.9169 | 280.993 | 286.61 | 300.7216 | 313.5166 | 0.036013 | 0.075863 | 0.12298 | 0.17585 | 0.23009 | 0.28968 | 0.35638 | 0.49949 | 0.62072 | 0.73422 | -0.35129 | -0.44364 | -0.54558 | -0.64658 | -0.73709 | -0.82061 | -0.90101 | -0.99489 | -1.0898 | -1.1744
Howrah Zone | 22330 | 7.3419 | 11.3584 | 11.3584 | 11.5314 | 11.9414 | 12.2286 | 12.291 | 12.3562 | 12.4543 | 12.8505 | 13.6753 | 14.5007 | 13.665 | 13.7154 | 13.7154 | 14.1426 | 14.4187 | 14.6809 | 14.7753 | 14.8907 | 15.0555 | 15.3565 | 16.1126 | 16.7981 | 0.0020333 | 0.0042625 | 0.0069201 | 0.0099315 | 0.013048 | 0.016494 | 0.020388 | 0.028751 | 0.035861 | 0.042535 | -0.01867 | -0.023872 | -0.02966 | -0.035447 | -0.040684 | -0.045562 | -0.050301 | -0.055876 | -0.061574 | -0.066701
Howrah Zone | 22331 | 110.8226 | 134.2434 | 134.2434 | 136.2879 | 141.1336 | 144.5275 | 145.2649 | 146.0358 | 147.1951 | 151.8784 | 161.6256 | 171.3819 | 217.1236 | 215.9798 | 215.9798 | 222.7074 | 227.0556 | 231.1838 | 232.6706 | 234.4879 | 237.0833 | 241.8226 | 253.729 | 264.5246 | 0.037847 | 0.079732 | 0.12926 | 0.18483 | 0.24184 | 0.30448 | 0.37459 | 0.52502 | 0.65245 | 0.77175 | -0.36902 | -0.46609 | -0.57325 | -0.67942 | -0.77457 | -0.86237 | -0.94689 | -1.0456 | -1.1454 | -1.2344
Huon River | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026215 | 0.00050237 | 0.00078565 | 0.0011076 | 0.0014439 | 0.0018224 | 0.0022516 | 0.0031885 | 0.0039825 | 0.0047358 | -0.0025183 | -0.0030478 | -0.003618 | -0.0041619 | -0.004628 | -0.0050347 | -0.0054034 | -0.0057548 | -0.0061269 | -0.0064464
Huon River | 38423 | 56.8 | 120.0656 | 120.0656 | 121.8942 | 126.2281 | 129.2636 | 129.9231 | 130.6126 | 131.6495 | 135.8382 | 144.5559 | 153.2818 | 67.0939 | 118.3379 | 118.3379 | 122.0241 | 124.4066 | 126.6684 | 127.483 | 128.4788 | 129.9009 | 132.4975 | 139.0212 | 144.9362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | 31002 | 105.8712 | 121.7173 | 121.7173 | 123.5711 | 127.9646 | 131.0418 | 131.7104 | 132.4094 | 133.4605 | 137.7068 | 146.5445 | 155.3904 | 119.7788 | 115.2159 | 115.2159 | 118.8048 | 121.1244 | 123.3266 | 124.1197 | 125.0892 | 126.4738 | 129.0019 | 135.3535 | 141.1125 | 0.022521 | 0.043303 | 0.067783 | 0.095565 | 0.12455 | 0.15714 | 0.19408 | 0.27465 | 0.34296 | 0.40776 | -0.21488 | -0.26064 | -0.30985 | -0.35675 | -0.39689 | -0.43187 | -0.46354 | -0.49369 | -0.52562 | -0.55302
Kermandie | 31007 | 93.3669 | 100.7228 | 100.7228 | 102.2568 | 105.8925 | 108.4389 | 108.9922 | 109.5706 | 110.4405 | 113.9543 | 121.2676 | 128.5877 | 138.8775 | 127.601 | 127.601 | 131.5757 | 134.1446 | 136.5835 | 137.4619 | 138.5356 | 140.069 | 142.8689 | 149.9033 | 156.2813 | 0.051332 | 0.10244 | 0.16217 | 0.22903 | 0.29791 | 0.3744 | 0.4602 | 0.64523 | 0.80153 | 0.94873 | -0.5206 | -0.63315 | -0.75358 | -0.86751 | -0.96442 | -1.0483 | -1.1236 | -1.1961 | -1.2711 | -1.3342
Kermandie | 31008 | 129.0743 | 134.7443 | 134.7443 | 136.7964 | 141.6602 | 145.0667 | 145.8069 | 146.5806 | 147.7443 | 152.4451 | 162.2286 | 172.0213 | 164.0761 | 148.9926 | 148.9926 | 153.6336 | 156.6333 | 159.481 | 160.5067 | 161.7604 | 163.5508 | 166.8202 | 175.0338 | 182.481 | 0.053798 | 0.10734 | 0.17036 | 0.2417 | 0.31593 | 0.39908 | 0.49298 | 0.69699 | 0.86941 | 1.0324 | -0.5359 | -0.65414 | -0.78134 | -0.9024 | -1.006 | -1.0961 | -1.1775 | -1.2552 | -1.3367 | -1.4062
Kermandie | 31010 | 59.4876 | 69.9535 | 69.9535 | 71.0188 | 73.5439 | 75.3124 | 75.6967 | 76.0984 | 76.7025 | 79.143 | 84.2222 | 89.3061 | 81.8584 | 77.7584 | 77.7584 | 80.1805 | 81.746 | 83.2322 | 83.7675 | 84.4218 | 85.3562 | 87.0625 | 91.3491 | 95.2358 | 0.024333 | 0.048174 | 0.075946 | 0.10692 | 0.13873 | 0.17397 | 0.21343 | 0.29839 | 0.3701 | 0.43757 | -0.24684 | -0.29909 | -0.35482 | -0.40735 | -0.45186 | -0.49025 | -0.52457 | -0.5575 | -0.59145 | -0.61986
Kingston (11 kV) | 34251 | 76.7946 | 107.9202 | 107.9202 | 109.5638 | 113.4593 | 116.1877 | 116.7805 | 117.4002 | 118.3323 | 122.0972 | 129.9331 | 137.7763 | 159.9076 | 133.6278 | 133.6278 | 137.7902 | 140.4805 | 143.0346 | 143.9545 | 145.0789 | 146.6847 | 149.6169 | 156.9834 | 163.6627 | 0.037144 | 0.074473 | 0.1176 | 0.1644 | 0.21105 | 0.26095 | 0.31538 | 0.42992 | 0.52751 | 0.61828 | -0.36205 | -0.44727 | -0.53967 | -0.62955 | -0.70868 | -0.78067 | -0.84901 | -0.93012 | -1.01 | -1.0808
Kingston (11 kV) | 34252 | 132.5824 | 200.8277 | 200.8277 | 203.8863 | 211.1354 | 216.2127 | 217.3159 | 218.4691 | 220.2035 | 227.2097 | 241.7914 | 256.3868 | 301.7398 | 286.1465 | 286.1465 | 295.0598 | 300.8207 | 306.2899 | 308.2598 | 310.6675 | 314.1062 | 320.3851 | 336.1596 | 350.4624 | 0.068902 | 0.13677 | 0.21646 | 0.30529 | 0.39606 | 0.49559 | 0.60617 | 0.84268 | 1.0442 | 1.2332 | -0.64568 | -0.80101 | -0.97082 | -1.137 | -1.2839 | -1.4175 | -1.5441 | -1.6877 | -1.8327 | -1.9612
Kingston (11 kV) | 34253 | 63.0525 | 96.3112 | 96.3112 | 97.778 | 101.2544 | 103.6893 | 104.2184 | 104.7714 | 105.6032 | 108.9632 | 115.9561 | 122.9556 | 152.879 | 138.1912 | 138.1912 | 142.4957 | 145.2779 | 147.9192 | 148.8705 | 150.0333 | 151.6939 | 154.7263 | 162.3444 | 169.2518 | 0.03634 | 0.072705 | 0.11477 | 0.16047 | 0.20601 | 0.25471 | 0.30776 | 0.41969 | 0.51485 | 0.60329 | -0.36497 | -0.44845 | -0.53921 | -0.62782 | -0.70612 | -0.77765 | -0.84582 | -0.92739 | -1.0075 | -1.0787
Kingston (11 kV) | 34254 | 11.25 | 14.985 | 14.985 | 15.2132 | 15.7541 | 16.133 | 16.2153 | 16.3013 | 16.4307 | 16.9535 | 18.0415 | 19.1306 | 21.0787 | 18.6547 | 18.6547 | 19.2357 | 19.6113 | 19.9679 | 20.0963 | 20.2533 | 20.4774 | 20.8868 | 21.9151 | 22.8476 | 3.8243e-05 | 7.5287e-05 | 0.00011753 | 0.00016269 | 0.00020714 | 0.00025426 | 0.00030536 | 0.00041054 | 0.00050108 | 0.00058592 | -0.00080901 | -0.00089167 | -0.00098002 | -0.0010646 | -0.0011377 | -0.0012032 | -0.0012644 | -0.001336 | -0.0014062 | -0.001467
Kingston (11 kV) | 34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34256 | 79.5259 | 108.7907 | 108.7907 | 110.4475 | 114.3745 | 117.1249 | 117.7225 | 118.3472 | 119.2868 | 123.0821 | 130.9812 | 138.8876 | 180.66 | 151.681 | 151.681 | 156.4058 | 159.4595 | 162.3587 | 163.4029 | 164.6792 | 166.5019 | 169.8302 | 178.192 | 185.7737 | 0.041987 | 0.083923 | 0.1326 | 0.18579 | 0.23908 | 0.29638 | 0.35907 | 0.49185 | 0.6047 | 0.70978 | -0.3988 | -0.49511 | -0.6 | -0.70251 | -0.79317 | -0.87596 | -0.95486 | -1.0484 | -1.1409 | -1.2229
Kingston (11 kV) | 34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11 kV) | 34259 | 126.6845 | 178.7903 | 178.7903 | 181.5133 | 187.9669 | 192.487 | 193.4692 | 194.4958 | 196.0399 | 202.2773 | 215.2589 | 228.2527 | 278.2736 | 271.715 | 271.715 | 280.1787 | 285.6491 | 290.8425 | 292.713 | 294.9993 | 298.2645 | 304.2267 | 319.2057 | 332.7871 | 0.068943 | 0.13782 | 0.21746 | 0.30389 | 0.38998 | 0.48199 | 0.58222 | 0.79341 | 0.97312 | 1.1402 | -0.73034 | -0.88825 | -1.0598 | -1.2271 | -1.3749 | -1.5097 | -1.6381 | -1.7916 | -1.9417 | -2.0757
Kingston (11 kV) | 34260 | 62.4778 | 81.5748 | 81.5748 | 82.8172 | 85.7617 | 87.824 | 88.2721 | 88.7406 | 89.4451 | 92.2909 | 98.2139 | 104.1425 | 96.1227 | 96.1167 | 96.1167 | 99.1106 | 101.0457 | 102.8829 | 103.5445 | 104.3533 | 105.5083 | 107.6174 | 112.9161 | 117.7204 | 0.017034 | 0.033788 | 0.053416 | 0.075224 | 0.097446 | 0.12175 | 0.14871 | 0.20621 | 0.25526 | 0.30124 | -0.1763 | -0.21457 | -0.25633 | -0.29712 | -0.33313 | -0.36583 | -0.39681 | -0.43201 | -0.46725 | -0.49866
Kingston (11 kV) | 34261 | 52.5336 | 83.681 | 83.681 | 84.9555 | 87.976 | 90.0916 | 90.5513 | 91.0318 | 91.7545 | 94.6739 | 100.7498 | 106.8314 | 59.5616 | 92.1863 | 92.1863 | 95.0579 | 96.9138 | 98.6758 | 99.3105 | 100.0861 | 101.194 | 103.2168 | 108.2988 | 112.9066 | 0.016168 | 0.032092 | 0.050792 | 0.071636 | 0.092936 | 0.11629 | 0.14224 | 0.19774 | 0.24504 | 0.28938 | -0.15151 | -0.18796 | -0.2278 | -0.26679 | -0.30126 | -0.3326 | -0.36232 | -0.39601 | -0.43005 | -0.46018
Kingston (11 kV) | 34262 | 99.6386 | 113.2026 | 113.2026 | 114.9267 | 119.0129 | 121.8748 | 122.4967 | 123.1467 | 124.1244 | 128.0736 | 136.293 | 144.5201 | 151.3446 | 134.3063 | 134.3063 | 138.4898 | 141.1938 | 143.7608 | 144.6854 | 145.8155 | 147.4295 | 150.3766 | 157.7805 | 164.4937 | 0.010922 | 0.021676 | 0.034302 | 0.04837 | 0.062741 | 0.078495 | 0.095992 | 0.1334 | 0.16529 | 0.19518 | -0.1037 | -0.12831 | -0.1552 | -0.18152 | -0.20478 | -0.22592 | -0.24597 | -0.26871 | -0.29165 | -0.31198
Kingston (11 kV) | 34263 | 84.9726 | 98.6383 | 98.6383 | 100.1405 | 103.701 | 106.1947 | 106.7366 | 107.303 | 108.1549 | 111.596 | 118.7579 | 125.9266 | 157.8801 | 129.71 | 129.71 | 133.7503 | 136.3617 | 138.841 | 139.7339 | 140.8253 | 142.384 | 145.2303 | 152.3808 | 158.8643 | 0.036655 | 0.072794 | 0.11508 | 0.16194 | 0.20958 | 0.26157 | 0.31911 | 0.44173 | 0.54629 | 0.6442 | -0.37304 | -0.45566 | -0.54581 | -0.63387 | -0.71163 | -0.78233 | -0.84935 | -0.92602 | -1.0027 | -1.0709
Kingston (11 kV) | 34264 | 175.1218 | 173.4732 | 173.4732 | 176.1152 | 182.3769 | 186.7626 | 187.7155 | 188.7116 | 190.2098 | 196.2617 | 208.8572 | 221.4646 | 145.964 | 192.6233 | 192.6233 | 198.6233 | 202.5014 | 206.1831 | 207.5091 | 209.1299 | 211.4447 | 215.6714 | 226.2902 | 235.9184 | 0.13422 | 0.17776 | 0.22881 | 0.28624 | 0.34564 | 0.41187 | 0.48648 | 0.64801 | 0.78499 | 0.91457 | -0.54621 | -0.64239 | -0.7458 | -0.8445 | -0.92924 | -1.0035 | -1.0713 | -1.1392 | -1.211 | -1.2716
Knights Road | 30603 | 188.4494 | 190.4302 | 190.4302 | 193.3304 | 200.2042 | 205.0186 | 206.0647 | 207.1582 | 208.8028 | 215.4462 | 229.273 | 243.1127 | 263.8683 | 237.708 | 237.708 | 245.1124 | 249.8981 | 254.4415 | 256.0779 | 258.0781 | 260.9347 | 266.1507 | 279.2549 | 291.1365 | 0.06297 | 0.12067 | 0.18871 | 0.26605 | 0.34683 | 0.43774 | 0.54083 | 0.76587 | 0.95659 | 1.1375 | -0.60489 | -0.73209 | -0.86904 | -0.99969 | -1.1117 | -1.2093 | -1.2979 | -1.3823 | -1.4717 | -1.5484
Knights Road | 30604 | 237.632 | 275.2599 | 275.2599 | 279.4521 | 289.3879 | 296.3469 | 297.859 | 299.4396 | 301.8169 | 311.4197 | 331.4058 | 351.4106 | 257.0131 | 240.3646 | 240.3646 | 247.8517 | 252.6909 | 257.2851 | 258.9398 | 260.9623 | 263.8508 | 269.1251 | 282.3758 | 294.3902 | 0.031884 | 0.061098 | 0.095549 | 0.1347 | 0.1756 | 0.22162 | 0.27381 | 0.38772 | 0.48426 | 0.57585 | -0.3063 | -0.3707 | -0.44004 | -0.50618 | -0.56286 | -0.61231 | -0.65714 | -0.69985 | -0.7451 | -0.78393
Knights Road | 30605 | 113.9057 | 160.6324 | 160.6324 | 163.0788 | 168.877 | 172.9381 | 173.8205 | 174.7429 | 176.1301 | 181.734 | 193.3973 | 205.0714 | 194.1739 | 174.2083 | 174.2083 | 179.6348 | 183.1421 | 186.4718 | 187.671 | 189.1369 | 191.2304 | 195.053 | 204.6567 | 213.3643 | 0.054457 | 0.10399 | 0.16175 | 0.22644 | 0.29319 | 0.36754 | 0.4512 | 0.63245 | 0.78553 | 0.93006 | -0.53441 | -0.64216 | -0.75693 | -0.86502 | -0.95648 | -1.0353 | -1.1057 | -1.1723 | -1.2418 | -1.3
Knights Road | 30606 | 106.6526 | 164.8605 | 164.8605 | 167.3713 | 173.3221 | 177.49 | 178.3957 | 179.3423 | 180.7661 | 186.5175 | 198.4877 | 210.4691 | 183.1226 | 166.9707 | 166.9707 | 172.1717 | 175.5333 | 178.7247 | 179.8741 | 181.279 | 183.2855 | 186.9494 | 196.154 | 204.4999 | 0.057825 | 0.11196 | 0.17557 | 0.24754 | 0.32243 | 0.4065 | 0.50167 | 0.70906 | 0.88502 | 1.0519 | -0.54096 | -0.65978 | -0.78728 | -0.90843 | -1.0118 | -1.1017 | -1.1829 | -1.2599 | -1.3416 | -1.4115
Knights Road | 30607 | 89.0741 | 113.1053 | 113.1053 | 114.8279 | 118.9106 | 121.77 | 122.3914 | 123.0408 | 124.0176 | 127.9635 | 136.1759 | 144.3959 | 155.6247 | 150.1625 | 150.1625 | 154.8399 | 157.8631 | 160.7332 | 161.767 | 163.0305 | 164.835 | 168.13 | 176.4081 | 183.9138 | 0.19681 | 0.27357 | 0.36375 | 0.46589 | 0.57237 | 0.69214 | 0.82798 | 1.1247 | 1.3764 | 1.6154 | -0.87329 | -1.0409 | -1.2202 | -1.39 | -1.5343 | -1.659 | -1.7708 | -1.8744 | -1.9876 | -2.0815
Knights Road | 30608 | 203.6921 | 153.9162 | 203.2633 | 206.359 | 213.696 | 218.8348 | 219.9514 | 221.1186 | 222.874 | 229.9652 | 244.7237 | 259.4961 | 244.348 | 121.6015 | 165.0089 | 170.1488 | 173.4709 | 176.6248 | 177.7607 | 179.1492 | 181.1321 | 184.7529 | 193.8494 | 202.0972 | 0.042312 | 0.081083 | 0.1268 | 0.17877 | 0.23305 | 0.29413 | 0.36341 | 0.51462 | 0.64277 | 0.76435 | -0.40645 | -0.49192 | -0.58394 | -0.67173 | -0.74697 | -0.81261 | -0.87211 | -0.92882 | -0.98888 | -1.0404
Meadowbank | 45001 | 82.911 | 84.829 | 84.829 | 86.1209 | 89.1829 | 91.3275 | 91.7935 | 92.2806 | 93.0132 | 95.9726 | 102.1319 | 108.2969 | 24.6014 | 48.6008 | 48.6008 | 50.1146 | 51.0931 | 52.022 | 52.3566 | 52.7656 | 53.3496 | 54.416 | 57.0953 | 59.5246 | 0.0067945 | 0.013551 | 0.022189 | 0.033488 | 0.046755 | 0.063298 | 0.083379 | 0.13088 | 0.1704 | 0.20877 | -0.057142 | -0.070578 | -0.084997 | -0.098148 | -0.10861 | -0.11643 | -0.12215 | -0.11935 | -0.11992 | -0.11911
Meadowbank | 45002 | 97.2198 | 81.5663 | 81.5663 | 82.8086 | 85.7528 | 87.8149 | 88.263 | 88.7314 | 89.4358 | 92.2814 | 98.2037 | 104.1317 | 64.7581 | 62.1822 | 62.1822 | 64.1191 | 65.371 | 66.5595 | 66.9876 | 67.5108 | 68.2581 | 69.6225 | 73.0505 | 76.1586 | 0.026396 | 0.054646 | 0.089093 | 0.13044 | 0.1757 | 0.2288 | 0.29073 | 0.43058 | 0.54807 | 0.6605 | -0.25437 | -0.31573 | -0.3825 | -0.44638 | -0.50101 | -0.54796 | -0.58972 | -0.62136 | -0.6591 | -0.69041
Meadowbank | 45003 | 98.8938 | 122.8933 | 122.8933 | 124.7649 | 129.2009 | 132.3078 | 132.9829 | 133.6886 | 134.7499 | 139.0373 | 147.9603 | 156.8917 | 71.7321 | 73.7317 | 73.7317 | 76.0284 | 77.5128 | 78.9221 | 79.4297 | 80.0501 | 80.9361 | 82.554 | 86.6186 | 90.3041 | 0.030144 | 0.060118 | 0.09844 | 0.14857 | 0.20743 | 0.28082 | 0.36991 | 0.58063 | 0.75597 | 0.92621 | -0.25351 | -0.31312 | -0.37708 | -0.43543 | -0.48182 | -0.51652 | -0.54192 | -0.5295 | -0.53203 | -0.52842
Mowbray | 62004 | 106.1224 | 120.9708 | 120.9708 | 122.8132 | 127.1798 | 130.2381 | 130.9027 | 131.5973 | 132.642 | 136.8623 | 145.6458 | 154.4374 | 235.254 | 195.6144 | 195.6144 | 201.7076 | 205.6459 | 209.3847 | 210.7313 | 212.3773 | 214.728 | 219.0204 | 229.8041 | 239.5817 | 0.041863 | 0.087154 | 0.14121 | 0.2026 | 0.26624 | 0.33665 | 0.41592 | 0.58605 | 0.72924 | 0.86267 | -0.47504 | -0.57989 | -0.69623 | -0.81177 | -0.91568 | -1.0116 | -1.104 | -1.2105 | -1.3175 | -1.414
Mowbray | 62005 | 117.1309 | 91.497 | 91.497 | 92.8905 | 96.1932 | 98.5064 | 99.009 | 99.5344 | 100.3246 | 103.5166 | 110.16 | 116.8097 | 179.3721 | 142.6364 | 142.6364 | 147.0795 | 149.9511 | 152.6774 | 153.6593 | 154.8595 | 156.5736 | 159.7034 | 167.5666 | 174.6962 | 0.023333 | 0.048577 | 0.078704 | 0.11292 | 0.1484 | 0.18764 | 0.23182 | 0.32665 | 0.40645 | 0.48082 | -0.26477 | -0.32321 | -0.38805 | -0.45245 | -0.51037 | -0.56385 | -0.61536 | -0.67469 | -0.73435 | -0.78809
Mowbray | 62006 | 82.9991 | 107.5015 | 107.5015 | 109.1387 | 113.0191 | 115.7369 | 116.3275 | 116.9448 | 117.8732 | 121.6235 | 129.429 | 137.2418 | 124.2509 | 126.5116 | 126.5116 | 130.4523 | 132.9994 | 135.4175 | 136.2884 | 137.3529 | 138.8732 | 141.6492 | 148.6235 | 154.9471 | 0.038123 | 0.076243 | 0.12137 | 0.1721 | 0.22424 | 0.28153 | 0.34546 | 0.48251 | 0.59753 | 0.7044 | -0.3975 | -0.48522 | -0.5818 | -0.67689 | -0.76164 | -0.83924 | -0.91331 | -0.99821 | -1.0828 | -1.1581
Mowbray | 62008 | 54.6066 | 70.5181 | 70.5181 | 71.5921 | 74.1375 | 75.9203 | 76.3077 | 76.7127 | 77.3217 | 79.7818 | 84.902 | 90.027 | 115.6514 | 105.5028 | 105.5028 | 108.7891 | 110.9132 | 112.9297 | 113.656 | 114.5437 | 115.8115 | 118.1266 | 123.9427 | 129.2161 | 0.038564 | 0.080274 | 0.13005 | 0.18659 | 0.24519 | 0.31002 | 0.383 | 0.53966 | 0.67149 | 0.79435 | -0.43746 | -0.53401 | -0.64115 | -0.74755 | -0.84322 | -0.93158 | -1.0167 | -1.1147 | -1.2132 | -1.302
Mowbray | 62009 | 110.2171 | 126.0254 | 141.2091 | 127.9448 | 132.4938 | 135.6799 | 136.3722 | 137.0959 | 138.1843 | 142.5809 | 151.7313 | 160.8904 | 139.7405 | 129.5675 | 142.9237 | 133.6035 | 136.212 | 138.6885 | 139.5805 | 140.6707 | 142.2277 | 145.0708 | 152.2135 | 158.6899 | 0.032306 | 0.063657 | 0.10064 | 0.14206 | 0.18447 | 0.23093 | 0.28259 | 0.39328 | 0.48606 | 0.57215 | -0.32614 | -0.39811 | -0.47709 | -0.55459 | -0.6234 | -0.68617 | -0.74586 | -0.81413 | -0.88194 | -0.94194
Mowbray | 62010 | 71.4217 | 75.216 | 75.216 | 76.3615 | 79.0765 | 80.9781 | 81.3913 | 81.8232 | 82.4728 | 85.0968 | 90.5581 | 96.0245 | 132.5054 | 116.2153 | 116.2153 | 119.8353 | 122.1751 | 124.3963 | 125.1964 | 126.1742 | 127.5708 | 130.1209 | 136.5276 | 142.3365 | 0.0556 | 0.11575 | 0.18753 | 0.26906 | 0.35358 | 0.44708 | 0.55234 | 0.77827 | 0.96841 | 1.1456 | -0.63086 | -0.7701 | -0.9246 | -1.078 | -1.216 | -1.3435 | -1.4662 | -1.6075 | -1.7497 | -1.8777
Mowbray | 62013 | 131.8928 | 152.4703 | 152.4703 | 154.7924 | 160.296 | 164.1507 | 164.9883 | 165.8638 | 167.1806 | 172.4997 | 183.5703 | 194.6512 | 172.8936 | 184.4124 | 184.4124 | 190.1567 | 193.8695 | 197.3942 | 198.6637 | 200.2154 | 202.4316 | 206.4781 | 216.6443 | 225.862 | 0.035237 | 0.072872 | 0.11773 | 0.1686 | 0.22125 | 0.27945 | 0.34488 | 0.48529 | 0.60341 | 0.71343 | -0.39436 | -0.4814 | -0.57786 | -0.67354 | -0.75945 | -0.83869 | -0.9149 | -1.0026 | -1.0907 | -1.1699
New Norfolk | 39010 | 40 | 82.246 | 82.246 | 83.4986 | 86.4673 | 88.5467 | 88.9985 | 89.4707 | 90.181 | 93.0503 | 99.022 | 104.9993 | 79.9371 | 76.6039 | 76.6039 | 78.99 | 80.5323 | 81.9964 | 82.5238 | 83.1684 | 84.0889 | 85.7698 | 89.9928 | 93.8218 | 0.035099 | 0.070001 | 0.11462 | 0.17299 | 0.24153 | 0.32698 | 0.43071 | 0.67608 | 0.88023 | 1.0785 | -0.29518 | -0.36459 | -0.43907 | -0.50701 | -0.56103 | -0.60142 | -0.631 | -0.61654 | -0.61949 | -0.61528
New Norfolk | 39011 | 35.874 | 28.0895 | 28.0895 | 28.5173 | 29.5312 | 30.2414 | 30.3957 | 30.557 | 30.7996 | 31.7795 | 33.819 | 35.8605 | 60.1749 | 26.5952 | 26.5952 | 27.4236 | 27.959 | 28.4673 | 28.6504 | 28.8742 | 29.1938 | 29.7774 | 31.2435 | 32.5728 | 0.029505 | 0.058845 | 0.096356 | 0.14542 | 0.20304 | 0.27487 | 0.36208 | 0.56834 | 0.73996 | 0.9066 | -0.24814 | -0.30649 | -0.3691 | -0.42621 | -0.47162 | -0.50558 | -0.53045 | -0.51829 | -0.52077 | -0.51723
New Norfolk | 39012 | 41.6 | 51.2237 | 51.2237 | 52.0038 | 53.8528 | 55.1478 | 55.4292 | 55.7233 | 56.1657 | 57.9527 | 61.672 | 65.3947 | 70.9038 | 63.4256 | 63.4256 | 65.4012 | 66.6782 | 67.8905 | 68.3271 | 68.8608 | 69.623 | 71.0147 | 74.5112 | 77.6815 | 0.020909 | 0.041701 | 0.068283 | 0.10306 | 0.14388 | 0.19479 | 0.25659 | 0.40276 | 0.52438 | 0.64247 | -0.17585 | -0.21719 | -0.26156 | -0.30203 | -0.33422 | -0.35828 | -0.3759 | -0.36729 | -0.36904 | -0.36654
New Norfolk | 39013 | 13.5648 | 72.0745 | 72.0745 | 73.1722 | 75.7738 | 77.596 | 77.9919 | 78.4058 | 79.0282 | 81.5427 | 86.7759 | 92.014 | 24.8062 | 68.8345 | 68.8345 | 70.9786 | 72.3644 | 73.6801 | 74.154 | 74.7332 | 75.5604 | 77.0708 | 80.8655 | 84.3061 | 0.014085 | 0.028079 | 0.045956 | 0.06931 | 0.096705 | 0.13084 | 0.17225 | 0.27016 | 0.35163 | 0.43073 | -0.11856 | -0.14642 | -0.17632 | -0.2036 | -0.22532 | -0.2416 | -0.25356 | -0.24804 | -0.24945 | -0.24798
New Norfolk | 39565 | 91.4 | 61.5554 | 61.5554 | 62.4929 | 64.7148 | 66.271 | 66.6091 | 66.9626 | 67.4942 | 69.6417 | 74.1111 | 78.5847 | 145.7121 | 30.7857 | 30.7857 | 31.7446 | 32.3645 | 32.9529 | 33.1648 | 33.4238 | 33.7938 | 34.4693 | 36.1665 | 37.7053 | 0.063403 | 0.12645 | 0.20705 | 0.3125 | 0.4363 | 0.59067 | 0.77805 | 1.2213 | 1.5901 | 1.9482 | -0.53322 | -0.6586 | -0.79314 | -0.91586 | -1.0135 | -1.0864 | -1.1398 | -1.1137 | -1.1191 | -1.1115
New Norfolk | 39568 | 24 | 133.8491 | 133.8491 | 135.8876 | 140.7191 | 144.103 | 144.8383 | 145.6069 | 146.7628 | 151.4324 | 161.1509 | 170.8785 | 27.4381 | 97.1913 | 97.1913 | 100.2187 | 102.1754 | 104.0331 | 104.7022 | 105.52 | 106.6879 | 108.8206 | 114.1785 | 119.0365 | 0.0086289 | 0.01788 | 0.029146 | 0.042634 | 0.057368 | 0.074616 | 0.094709 | 0.13999 | 0.17806 | 0.21446 | -0.083494 | -0.10364 | -0.12557 | -0.14658 | -0.16459 | -0.18011 | -0.19398 | -0.20478 | -0.2175 | -0.22812
New Norfolk | 39569 | 0 | 5.2202 | 5.2202 | 5.2997 | 5.4882 | 5.6202 | 5.6488 | 5.6788 | 5.7239 | 5.906 | 6.285 | 6.6644 | 0 | 3.0613 | 3.0613 | 3.1566 | 3.2183 | 3.2768 | 3.2979 | 3.3236 | 3.3604 | 3.4276 | 3.5963 | 3.7493 | 0.00018769 | 0.00037433 | 0.00061295 | 0.00092509 | 0.0012916 | 0.0017486 | 0.0023033 | 0.0036154 | 0.0047071 | 0.0057672 | -0.0015785 | -0.0019497 | -0.002348 | -0.0027113 | -0.0030002 | -0.0032162 | -0.0033743 | -0.003297 | -0.0033128 | -0.0032903
New Norfolk | 39570 | 209.3 | 61.5554 | 61.5554 | 62.4929 | 64.7148 | 66.271 | 66.6091 | 66.9626 | 67.4942 | 69.6417 | 74.1111 | 78.5847 | 149.5547 | 24.3461 | 24.3461 | 25.1045 | 25.5946 | 26.0599 | 26.2275 | 26.4324 | 26.725 | 27.2592 | 28.6013 | 29.8183 | 0.00090093 | 0.0017968 | 0.0029422 | 0.0044405 | 0.0061996 | 0.0083931 | 0.011056 | 0.017354 | 0.022594 | 0.027683 | -0.0075768 | -0.0093584 | -0.01127 | -0.013014 | -0.014401 | -0.015438 | -0.016197 | -0.015826 | -0.015901 | -0.015793
New Norfolk | 39571 | 108.5 | 136.9227 | 136.9227 | 139.008 | 143.9504 | 147.412 | 148.1641 | 148.9504 | 150.1329 | 154.9096 | 164.8514 | 174.8023 | 65.4886 | 83.2697 | 83.2697 | 85.8635 | 87.54 | 89.1316 | 89.7048 | 90.4054 | 91.4061 | 93.2333 | 97.8237 | 101.9859 | 0.032621 | 0.065059 | 0.10653 | 0.16078 | 0.22448 | 0.3039 | 0.40031 | 0.62836 | 0.8181 | 1.0023 | -0.27434 | -0.33885 | -0.40808 | -0.47122 | -0.52143 | -0.55897 | -0.58646 | -0.57302 | -0.57576 | -0.57185
New Town Zone | 16091 | 109.7905 | 204.1746 | 204.1746 | 207.2842 | 214.6541 | 219.8159 | 220.9375 | 222.11 | 223.8733 | 230.9962 | 245.821 | 260.6595 | 200.0731 | 192.905 | 192.905 | 198.9138 | 202.7975 | 206.4846 | 207.8126 | 209.4357 | 211.7539 | 215.9868 | 226.6212 | 236.2634 | 0.030325 | 0.064474 | 0.10545 | 0.15244 | 0.20161 | 0.25693 | 0.31977 | 0.45594 | 0.57095 | 0.67926 | -0.29341 | -0.37256 | -0.46071 | -0.54885 | -0.62857 | -0.70269 | -0.77459 | -0.85792 | -0.94303 | -1.0189
New Town Zone | 16092 | 88.4179 | 101.9958 | 101.9958 | 103.5492 | 107.2309 | 109.8095 | 110.3698 | 110.9554 | 111.8363 | 115.3946 | 122.8003 | 130.213 | 134.7257 | 124.3008 | 124.3008 | 128.1726 | 130.6752 | 133.051 | 133.9067 | 134.9526 | 136.4463 | 139.1738 | 146.0262 | 152.2393 | 0.016803 | 0.035726 | 0.05843 | 0.084471 | 0.11171 | 0.14237 | 0.17719 | 0.25264 | 0.31637 | 0.37639 | -0.16258 | -0.20644 | -0.25529 | -0.30413 | -0.3483 | -0.38937 | -0.42921 | -0.47539 | -0.52254 | -0.56461
New Town Zone | 16093 | 91.9957 | 99.8961 | 99.8961 | 101.4175 | 105.0234 | 107.5489 | 108.0977 | 108.6713 | 109.5341 | 113.0191 | 120.2724 | 127.5324 | 126.7117 | 121.7731 | 121.7731 | 125.5662 | 128.0179 | 130.3454 | 131.1837 | 132.2083 | 133.6717 | 136.3437 | 143.0568 | 149.1435 | 0.0075352 | 0.016021 | 0.026202 | 0.03788 | 0.050096 | 0.063844 | 0.079459 | 0.11329 | 0.14187 | 0.16879 | -0.072907 | -0.092574 | -0.11448 | -0.13638 | -0.15619 | -0.17461 | -0.19247 | -0.21318 | -0.23433 | -0.25319
New Town Zone | 16094 | 149.409 | 176.1984 | 176.1984 | 178.8819 | 185.242 | 189.6965 | 190.6645 | 191.6762 | 193.1979 | 199.3449 | 212.1383 | 224.9437 | 239.9016 | 224.1721 | 224.1721 | 231.1548 | 235.668 | 239.9527 | 241.496 | 243.3822 | 246.0761 | 250.9951 | 263.3531 | 274.5582 | 0.028352 | 0.060267 | 0.098557 | 0.14247 | 0.1884 | 0.24009 | 0.2988 | 0.426 | 0.53344 | 0.63462 | -0.27411 | -0.34807 | -0.43044 | -0.51279 | -0.58726 | -0.65649 | -0.72365 | -0.80147 | -0.88093 | -0.95181
New Town Zone | 16095 | 70.1719 | 79.1082 | 79.1082 | 80.313 | 170.9652 | 175.0764 | 175.9697 | 176.9035 | 178.308 | 183.9812 | 195.7886 | 207.6071 | 85.1085 | 77.8075 | 77.8075 | 80.2311 | 159.0235 | 161.9147 | 162.956 | 164.2289 | 166.0466 | 169.3659 | 177.7048 | 185.2657 | 0.0049461 | 0.010371 | 0.016843 | 0.02422 | 0.031898 | 0.040505 | 0.050257 | 0.071355 | 0.089105 | 0.10576 | -0.045561 | -0.058057 | -0.071887 | -0.085615 | -0.097937 | -0.10931 | -0.12026 | -0.13286 | -0.14564 | -0.15688
New Town Zone | 16096 | 129.9045 | 133.7864 | 133.7864 | 135.8239 | 140.6531 | 144.0354 | 144.7704 | 145.5386 | 146.694 | 151.3614 | 161.0753 | 170.7984 | 209.6802 | 207.9665 | 207.9665 | 214.4445 | 218.6314 | 222.6064 | 224.038 | 225.7879 | 228.2871 | 232.8505 | 244.3152 | 254.7102 | 0.032885 | 0.067591 | 0.10898 | 0.15632 | 0.20576 | 0.26156 | 0.32488 | 0.46268 | 0.57817 | 0.68594 | -0.30589 | -0.38503 | -0.47218 | -0.55811 | -0.63465 | -0.70465 | -0.77142 | -0.84648 | -0.92222 | -0.98775
New Town Zone | 16097 | 50.0269 | 60.5403 | 60.5403 | 61.4624 | 63.6476 | 65.1782 | 65.5108 | 65.8584 | 66.3812 | 68.4933 | 72.889 | 77.2888 | 58.6549 | 64.326 | 64.326 | 66.3297 | 67.6248 | 68.8543 | 69.2971 | 69.8384 | 70.6114 | 72.0229 | 75.569 | 78.7843 | 0.0063577 | 0.013246 | 0.021442 | 0.030755 | 0.040424 | 0.051244 | 0.063488 | 0.089955 | 0.11218 | 0.133 | -0.057219 | -0.073039 | -0.090495 | -0.10776 | -0.1232 | -0.1374 | -0.15101 | -0.16665 | -0.18241 | -0.19619
New Town Zone | 16098 | 118.6355 | 210.752 | 210.752 | 213.9617 | 221.5691 | 226.8972 | 228.0549 | 229.2651 | 231.0853 | 238.4376 | 253.74 | 269.0566 | 236.3545 | 220.8741 | 220.8741 | 227.7542 | 232.201 | 236.4226 | 237.9431 | 239.8017 | 242.4559 | 247.3025 | 259.4788 | 270.519 | 0.032431 | 0.068106 | 0.11071 | 0.15932 | 0.20996 | 0.26679 | 0.33121 | 0.47063 | 0.588 | 0.69817 | -0.30128 | -0.38351 | -0.4746 | -0.56511 | -0.64643 | -0.72154 | -0.79394 | -0.8773 | -0.96193 | -1.0365
Newton | 96202 | 100.0687 | 119.8443 | 119.8443 | 121.6695 | 125.9954 | 129.0253 | 129.6836 | 130.3718 | 131.4068 | 135.5878 | 144.2894 | 152.9992 | 99.7231 | 110.8119 | 110.8119 | 114.2636 | 116.4945 | 118.6125 | 119.3754 | 120.3078 | 121.6394 | 124.0709 | 130.1797 | 135.7186 | 1.8738e-05 | 3.8838e-05 | 6.4843e-05 | 9.8929e-05 | 0.00013875 | 0.00018787 | 0.00024683 | 0.00038464 | 0.00049784 | 0.00060605 | -0.00016123 | -0.00020268 | -0.00024863 | -0.00029287 | -0.00033085 | -0.00036297 | -0.00039111 | -0.00040442 | -0.00042529 | -0.00044116
North Hobart | 18131A | 150.3335 | 171.8331 | 171.8331 | 174.45 | 180.6526 | 184.9968 | 185.9407 | 186.9274 | 188.4114 | 194.4061 | 206.8826 | 219.3707 | 177.411 | 165.244 | 165.244 | 170.3912 | 173.718 | 176.8764 | 178.014 | 179.4044 | 181.3901 | 185.0161 | 194.1256 | 202.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18131B | 179.3845 | 186.2081 | 186.2081 | 189.0441 | 195.7655 | 200.4731 | 201.496 | 202.5653 | 204.1734 | 210.6696 | 224.1898 | 237.7226 | 183.4511 | 195.3167 | 195.3167 | 201.4007 | 205.333 | 209.0661 | 210.4107 | 212.0542 | 214.4013 | 218.6871 | 229.4544 | 239.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18132A | 11.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6351 | 1.6359 | 1.6359 | 1.6868 | 1.7198 | 1.751 | 1.7623 | 1.7761 | 1.7957 | 1.8316 | 1.9218 | 2.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18132B | 55.664 | 73.1922 | 73.1922 | 74.3069 | 76.9489 | 78.7993 | 79.2013 | 79.6216 | 80.2537 | 82.8071 | 88.1215 | 93.4408 | 57.5111 | 60.7042 | 60.7042 | 62.5951 | 63.8173 | 64.9775 | 65.3954 | 65.9062 | 66.6357 | 67.9677 | 71.3142 | 74.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18133A | 53.2262 | 69.0595 | 69.0595 | 70.1113 | 72.604 | 74.35 | 74.7293 | 75.1259 | 75.7223 | 78.1316 | 83.1458 | 88.1648 | 55.9773 | 57.0527 | 57.0527 | 58.8298 | 59.9785 | 61.0689 | 61.4617 | 61.9417 | 62.6273 | 63.8793 | 67.0244 | 69.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18133B | 30.2699 | 39.0598 | 39.0598 | 39.6547 | 41.0646 | 42.0521 | 42.2667 | 42.4909 | 42.8283 | 44.1909 | 47.027 | 49.8657 | 45.4852 | 53.5813 | 53.5813 | 55.2503 | 56.329 | 57.3532 | 57.722 | 58.1729 | 58.8168 | 59.9925 | 62.9463 | 65.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18134A | 41.6464 | 61.7085 | 61.7085 | 62.6483 | 64.8757 | 66.4358 | 66.7748 | 67.1292 | 67.6621 | 69.8149 | 74.2954 | 78.7802 | 236.3509 | 59.4684 | 59.4684 | 61.3208 | 62.5181 | 63.6548 | 64.0641 | 64.5645 | 65.2792 | 66.5841 | 69.8624 | 72.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18134B | 20.5965 | 32.8408 | 32.8408 | 33.341 | 34.5264 | 35.3567 | 35.5371 | 35.7257 | 36.0093 | 37.155 | 39.5395 | 41.9262 | 50.3073 | 48.1716 | 48.1716 | 49.6721 | 50.642 | 51.5627 | 51.8943 | 52.2996 | 52.8785 | 53.9356 | 56.5911 | 58.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18135A | 15.4397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18135B | 78.2141 | 83.7318 | 83.7318 | 85.007 | 88.0294 | 90.1463 | 90.6063 | 91.0871 | 91.8102 | 94.7313 | 100.8109 | 106.8962 | 116.4289 | 123.2947 | 123.2947 | 127.1352 | 129.6175 | 131.9741 | 132.8228 | 133.8603 | 135.3419 | 138.0474 | 144.8443 | 151.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18136A | 53.4221 | 67.7662 | 67.7662 | 68.7982 | 71.2443 | 72.9576 | 73.3298 | 73.719 | 74.3042 | 76.6683 | 81.5887 | 86.5137 | 113.9829 | 107.738 | 107.738 | 111.094 | 113.263 | 115.3223 | 116.0639 | 116.9705 | 118.2652 | 120.6293 | 126.5686 | 131.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18136B | 0 | 2.0663 | 2.0663 | 2.0978 | 2.1724 | 2.2246 | 2.236 | 2.2479 | 2.2657 | 2.3378 | 2.4878 | 2.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141B | 107.4681 | 146.0974 | 146.0974 | 148.3224 | 153.596 | 157.2895 | 158.0921 | 158.931 | 160.1928 | 165.2896 | 175.8974 | 186.5152 | 163.9327 | 167.0021 | 167.0021 | 172.2041 | 175.5663 | 178.7583 | 179.9079 | 181.3132 | 183.32 | 186.9845 | 196.191 | 204.5384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18142A | 16.0687 | 30.9922 | 30.9922 | 31.4642 | 32.5829 | 33.3665 | 33.5367 | 33.7147 | 33.9823 | 35.0636 | 37.3138 | 39.5662 | 30.7138 | 30.3955 | 30.3955 | 31.3422 | 31.9542 | 32.5352 | 32.7444 | 33.0002 | 33.3654 | 34.0324 | 35.708 | 37.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18142B | 29.8635 | 34.5613 | 34.5613 | 35.0876 | 36.3352 | 37.2089 | 37.3988 | 37.5973 | 37.8957 | 39.1015 | 41.6109 | 44.1227 | 43.3004 | 41.3235 | 41.3235 | 42.6107 | 43.4427 | 44.2325 | 44.517 | 44.8647 | 45.3613 | 46.268 | 48.5461 | 50.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18143B | 121.5794 | 161.3021 | 161.3021 | 163.7587 | 169.5811 | 173.659 | 174.5451 | 175.4714 | 176.8644 | 182.4917 | 194.2035 | 205.9263 | 273.8031 | 222.4917 | 222.4917 | 229.4222 | 233.9016 | 238.1542 | 239.6858 | 241.5579 | 244.2316 | 249.1137 | 261.3791 | 272.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18144A | 55.2047 | 105.4468 | 105.4468 | 107.0527 | 110.859 | 113.5248 | 114.1041 | 114.7096 | 115.6202 | 119.2989 | 126.9552 | 134.6186 | 118.304 | 110.2015 | 110.2015 | 113.6342 | 115.8528 | 117.9592 | 118.7178 | 119.6451 | 120.9694 | 123.3875 | 129.4627 | 134.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18144B | 97.3105 | 110.9824 | 110.9824 | 112.6727 | 116.6787 | 119.4845 | 120.0942 | 120.7315 | 121.6899 | 125.5617 | 133.62 | 141.6857 | 154.5058 | 193.7611 | 193.7611 | 199.7966 | 203.6975 | 207.401 | 208.7348 | 210.3652 | 212.6937 | 216.9453 | 227.6269 | 237.3119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18145A | 50.6465 | 54.3967 | 54.3967 | 55.2252 | 57.1887 | 58.5639 | 58.8627 | 59.1751 | 59.6449 | 61.5426 | 65.4922 | 69.4456 | 71.3823 | 63.0367 | 63.0367 | 65.0003 | 66.2694 | 67.4742 | 67.9082 | 68.4386 | 69.1961 | 70.5793 | 74.0544 | 77.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18146A | 112.1463 | 127.6915 | 127.6915 | 129.6362 | 134.2454 | 137.4736 | 138.1751 | 138.9083 | 140.0111 | 144.4658 | 153.7373 | 163.0174 | 210.6488 | 179.4186 | 179.4186 | 185.0073 | 188.6196 | 192.0489 | 193.284 | 194.7937 | 196.9498 | 200.8867 | 210.7776 | 219.7457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18146B | 173.1726 | 187.537 | 187.537 | 190.3932 | 197.1625 | 201.9038 | 202.934 | 204.0109 | 205.6305 | 212.173 | 225.7897 | 239.4191 | 326.894 | 264.7212 | 264.7212 | 272.9671 | 278.2967 | 283.3564 | 285.1788 | 287.4062 | 290.5874 | 296.3962 | 310.9896 | 324.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | 65060 | 32.8824 | 9.788 | 9.788 | 9.937 | 10.2903 | 10.5378 | 10.5916 | 10.6478 | 10.7323 | 11.0738 | 11.7844 | 12.4958 | 22.9114 | 7.6577 | 7.6577 | 7.8962 | 8.0504 | 8.1968 | 8.2495 | 8.3139 | 8.4059 | 8.574 | 8.9961 | 9.3789 | 0.0078918 | 0.015453 | 0.024423 | 0.034534 | 0.044937 | 0.05638 | 0.069255 | 0.096682 | 0.11961 | 0.14088 | -0.087679 | -0.10514 | -0.12443 | -0.14351 | -0.16059 | -0.17632 | -0.19142 | -0.20896 | -0.22626 | -0.24175
Norwood | 65061 | 56.1284 | 126.1559 | 126.1559 | 128.0772 | 132.631 | 135.8204 | 136.5134 | 137.2379 | 138.3274 | 142.7285 | 151.8885 | 161.057 | 102.1521 | 101.9274 | 101.9274 | 105.1023 | 107.1544 | 109.1026 | 109.8043 | 110.6619 | 111.8868 | 114.1234 | 119.7424 | 124.8371 | 0.034417 | 0.067417 | 0.10658 | 0.15073 | 0.19617 | 0.24618 | 0.30243 | 0.42228 | 0.52249 | 0.61548 | -0.38351 | -0.45975 | -0.54398 | -0.62731 | -0.70196 | -0.77069 | -0.83669 | -0.91341 | -0.98905 | -1.0568
Norwood | 65062 | 64.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048559 | 0.095058 | 0.15022 | 0.21238 | 0.27633 | 0.34667 | 0.4258 | 0.59436 | 0.7353 | 0.86597 | -0.53856 | -0.64594 | -0.76455 | -0.88183 | -0.98683 | -1.0835 | -1.1762 | -1.284 | -1.3902 | -1.4854
Norwood | 65063 | 25.4184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019528 | 0.037255 | 0.058059 | 0.081235 | 0.10488 | 0.13074 | 0.15932 | 0.22066 | 0.27197 | 0.31953 | -0.18567 | -0.22602 | -0.27 | -0.31277 | -0.35037 | -0.38432 | -0.41624 | -0.45211 | -0.48758 | -0.51855
Norwood | 65064 | 39.8226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.7133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040472 | 0.078152 | 0.12248 | 0.17194 | 0.22241 | 0.27755 | 0.33879 | 0.46964 | 0.57907 | 0.68038 | -0.40334 | -0.48971 | -0.58428 | -0.67684 | -0.75882 | -0.83344 | -0.90422 | -0.98532 | -1.0653 | -1.1358
Norwood | 65065 | 121.3804 | 152.9072 | 152.9072 | 155.2359 | 160.7553 | 164.621 | 165.461 | 166.339 | 167.6596 | 172.994 | 184.0963 | 195.209 | 188.9869 | 181.6533 | 181.6533 | 187.3117 | 190.9689 | 194.4409 | 195.6914 | 197.2199 | 199.4029 | 203.3889 | 213.403 | 222.4827 | 0.036126 | 0.070335 | 0.11095 | 0.15681 | 0.20411 | 0.25621 | 0.3149 | 0.44035 | 0.54519 | 0.64241 | -0.3998 | -0.47857 | -0.5655 | -0.65134 | -0.72806 | -0.79852 | -0.86597 | -0.94363 | -1.0204 | -1.089
Norwood | 65066 | 89.2 | 99.5636 | 99.5636 | 101.0799 | 104.6738 | 107.1909 | 107.7378 | 108.3096 | 109.1694 | 112.6428 | 119.872 | 127.1078 | 133.5239 | 129.0441 | 129.0441 | 133.0637 | 135.6617 | 138.1282 | 139.0166 | 140.1024 | 141.6531 | 144.4847 | 151.5986 | 158.0488 | 0.074519 | 0.13685 | 0.21087 | 0.29703 | 0.38921 | 0.49557 | 0.61818 | 0.89245 | 1.121 | 1.3383 | -0.88184 | -1.0131 | -1.1518 | -1.2798 | -1.385 | -1.4711 | -1.5433 | -1.5893 | -1.6439 | -1.6823
Norwood | 65067 | 50.2 | 60.3853 | 60.3853 | 61.305 | 63.4847 | 65.0113 | 65.343 | 65.6898 | 66.2113 | 68.3179 | 72.7024 | 77.091 | 66.2091 | 68.8843 | 68.8843 | 71.03 | 72.4168 | 73.7334 | 74.2076 | 74.7872 | 75.615 | 77.1265 | 80.9239 | 84.3671 | 0.043192 | 0.076936 | 0.11871 | 0.17131 | 0.2315 | 0.30522 | 0.3937 | 0.60109 | 0.77256 | 0.93804 | -0.34421 | -0.41019 | -0.47902 | -0.53967 | -0.58596 | -0.61865 | -0.64029 | -0.62238 | -0.61696 | -0.60443
Palmerston | 51001 | 29.7289 | 30.3443 | 30.3443 | 30.8065 | 31.9018 | 32.6689 | 32.8356 | 33.0099 | 33.2719 | 34.3305 | 36.5338 | 38.7391 | 30.9496 | 29.3789 | 29.3789 | 30.2941 | 30.8855 | 31.4471 | 31.6493 | 31.8965 | 32.2496 | 32.8942 | 34.5138 | 35.9823 | 0.00029553 | 0.00053156 | 0.00082427 | 0.0011863 | 0.0015925 | 0.0020794 | 0.0026548 | 0.003975 | 0.0050756 | 0.0061315 | -0.0032358 | -0.0037341 | -0.0042744 | -0.0047829 | -0.0052083 | -0.0055592 | -0.0058558 | -0.0059953 | -0.0062016 | -0.0063477
Palmerston | 51002 | 0 | 10.0298 | 10.0298 | 10.1825 | 10.5446 | 10.7981 | 10.8532 | 10.9108 | 10.9974 | 11.3474 | 12.0756 | 12.8045 | 0 | 7.9253 | 7.9253 | 8.1722 | 8.3318 | 8.4833 | 8.5378 | 8.6045 | 8.6997 | 8.8736 | 9.3106 | 9.7067 | 0.0028896 | 0.0051975 | 0.0080595 | 0.011599 | 0.015572 | 0.020332 | 0.025958 | 0.038867 | 0.049628 | 0.059952 | -0.031639 | -0.036511 | -0.041794 | -0.046766 | -0.050925 | -0.054357 | -0.057257 | -0.05862 | -0.060638 | -0.062066
Palmerston | 51003 | 189.1575 | 329.1639 | 296.8985 | 301.4202 | 312.1371 | 319.6431 | 321.2741 | 322.979 | 325.5431 | 335.9008 | 357.4581 | 379.0355 | 72.0805 | 225.4688 | 197.087 | 203.2261 | 207.194 | 210.961 | 212.3177 | 213.9761 | 216.3445 | 220.6692 | 231.5341 | 241.3853 | 0.017994 | 0.033316 | 0.052434 | 0.076477 | 0.10386 | 0.13715 | 0.17688 | 0.26915 | 0.3458 | 0.41961 | -0.18716 | -0.21853 | -0.25218 | -0.28316 | -0.30832 | -0.32806 | -0.34364 | -0.34518 | -0.35197 | -0.35512
Palmerston | 51004 | 89.957 | 105.0577 | 143.017 | 106.6577 | 110.4499 | 113.1059 | 113.683 | 114.2863 | 115.1936 | 118.8587 | 126.4867 | 134.1219 | 37.2187 | 36.7328 | 70.1232 | 37.877 | 38.6166 | 39.3187 | 39.5715 | 39.8806 | 40.322 | 41.1281 | 43.1531 | 44.9891 | 0.028202 | 0.053286 | 0.083235 | 0.118 | 0.15501 | 0.19734 | 0.24582 | 0.35305 | 0.443 | 0.52827 | -0.30673 | -0.36142 | -0.42033 | -0.47616 | -0.52359 | -0.56426 | -0.60033 | -0.63054 | -0.66374 | -0.69062
Port Latta | 94001 | 107.9383 | 124.8509 | 124.8509 | 126.7523 | 131.259 | 134.4154 | 135.1012 | 135.8182 | 136.8964 | 141.252 | 150.3172 | 159.3909 | 58.3877 | 61.6611 | 61.6611 | 63.5818 | 64.8232 | 66.0018 | 66.4263 | 66.9451 | 67.6861 | 69.0391 | 72.4383 | 75.5204 | 0.026235 | 0.053613 | 0.087709 | 0.13004 | 0.17764 | 0.23472 | 0.30213 | 0.45669 | 0.58531 | 0.70849 | -0.26227 | -0.32035 | -0.38371 | -0.44389 | -0.49484 | -0.53761 | -0.57457 | -0.59515 | -0.62348 | -0.64581
Port Latta | 94002 | 198.4134 | 206.6347 | 225.6143 | 209.7817 | 217.2404 | 222.4645 | 223.5996 | 224.7861 | 226.5707 | 233.7794 | 248.7828 | 263.8002 | 128.68 | 124.4682 | 141.1633 | 128.3452 | 130.8511 | 133.2301 | 134.087 | 135.1343 | 136.6301 | 139.3612 | 146.2229 | 152.4443 | 0.094982 | 0.18428 | 0.29494 | 0.43245 | 0.58758 | 0.77468 | 0.99681 | 1.5097 | 1.9368 | 2.3477 | -0.81433 | -0.9995 | -1.1982 | -1.382 | -1.5323 | -1.6518 | -1.7479 | -1.7702 | -1.8214 | -1.8531
Queenstown | 98001 | 42.51 | 56.7814 | 56.7814 | 57.6461 | 59.6957 | 61.1312 | 61.4432 | 61.7692 | 62.2596 | 64.2405 | 68.3633 | 72.4899 | 53.987 | 56.5659 | 56.5659 | 58.3278 | 59.4667 | 60.5478 | 60.9372 | 61.4132 | 62.093 | 63.3342 | 66.4525 | 69.2799 | 0.015455 | 0.030348 | 0.05112 | 0.08194 | 0.1212 | 0.17313 | 0.23822 | 0.39793 | 0.52812 | 0.65492 | -0.11285 | -0.13778 | -0.16414 | -0.18614 | -0.201 | -0.20768 | -0.20724 | -0.16811 | -0.14246 | -0.11353
Queenstown | 98002 | 44.6815 | 53.106 | 53.106 | 53.9148 | 55.8317 | 57.1743 | 57.466 | 57.771 | 58.2296 | 60.0823 | 63.9382 | 67.7978 | 60.6108 | 64.6424 | 64.6424 | 66.6559 | 67.9574 | 69.1929 | 69.6379 | 70.1818 | 70.9587 | 72.3771 | 75.9407 | 79.1718 | 0.015571 | 0.032275 | 0.053884 | 0.08221 | 0.1153 | 0.15612 | 0.20511 | 0.31964 | 0.41371 | 0.50363 | -0.13399 | -0.16843 | -0.20662 | -0.24338 | -0.27493 | -0.30163 | -0.32501 | -0.33607 | -0.35342 | -0.36661
Queenstown | 98003 | 26.7514 | 32.5074 | 32.5074 | 33.0024 | 34.1758 | 34.9977 | 35.1763 | 35.3629 | 35.6437 | 36.7777 | 39.138 | 41.5005 | 37.0815 | 43.3335 | 43.3335 | 44.6833 | 45.5558 | 46.384 | 46.6823 | 47.047 | 47.5677 | 48.5186 | 50.9074 | 53.0734 | 0.012172 | 0.024535 | 0.041054 | 0.064046 | 0.09215 | 0.12818 | 0.17253 | 0.27921 | 0.36665 | 0.45127 | -0.090772 | -0.11383 | -0.13875 | -0.16122 | -0.17874 | -0.19103 | -0.1991 | -0.18669 | -0.18215 | -0.17479
Railton | 85001 | 112.9253 | 166.7945 | 166.7945 | 169.3347 | 175.3554 | 179.5722 | 180.4884 | 181.4462 | 182.8867 | 188.7056 | 200.8162 | 212.9382 | 195.0522 | 166.1471 | 166.1471 | 171.3224 | 174.6674 | 177.8431 | 178.9868 | 180.3848 | 182.3814 | 186.0272 | 195.1865 | 203.4912 | 0.11127 | 0.22644 | 0.36308 | 0.52083 | 0.68818 | 0.87945 | 1.0985 | 1.5838 | 1.9912 | 2.3781 | -1.1977 | -1.4459 | -1.7107 | -1.9586 | -2.1661 | -2.3406 | -2.4919 | -2.6086 | -2.74 | -2.8442
Railton | 85002 | 161.4 | 190.3214 | 190.3214 | 193.22 | 200.0899 | 204.9015 | 205.947 | 207.0399 | 208.6835 | 215.3232 | 229.1421 | 242.9739 | 152.8407 | 150.9798 | 150.9798 | 155.6827 | 158.7224 | 161.6081 | 162.6475 | 163.9179 | 165.7322 | 169.0451 | 177.3683 | 184.9149 | 0.086832 | 0.17279 | 0.27606 | 0.39802 | 0.53007 | 0.68386 | 0.86236 | 1.264 | 1.6005 | 1.9218 | -0.87433 | -1.0573 | -1.2526 | -1.4342 | -1.5846 | -1.7085 | -1.813 | -1.876 | -1.9554 | -2.0149
Railton | 85003 | 81.1075 | 44.5896 | 44.5896 | 45.2687 | 46.8782 | 48.0055 | 48.2504 | 48.5065 | 48.8916 | 50.4471 | 53.6847 | 56.9253 | 95.7849 | 43.4468 | 43.4468 | 44.8001 | 45.6748 | 46.5052 | 46.8043 | 47.1699 | 47.692 | 48.6453 | 51.0405 | 53.2121 | 0.056202 | 0.11499 | 0.18492 | 0.26539 | 0.35032 | 0.44664 | 0.55626 | 0.79675 | 0.99898 | 1.1903 | -0.60063 | -0.72996 | -0.86964 | -1.0028 | -1.1168 | -1.2157 | -1.3048 | -1.3856 | -1.472 | -1.5451
Railton | 85004 | 122.6535 | 116.2592 | 116.2592 | 118.0298 | 122.2263 | 125.1655 | 125.8042 | 126.4718 | 127.4758 | 131.5317 | 139.9731 | 148.4223 | 77.3535 | 100.6395 | 100.6395 | 103.7743 | 105.8005 | 107.7241 | 108.4169 | 109.2637 | 110.4731 | 112.6814 | 118.2294 | 123.2598 | 0.022311 | 0.046669 | 0.075175 | 0.10692 | 0.13938 | 0.17503 | 0.21465 | 0.29894 | 0.37022 | 0.43691 | -0.25222 | -0.30707 | -0.36642 | -0.4235 | -0.47302 | -0.51699 | -0.5576 | -0.60071 | -0.64411 | -0.68169
Railton | 85005 | 345.9045 | 346.0922 | 346.0922 | 351.3631 | 363.8557 | 372.6054 | 374.5066 | 376.494 | 379.4829 | 391.5569 | 416.686 | 441.8386 | 330.5948 | 297.8327 | 297.8327 | 307.1099 | 313.1062 | 318.7988 | 320.849 | 323.3551 | 326.9342 | 333.4695 | 349.8883 | 364.7752 | 4.0308e-05 | 8.3895e-05 | 0.00013446 | 0.00018989 | 0.00024576 | 0.00030627 | 0.00037286 | 0.00051258 | 0.00063156 | 0.0007427 | -0.00041469 | -0.00051318 | -0.00061944 | -0.00072148 | -0.00080999 | -0.00088875 | -0.0009617 | -0.0010416 | -0.0011215 | -0.0011913
Railton | 85006 | 240.4523 | 244.5902 | 244.5902 | 248.3153 | 257.1441 | 263.3277 | 264.6713 | 266.0758 | 268.1882 | 276.7211 | 294.4803 | 312.2561 | 191.292 | 177.3782 | 177.3782 | 182.9034 | 186.4745 | 189.8648 | 191.0859 | 192.5784 | 194.71 | 198.6022 | 208.3806 | 217.2467 | 0.10827 | 0.21497 | 0.34356 | 0.49637 | 0.66271 | 0.85743 | 1.0842 | 1.5967 | 2.0256 | 2.4357 | -1.082 | -1.3079 | -1.549 | -1.7725 | -1.9569 | -2.1076 | -2.2335 | -2.302 | -2.3926 | -2.4587
Railton | 85007 | 410.5 | 563.7124 | 563.7124 | 572.2976 | 592.6456 | 606.8971 | 609.9937 | 613.2307 | 618.0991 | 637.765 | 678.6952 | 719.6635 | 418.931 | 495.8583 | 495.8583 | 511.3038 | 521.2869 | 530.7644 | 534.1779 | 538.3503 | 544.309 | 555.1896 | 582.525 | 607.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton | 85008 | 96.49 | 120.5448 | 158.5041 | 122.3807 | 126.7319 | 129.7795 | 130.4417 | 131.1339 | 132.1749 | 136.3803 | 145.1329 | 153.8936 | 179.0406 | 190.4136 | 223.804 | 196.3449 | 200.1784 | 203.8179 | 205.1287 | 206.7309 | 209.0191 | 213.1974 | 223.6944 | 233.212 | 0.062839 | 0.13148 | 0.21185 | 0.30144 | 0.39312 | 0.49391 | 0.60597 | 0.84454 | 1.0462 | 1.2349 | -0.7136 | -0.86817 | -1.0355 | -1.1964 | -1.336 | -1.4601 | -1.5747 | -1.6961 | -1.8185 | -1.9244
Richmond Rural Zone | 40001 | 23.8333 | 29.6176 | 29.6176 | 30.0687 | 31.1378 | 31.8866 | 32.0493 | 32.2193 | 32.4751 | 33.5084 | 35.6589 | 37.8114 | 36.0037 | 35.2908 | 35.2908 | 36.3901 | 37.1006 | 37.7751 | 38.018 | 38.315 | 38.7391 | 39.5135 | 41.459 | 43.2229 | 0.01268 | 0.023733 | 0.036525 | 0.050703 | 0.065197 | 0.081213 | 0.099142 | 0.13776 | 0.1704 | 0.20117 | -0.12348 | -0.14733 | -0.17262 | -0.19641 | -0.21653 | -0.23393 | -0.24957 | -0.26511 | -0.281 | -0.29447
Richmond Rural Zone | 40002 | 82.6333 | 102.6648 | 102.6648 | 104.2284 | 107.9342 | 110.5297 | 111.0937 | 111.6832 | 112.5699 | 116.1515 | 123.6058 | 131.067 | 103.0654 | 117.3051 | 117.3051 | 120.9591 | 123.3208 | 125.5629 | 126.3704 | 127.3575 | 128.7671 | 131.3411 | 137.8079 | 143.6713 | 0.036099 | 0.074247 | 0.12078 | 0.17758 | 0.24092 | 0.3168 | 0.40666 | 0.61368 | 0.78678 | 0.95366 | -0.35366 | -0.43173 | -0.51433 | -0.58966 | -0.65017 | -0.69741 | -0.73448 | -0.741 | -0.75895 | -0.76907
Richmond Rural Zone | 40003 | 12.8 | 43.6833 | 43.6833 | 44.3486 | 45.9254 | 47.0298 | 47.2697 | 47.5206 | 47.8978 | 49.4218 | 52.5936 | 55.7683 | 13.3655 | 43.1119 | 43.1119 | 44.4548 | 45.3227 | 46.1468 | 46.4435 | 46.8063 | 47.3244 | 48.2704 | 50.647 | 52.8019 | 0.0054521 | 0.01069 | 0.016721 | 0.023339 | 0.030037 | 0.037363 | 0.045504 | 0.062866 | 0.077581 | 0.091417 | -0.05732 | -0.068667 | -0.080704 | -0.092052 | -0.10169 | -0.11008 | -0.11769 | -0.12561 | -0.1336 | -0.14044
Rokeby | 28221 | 63.8969 | 118.6483 | 118.6483 | 120.4553 | 124.7381 | 127.7377 | 128.3894 | 129.0707 | 130.0954 | 134.2346 | 142.8495 | 151.4724 | 138.012 | 110.9605 | 110.9605 | 114.4168 | 116.6508 | 118.7716 | 119.5355 | 120.4692 | 121.8026 | 124.2374 | 130.3543 | 135.9006 | 0.022266 | 0.046677 | 0.07578 | 0.10876 | 0.14288 | 0.18062 | 0.22325 | 0.31484 | 0.39269 | 0.46577 | -0.20447 | -0.26143 | -0.32482 | -0.38819 | -0.44553 | -0.49894 | -0.55084 | -0.61189 | -0.67427 | -0.73041
Rokeby | 28222 | 95.3935 | 129.0497 | 129.0497 | 131.0151 | 135.6733 | 138.9359 | 139.6448 | 140.3858 | 141.5004 | 146.0024 | 155.3725 | 164.7513 | 186.7255 | 180.0173 | 180.0173 | 185.6247 | 189.249 | 192.6897 | 193.929 | 195.4437 | 197.607 | 201.5571 | 211.481 | 220.479 | 0.062327 | 0.12233 | 0.19122 | 0.26599 | 0.34073 | 0.42133 | 0.50985 | 0.69554 | 0.85373 | 1.0021 | -0.61563 | -0.74784 | -0.88896 | -1.0235 | -1.1393 | -1.242 | -1.3372 | -1.444 | -1.55 | -1.6423
Rokeby | 28223 | 159.6874 | 210.9675 | 210.9675 | 214.1805 | 221.7956 | 227.1292 | 228.2881 | 229.4996 | 231.3215 | 238.6814 | 253.9994 | 269.3317 | 296.6908 | 279.6137 | 279.6137 | 288.3235 | 293.9529 | 299.2973 | 301.2221 | 303.5749 | 306.935 | 313.0706 | 328.485 | 342.4612 | 0.06384 | 0.12966 | 0.20652 | 0.29157 | 0.37791 | 0.47207 | 0.57626 | 0.7982 | 0.98718 | 1.1641 | -0.68989 | -0.83952 | -1.0023 | -1.1609 | -1.3006 | -1.4272 | -1.547 | -1.6837 | -1.82 | -1.9413
Rokeby | 28224 | 86.7086 | 93.5373 | 93.5373 | 94.9618 | 98.3382 | 100.703 | 101.2168 | 101.7539 | 102.5617 | 105.8249 | 112.6165 | 119.4144 | 144.1251 | 144.6463 | 144.6463 | 149.1519 | 152.064 | 154.8287 | 155.8245 | 157.0416 | 158.7798 | 161.9538 | 169.9277 | 177.1578 | 0.02581 | 0.054105 | 0.08784 | 0.12606 | 0.16562 | 0.20937 | 0.25879 | 0.36495 | 0.4552 | 0.53992 | -0.23699 | -0.30301 | -0.37649 | -0.44995 | -0.51642 | -0.57833 | -0.63849 | -0.70926 | -0.78158 | -0.84665
Rokeby | 28225 | 4.9295 | 5.7882 | 5.7882 | 5.8764 | 6.0853 | 6.2316 | 6.2634 | 6.2967 | 6.3467 | 6.5486 | 6.9689 | 7.3895 | 5.9021 | 7.3367 | 7.3367 | 7.5652 | 7.7129 | 7.8531 | 7.9036 | 7.9654 | 8.0535 | 8.2145 | 8.619 | 8.9857 | 0.00034404 | 0.0007245 | 0.0011747 | 0.0016801 | 0.0021991 | 0.0027695 | 0.0034086 | 0.0047796 | 0.0059414 | 0.0070294 | -0.0033391 | -0.0042213 | -0.0051959 | -0.0061621 | -0.0070287 | -0.007829 | -0.0085999 | -0.0095008 | -0.010412 | -0.011226
Rokeby | 28228 | 60.5855 | 119.9962 | 119.9962 | 121.8237 | 126.1551 | 129.1888 | 129.848 | 130.5371 | 131.5734 | 135.7596 | 144.4723 | 153.1932 | 118.4323 | 124.281 | 124.281 | 128.1522 | 130.6543 | 133.0298 | 133.8853 | 134.9311 | 136.4246 | 139.1517 | 146.003 | 152.215 | 0.020252 | 0.042454 | 0.068924 | 0.098917 | 0.12996 | 0.16428 | 0.20306 | 0.28636 | 0.35718 | 0.42365 | -0.18596 | -0.23776 | -0.29542 | -0.35306 | -0.40521 | -0.45379 | -0.501 | -0.55653 | -0.61327 | -0.66434
Rokeby | 28229 | 7.2662 | 9.4135 | 9.4135 | 9.5569 | 9.8967 | 10.1347 | 10.1864 | 10.2404 | 10.3217 | 10.6501 | 11.3336 | 12.0178 | 14.0211 | 11.1117 | 11.1117 | 11.4578 | 11.6816 | 11.8939 | 11.9704 | 12.0639 | 12.1975 | 12.4413 | 13.0538 | 13.6093 | 0.0020062 | 0.0042056 | 0.0068279 | 0.009799 | 0.012874 | 0.016274 | 0.020116 | 0.028368 | 0.035383 | 0.041968 | -0.018421 | -0.023554 | -0.029265 | -0.034975 | -0.040142 | -0.044954 | -0.049631 | -0.055131 | -0.060753 | -0.065811
Rokeby | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | 28231 | 165.3339 | 204.2627 | 204.2627 | 207.3735 | 214.7467 | 219.9107 | 221.0328 | 222.2057 | 223.9698 | 231.0958 | 245.927 | 260.7719 | 264.9803 | 268.1754 | 268.1754 | 276.5288 | 281.928 | 287.0537 | 288.8998 | 291.1564 | 294.3791 | 300.2636 | 315.0474 | 328.452 | 0.036456 | 0.076781 | 0.12449 | 0.17804 | 0.23301 | 0.29343 | 0.36109 | 0.50627 | 0.62928 | 0.74446 | -0.35428 | -0.44777 | -0.55103 | -0.65338 | -0.74516 | -0.82991 | -0.91153 | -1.0069 | -1.1033 | -1.1894
Rokeby | 28232 | 104.26 | 132.0998 | 132.0998 | 134.1117 | 138.88 | 142.2197 | 142.9454 | 143.7039 | 144.8448 | 149.4533 | 159.0448 | 168.6453 | 202.495 | 194.3414 | 194.3414 | 200.3949 | 204.3076 | 208.0221 | 209.36 | 210.9952 | 213.3306 | 217.5951 | 228.3086 | 238.0226 | 0.073264 | 0.13946 | 0.21624 | 0.3006 | 0.38582 | 0.47848 | 0.58085 | 0.79676 | 0.98158 | 1.1553 | -0.65845 | -0.80674 | -0.96681 | -1.1213 | -1.2559 | -1.3769 | -1.4901 | -1.6176 | -1.7459 | -1.8589
Rosebery (22 kV) | 97001 | 0 | 33.5657 | 33.5657 | 34.0769 | 35.2885 | 36.137 | 36.3214 | 36.5142 | 36.8041 | 37.975 | 40.4122 | 42.8516 | 36.374 | 33.6953 | 33.6953 | 34.7449 | 35.4233 | 36.0673 | 36.2993 | 36.5828 | 36.9877 | 37.7271 | 39.5847 | 41.2689 | 2.092e-05 | 4.3124e-05 | 7.2067e-05 | 0.0001106 | 0.00015618 | 0.00021304 | 0.00028182 | 0.00044402 | 0.00057709 | 0.00070493 | -0.00016488 | -0.0002095 | -0.00025857 | -0.00030493 | -0.00034369 | -0.00037506 | -0.00040098 | -0.00040447 | -0.00041793 | -0.00042591
Rosebery (22 kV) | 97002 | 0 | 31.947 | 31.947 | 32.4335 | 33.5867 | 34.3944 | 34.5699 | 34.7533 | 35.0292 | 36.1437 | 38.4634 | 40.7851 | 36.8103 | 36.7146 | 36.7146 | 37.8582 | 38.5974 | 39.2991 | 39.5519 | 39.8608 | 40.302 | 41.1076 | 43.1316 | 44.9668 | 0.024542 | 0.049013 | 0.080751 | 0.12293 | 0.17287 | 0.23534 | 0.3111 | 0.49034 | 0.63781 | 0.77998 | -0.19087 | -0.23934 | -0.29197 | -0.34066 | -0.38021 | -0.41073 | -0.43427 | -0.4285 | -0.43489 | -0.43536
Rosebery (44 kV) | 97013 | 30.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00033808 | 0.00059326 | 0.0010189 | 0.0018044 | 0.0029297 | 0.0045646 | 0.0067263 | 0.012289 | 0.016825 | 0.021335 | -0.0007686 | -0.00094784 | -0.0010703 | -0.00098539 | -0.0006686 | -4.4228e-05 | 0.00030892 | 0.00043093 | 0.00053772 | 0.00063947
Rosebery (44 kV) | 97014 | 220.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.092e-05 | 4.3124e-05 | 7.2067e-05 | 0.0001106 | 0.00015618 | 0.00021304 | 0.00028182 | 0.00044402 | 0.00057709 | 0.00070493 | -0.00016488 | -0.0002095 | -0.00025857 | -0.00030493 | -0.00034369 | -0.00037506 | -0.00040098 | -0.00040447 | -0.00041793 | -0.00042591
Rosny Park Zone | 23340 | 88.7121 | 103.8974 | 103.8974 | 105.4797 | 109.23 | 111.8567 | 112.4274 | 113.024 | 113.9213 | 117.5459 | 125.0897 | 132.6406 | 0 | 84.7226 | 84.7226 | 87.3616 | 89.0673 | 90.6866 | 91.2699 | 91.9828 | 93.0009 | 94.8599 | 99.5305 | 103.7653 | 0.0037327 | 0.0078637 | 0.012749 | 0.018229 | 0.023852 | 0.030029 | 0.036944 | 0.051779 | 0.064345 | 0.076111 | -0.036395 | -0.045969 | -0.056538 | -0.067009 | -0.076393 | -0.085053 | -0.093389 | -0.10312 | -0.11296 | -0.12174
Rosny Park Zone | 23341 | 64.8699 | 90.2421 | 90.2421 | 91.6165 | 94.8739 | 97.1553 | 97.651 | 98.1692 | 98.9486 | 102.0968 | 108.6491 | 115.2076 | 136.7685 | 120.4153 | 120.4153 | 124.1661 | 126.5904 | 128.892 | 129.7209 | 130.7341 | 132.1812 | 134.8234 | 141.4616 | 147.4805 | 0.023453 | 0.049408 | 0.080099 | 0.11453 | 0.14986 | 0.18867 | 0.23212 | 0.32533 | 0.40428 | 0.47821 | -0.22867 | -0.28883 | -0.35523 | -0.42102 | -0.47998 | -0.53439 | -0.58676 | -0.64793 | -0.70975 | -0.76491
Rosny Park Zone | 23342 | 125.3254 | 161.185 | 161.185 | 163.6398 | 169.458 | 173.533 | 174.4184 | 175.344 | 176.736 | 182.3592 | 194.0626 | 205.7768 | 211.4313 | 197.0505 | 197.0505 | 203.1885 | 207.1557 | 210.922 | 212.2785 | 213.9365 | 216.3045 | 220.6284 | 231.4913 | 241.3407 | 0.029449 | 0.062815 | 0.10226 | 0.14655 | 0.19203 | 0.24205 | 0.29804 | 0.41839 | 0.52022 | 0.61556 | -0.29132 | -0.36846 | -0.45351 | -0.53762 | -0.61284 | -0.6821 | -0.7486 | -0.82577 | -0.90382 | -0.97325
Rosny Park Zone | 23343 | 132.9669 | 172.4048 | 172.4048 | 175.0305 | 181.2537 | 185.6123 | 186.5594 | 187.5494 | 189.0384 | 195.0529 | 207.5709 | 220.1006 | 202.1728 | 182.1467 | 182.1467 | 187.8204 | 191.4875 | 194.969 | 196.2229 | 197.7555 | 199.9444 | 203.9413 | 213.9825 | 223.087 | 0.02877 | 0.06061 | 0.09826 | 0.1405 | 0.18384 | 0.23145 | 0.28474 | 0.39909 | 0.49595 | 0.58663 | -0.28052 | -0.35431 | -0.43577 | -0.51648 | -0.5888 | -0.65555 | -0.7198 | -0.79483 | -0.87067 | -0.93834
Rosny Park Zone | 23346 | 27.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosny Park Zone | 23347 | 70.5289 | 88.6788 | 88.6788 | 90.0294 | 93.2303 | 95.4723 | 95.9594 | 96.4686 | 97.2345 | 100.3282 | 106.767 | 113.2118 | 134.7452 | 113.7003 | 113.7003 | 117.242 | 119.5311 | 121.7043 | 122.487 | 123.4437 | 124.8101 | 127.305 | 133.573 | 139.2562 | 0.0191 | 0.040248 | 0.065256 | 0.093313 | 0.12211 | 0.15374 | 0.18915 | 0.26512 | 0.32948 | 0.38973 | -0.18632 | -0.23533 | -0.28942 | -0.34302 | -0.39104 | -0.43536 | -0.47801 | -0.52781 | -0.57815 | -0.62305
Rosny Park Zone | 23348 | 81.3937 | 100.8394 | 100.8394 | 102.3752 | 106.0151 | 108.5645 | 109.1184 | 109.6975 | 110.5684 | 114.0863 | 121.408 | 128.7367 | 169.3206 | 148.5813 | 148.5813 | 153.2095 | 156.2008 | 159.0408 | 160.0636 | 161.3138 | 163.0993 | 166.3596 | 174.5505 | 181.9772 | 0.029721 | 0.063637 | 0.10373 | 0.14876 | 0.19501 | 0.24589 | 0.30284 | 0.42535 | 0.52895 | 0.62596 | -0.29532 | -0.37367 | -0.46003 | -0.54538 | -0.62167 | -0.69186 | -0.7592 | -0.83719 | -0.91609 | -0.98622
Sandy Bay Zone | 12017 | 110.3723 | 126.5034 | 126.5034 | 128.4301 | 132.9964 | 136.1946 | 136.8895 | 137.6159 | 138.7084 | 143.1217 | 152.3069 | 161.5006 | 202.8424 | 169.5775 | 169.5775 | 174.8597 | 178.2738 | 181.515 | 182.6824 | 184.1093 | 186.1471 | 189.8681 | 199.2165 | 207.6927 | 0.054293 | 0.1022 | 0.15831 | 0.22072 | 0.28435 | 0.35401 | 0.43138 | 0.59827 | 0.73831 | 0.8689 | -0.48637 | -0.59536 | -0.71406 | -0.82978 | -0.93171 | -1.0241 | -1.1116 | -1.2111 | -1.3103 | -1.3971
Sandy Bay Zone | 12018 | 69.6416 | 108.2215 | 108.2215 | 109.8697 | 113.7761 | 116.5121 | 117.1066 | 117.7281 | 118.6627 | 122.4382 | 130.2959 | 138.161 | 154.1768 | 151.3488 | 151.3488 | 156.0632 | 159.1103 | 162.0031 | 163.045 | 164.3185 | 166.1372 | 169.4583 | 177.8018 | 185.3668 | 0.032969 | 0.062147 | 0.097004 | 0.13712 | 0.17927 | 0.22736 | 0.282 | 0.40239 | 0.50217 | 0.59488 | -0.27392 | -0.33975 | -0.41199 | -0.48283 | -0.54554 | -0.60245 | -0.65631 | -0.71561 | -0.7749 | -0.8252
Sandy Bay Zone | 12019 | 108.7889 | 131.7956 | 131.7956 | 133.8028 | 138.5602 | 141.8922 | 142.6162 | 143.373 | 144.5112 | 149.1091 | 158.6785 | 168.2569 | 208.9262 | 203.841 | 203.841 | 210.1904 | 214.2943 | 218.1904 | 219.5937 | 221.3089 | 223.7585 | 228.2313 | 239.4686 | 249.6574 | 0.040231 | 0.075837 | 0.11837 | 0.16733 | 0.21875 | 0.27745 | 0.34412 | 0.49103 | 0.61279 | 0.72592 | -0.33426 | -0.41459 | -0.50274 | -0.58919 | -0.66571 | -0.73516 | -0.80089 | -0.87324 | -0.9456 | -1.007
Sandy Bay Zone | 12030 | 83.9583 | 122.6332 | 122.6332 | 124.5008 | 128.9274 | 132.0278 | 132.7015 | 133.4056 | 134.4647 | 138.743 | 147.6472 | 156.5596 | 226.4858 | 176.4098 | 176.4098 | 181.9048 | 185.4565 | 188.8283 | 190.0427 | 191.5271 | 193.647 | 197.5179 | 207.243 | 216.0607 | 0.040111 | 0.078033 | 0.12275 | 0.17308 | 0.22494 | 0.28228 | 0.34682 | 0.48661 | 0.60333 | 0.71227 | -0.34853 | -0.43464 | -0.5287 | -0.62061 | -0.7017 | -0.77524 | -0.84478 | -0.92276 | -1.0013 | -1.0693
Sandy Bay Zone | 12031 | 97.262 | 159.3805 | 265.6665 | 161.8079 | 167.5609 | 171.5903 | 172.4658 | 173.381 | 174.7575 | 180.3177 | 191.89 | 203.4732 | 247.5934 | 226.4877 | 319.9807 | 233.5426 | 238.1024 | 242.4314 | 243.9905 | 245.8962 | 248.618 | 253.5878 | 266.0735 | 277.3943 | 0.054259 | 0.10695 | 0.16861 | 0.23706 | 0.30675 | 0.38294 | 0.46736 | 0.6481 | 0.80123 | 0.94451 | -0.48512 | -0.60519 | -0.73599 | -0.8635 | -0.9758 | -1.0776 | -1.1738 | -1.2831 | -1.3931 | -1.4896
Sandy Bay Zone | 12032 | 62.5736 | 71.3318 | 71.3318 | 72.4182 | 74.993 | 76.7964 | 77.1882 | 77.5978 | 78.2138 | 80.7024 | 85.8816 | 91.0657 | 122.6131 | 111.8093 | 111.8093 | 115.292 | 117.5431 | 119.6801 | 120.4498 | 121.3906 | 122.7343 | 125.1877 | 131.3515 | 136.9401 | 0.025917 | 0.048885 | 0.076321 | 0.10789 | 0.14106 | 0.17891 | 0.2219 | 0.31662 | 0.39513 | 0.46808 | -0.21543 | -0.26725 | -0.3241 | -0.37986 | -0.4292 | -0.47398 | -0.51636 | -0.56302 | -0.60967 | -0.64923
Sandy Bay Zone | 12033 | 30.6797 | 46.2884 | 46.2884 | 46.9933 | 48.6642 | 49.8344 | 50.0887 | 50.3545 | 50.7543 | 52.3691 | 55.73 | 59.0941 | 70.5613 | 68.8639 | 68.8639 | 71.009 | 72.3954 | 73.7117 | 74.1857 | 74.7652 | 75.5927 | 77.1038 | 80.9001 | 84.3422 | 0.013323 | 0.025103 | 0.039124 | 0.055161 | 0.071921 | 0.090874 | 0.1124 | 0.15941 | 0.19863 | 0.23509 | -0.11232 | -0.13894 | -0.16811 | -0.19668 | -0.22195 | -0.24488 | -0.26658 | -0.29058 | -0.31464 | -0.33514
Sandy Bay Zone | 12034 | 0 | 2.492 | 2.492 | 2.53 | 2.6199 | 2.6829 | 2.6966 | 2.7109 | 2.7325 | 2.8194 | 3.0003 | 3.1815 | 0 | 2.1914 | 2.1914 | 2.2597 | 2.3038 | 2.3457 | 2.3608 | 2.3792 | 2.4055 | 2.4536 | 2.5744 | 2.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sandy Bay Zone | 12035 | 81.2345 | 109.3673 | 109.3673 | 111.033 | 114.9807 | 117.7457 | 118.3465 | 118.9745 | 119.919 | 123.7345 | 131.6754 | 139.6238 | 232.3415 | 179.3162 | 179.3162 | 184.9017 | 188.5118 | 191.9392 | 193.1736 | 194.6824 | 196.8373 | 200.772 | 210.6573 | 219.6202 | 0.031639 | 0.059639 | 0.09309 | 0.13159 | 0.17203 | 0.21819 | 0.27062 | 0.38615 | 0.48191 | 0.57088 | -0.26287 | -0.32604 | -0.39536 | -0.46335 | -0.52353 | -0.57814 | -0.62983 | -0.68673 | -0.74363 | -0.7919
Sandy Bay Zone | 12036 | 142.5001 | 160.1796 | 160.1796 | 162.6191 | 168.401 | 172.4506 | 173.3305 | 174.2503 | 175.6336 | 181.2217 | 192.8521 | 204.4933 | 207.3053 | 208.931 | 208.931 | 215.439 | 219.6454 | 223.6388 | 225.0771 | 226.8351 | 229.3458 | 233.9304 | 245.4482 | 255.8914 | 7.1906e-05 | 0.00013554 | 0.00021157 | 0.00029906 | 0.00039098 | 0.00049589 | 0.00061505 | 0.00087761 | 0.0010952 | 0.0012974 | -0.00059743 | -0.00074101 | -0.00089856 | -0.0010531 | -0.0011898 | -0.001314 | -0.0014314 | -0.0015608 | -0.0016901 | -0.0017998
Sandy Bay Zone | 12037 | 109.5099 | 132.4958 | 132.4958 | 134.5137 | 139.2963 | 142.646 | 143.3738 | 144.1346 | 145.2789 | 149.9012 | 159.5215 | 169.1507 | 149.7725 | 152.8182 | 152.8182 | 157.5783 | 160.655 | 163.5759 | 164.6279 | 165.9138 | 167.7502 | 171.1035 | 179.528 | 187.1664 | 0.0084849 | 0.015994 | 0.024965 | 0.035289 | 0.046136 | 0.058515 | 0.072576 | 0.10356 | 0.12924 | 0.1531 | -0.070496 | -0.087439 | -0.10603 | -0.12426 | -0.1404 | -0.15505 | -0.16891 | -0.18417 | -0.19943 | -0.21237
Sandy Bay Zone | 12038 | 98.4381 | 115.6536 | 115.6536 | 117.415 | 121.5897 | 124.5136 | 125.1489 | 125.813 | 126.8118 | 130.8466 | 139.244 | 147.6492 | 222.1189 | 169.0352 | 169.0352 | 174.3005 | 177.7037 | 180.9345 | 182.0982 | 183.5205 | 185.5518 | 189.2609 | 198.5794 | 207.0285 | 0.034555 | 0.066063 | 0.10317 | 0.14483 | 0.18767 | 0.23494 | 0.28806 | 0.40294 | 0.49893 | 0.58847 | -0.30476 | -0.37636 | -0.45453 | -0.53089 | -0.59828 | -0.65941 | -0.71725 | -0.78241 | -0.84771 | -0.90447
Sandy Bay Zone | 12039 | 106.2644 | 117.0767 | 117.0767 | 118.8597 | 123.0858 | 126.0456 | 126.6888 | 127.3611 | 128.3722 | 132.4566 | 140.9573 | 149.4659 | 204.4284 | 187.6669 | 187.6669 | 193.5126 | 197.2908 | 200.8778 | 202.1697 | 203.7488 | 206.004 | 210.122 | 220.4676 | 229.8479 | 0.041002 | 0.077987 | 0.12212 | 0.17283 | 0.22604 | 0.28671 | 0.35558 | 0.50724 | 0.63293 | 0.74967 | -0.34292 | -0.42629 | -0.51766 | -0.60717 | -0.68631 | -0.75806 | -0.8259 | -0.90061 | -0.97517 | -1.0383
Savage River | 95001 | 24.9206 | 27.0831 | 27.0831 | 27.4955 | 28.4731 | 29.1578 | 29.3066 | 29.4621 | 29.696 | 30.6409 | 32.6073 | 34.5756 | 33.9432 | 31.7871 | 31.7871 | 32.7772 | 33.4172 | 34.0248 | 34.2436 | 34.5111 | 34.893 | 35.5905 | 37.3429 | 38.9317 | 0.011228 | 0.021197 | 0.033998 | 0.05095 | 0.071054 | 0.09634 | 0.12718 | 0.20061 | 0.26136 | 0.32034 | -0.085333 | -0.1045 | -0.12475 | -0.1426 | -0.15609 | -0.16519 | -0.17063 | -0.1606 | -0.15597 | -0.14928
Scottsdale | 54003 | 157.3874 | 183.0711 | 183.0711 | 185.8592 | 192.4674 | 197.0957 | 198.1014 | 199.1526 | 200.7337 | 207.1204 | 220.4128 | 233.7177 | 146.1405 | 131.1166 | 131.1166 | 135.2008 | 137.8405 | 140.3466 | 141.2492 | 142.3525 | 143.9281 | 146.8052 | 154.0333 | 160.5871 | 0.08086 | 0.15989 | 0.25718 | 0.37652 | 0.50968 | 0.66867 | 0.85617 | 1.2856 | 1.6437 | 1.9871 | -0.66484 | -0.83099 | -1.0099 | -1.177 | -1.3155 | -1.4285 | -1.5227 | -1.5638 | -1.6278 | -1.6734
Scottsdale | 54004 | 18.2606 | 24.3798 | 24.3798 | 24.7511 | 25.6311 | 26.2475 | 26.3814 | 26.5214 | 26.7319 | 27.5825 | 29.3526 | 31.1245 | 20.6667 | 21.3288 | 21.3288 | 21.9932 | 22.4226 | 22.8303 | 22.9771 | 23.1566 | 23.4129 | 23.8809 | 25.0567 | 26.1228 | 0.0051568 | 0.010876 | 0.01767 | 0.02552 | 0.033852 | 0.043374 | 0.05428 | 0.078425 | 0.098715 | 0.11799 | -0.062688 | -0.075065 | -0.088303 | -0.10073 | -0.11115 | -0.11995 | -0.12762 | -0.1336 | -0.14032 | -0.14563
Scottsdale | 54005 | 96.3333 | 95.7045 | 95.7045 | 97.162 | 100.6166 | 103.0362 | 103.5619 | 104.1115 | 104.938 | 108.2768 | 115.2257 | 122.1811 | 88.225 | 98.0149 | 98.0149 | 101.068 | 103.0413 | 104.9147 | 105.5894 | 106.4142 | 107.592 | 109.7428 | 115.1461 | 120.0453 | 0.088129 | 0.16025 | 0.24478 | 0.34082 | 0.44139 | 0.55515 | 0.68456 | 0.96924 | 1.2081 | 1.4343 | -0.79334 | -0.94684 | -1.109 | -1.2593 | -1.3837 | -1.4875 | -1.5767 | -1.6468 | -1.7237 | -1.7842
Scottsdale | 54006 | 3.3552 | 9.8738 | 9.8738 | 10.0242 | 10.3806 | 10.6303 | 10.6845 | 10.7412 | 10.8265 | 11.1709 | 11.8879 | 12.6054 | 3.3333 | 13.9294 | 13.9294 | 14.3632 | 14.6437 | 14.9099 | 15.0058 | 15.123 | 15.2904 | 15.5961 | 16.3639 | 17.0602 | 0.0041605 | 0.0087029 | 0.014098 | 0.020331 | 0.026946 | 0.034506 | 0.043164 | 0.062331 | 0.078438 | 0.093736 | -0.049899 | -0.059727 | -0.070237 | -0.080097 | -0.088372 | -0.095355 | -0.10143 | -0.10618 | -0.11151 | -0.11571
Scottsdale | 54007 | 58.7638 | 75.619 | 75.619 | 76.7706 | 79.5002 | 81.412 | 81.8274 | 82.2616 | 82.9147 | 85.5527 | 91.0433 | 96.539 | 104.8026 | 101.3394 | 101.3394 | 104.496 | 106.5363 | 108.4732 | 109.1708 | 110.0235 | 111.2413 | 113.465 | 119.0516 | 124.117 | 0.037542 | 0.079177 | 0.12864 | 0.18579 | 0.24644 | 0.31576 | 0.39516 | 0.57094 | 0.71865 | 0.85894 | -0.45637 | -0.54647 | -0.64285 | -0.73328 | -0.80919 | -0.87326 | -0.92904 | -0.97263 | -1.0216 | -1.0602
Smithton | 93001 | 109.3501 | 166.7897 | 166.7897 | 169.3299 | 175.3504 | 179.5671 | 180.4833 | 181.441 | 182.8815 | 188.7002 | 200.8105 | 212.9321 | 41.0165 | 122.4287 | 122.4287 | 126.2422 | 128.707 | 131.0471 | 131.8899 | 132.92 | 134.3913 | 137.0777 | 143.8269 | 149.9464 | 0.0080013 | 0.016954 | 0.02777 | 0.040444 | 0.053997 | 0.069505 | 0.087241 | 0.12631 | 0.15911 | 0.1901 | -0.096146 | -0.11614 | -0.13809 | -0.15941 | -0.17806 | -0.19462 | -0.2099 | -0.22451 | -0.24007 | -0.25359
Smithton | 93002 | 176.0583 | 199.247 | 199.247 | 202.2815 | 209.4736 | 214.5108 | 215.6053 | 216.7495 | 218.4702 | 225.4213 | 239.8882 | 254.3687 | 90.08 | 114.7645 | 114.7645 | 118.3393 | 120.6498 | 122.8434 | 123.6334 | 124.5991 | 125.9782 | 128.4965 | 134.8232 | 140.5596 | 0.024951 | 0.05287 | 0.086599 | 0.12612 | 0.16839 | 0.21675 | 0.27206 | 0.3939 | 0.49616 | 0.59283 | -0.29982 | -0.36218 | -0.43062 | -0.49711 | -0.55526 | -0.6069 | -0.65456 | -0.70012 | -0.74864 | -0.7908
Smithton | 93003 | 128.9746 | 154.5545 | 154.5545 | 156.9083 | 162.4872 | 166.3945 | 167.2436 | 168.1311 | 169.4658 | 174.8577 | 186.0796 | 197.312 | 48.1135 | 126.684 | 126.684 | 130.6301 | 133.1806 | 135.602 | 136.4741 | 137.54 | 139.0624 | 141.8422 | 148.826 | 155.1582 | 0.032926 | 0.069768 | 0.11428 | 0.16643 | 0.22221 | 0.28602 | 0.35901 | 0.5198 | 0.65474 | 0.78231 | -0.39565 | -0.47794 | -0.56825 | -0.65599 | -0.73274 | -0.80087 | -0.86378 | -0.92389 | -0.98792 | -1.0436
Smithton | 93004 | 114.4758 | 112.9233 | 112.9233 | 114.6431 | 118.7192 | 121.5741 | 122.1944 | 122.8428 | 123.8181 | 127.7575 | 135.9567 | 144.1635 | 50.6261 | 124.1006 | 124.1006 | 127.9662 | 130.4647 | 132.8367 | 133.691 | 134.7353 | 136.2266 | 138.9497 | 145.7911 | 151.9941 | 0.0078171 | 0.016564 | 0.027131 | 0.039513 | 0.052754 | 0.067905 | 0.085232 | 0.12341 | 0.15544 | 0.18573 | -0.093932 | -0.11347 | -0.13491 | -0.15574 | -0.17396 | -0.19014 | -0.20507 | -0.21934 | -0.23454 | -0.24775
Smithton | 93005 | 105.435 | 110.5818 | 110.5818 | 112.2659 | 116.2575 | 119.0532 | 119.6606 | 120.2956 | 121.2506 | 125.1084 | 133.1376 | 141.1742 | 77.4235 | 148.8718 | 148.8718 | 153.509 | 156.5062 | 159.3517 | 160.3765 | 161.6292 | 163.4182 | 166.6849 | 174.8918 | 182.333 | 0.035085 | 0.074341 | 0.12177 | 0.17734 | 0.23677 | 0.30477 | 0.38254 | 0.55387 | 0.69766 | 0.83358 | -0.42159 | -0.50927 | -0.6055 | -0.69899 | -0.78077 | -0.85337 | -0.92039 | -0.98445 | -1.0527 | -1.112
Smithton | 93006 | 67.5014 | 75.2805 | 75.2805 | 76.427 | 79.1444 | 81.0476 | 81.4611 | 81.8934 | 82.5436 | 85.1698 | 90.6358 | 96.1069 | 50.548 | 60.4645 | 60.4645 | 62.3479 | 63.5653 | 64.7209 | 65.1372 | 65.646 | 66.3726 | 67.6993 | 71.0326 | 74.0549 | 2.632e-05 | 5.577e-05 | 9.1349e-05 | 0.00013304 | 0.00017762 | 0.00022864 | 0.00028698 | 0.00041551 | 0.00052337 | 0.00062534 | -0.00031627 | -0.00038205 | -0.00045424 | -0.00052438 | -0.00058572 | -0.00064019 | -0.00069047 | -0.00073852 | -0.0007897 | -0.00083417
Sorell | 41511 | 72.7733 | 87.4246 | 87.4246 | 88.7561 | 91.9118 | 94.122 | 94.6023 | 95.1043 | 95.8593 | 98.9092 | 105.257 | 111.6107 | 133.77 | 125.267 | 125.267 | 129.169 | 131.6909 | 134.0852 | 134.9476 | 136.0016 | 137.507 | 140.2557 | 147.1613 | 153.4227 | 0.06029 | 0.12445 | 0.19972 | 0.28292 | 0.36709 | 0.45825 | 0.55891 | 0.77246 | 0.95475 | 1.1251 | -0.57452 | -0.72414 | -0.88905 | -1.0524 | -1.199 | -1.3347 | -1.4657 | -1.6227 | -1.78 | -1.9212
Sorell | 41512 | 80.8592 | 100.4283 | 147.8774 | 101.9578 | 105.5829 | 108.1219 | 108.6736 | 109.2503 | 110.1176 | 113.6212 | 120.9131 | 128.2118 | 108.7384 | 130.7168 | 172.4547 | 134.7885 | 137.4202 | 139.9187 | 140.8185 | 141.9184 | 143.4893 | 146.3576 | 153.5636 | 160.0974 | 0.01895 | 0.037212 | 0.058439 | 0.081912 | 0.10579 | 0.13195 | 0.16102 | 0.2229 | 0.2755 | 0.32494 | -0.18776 | -0.22835 | -0.27204 | -0.31399 | -0.35034 | -0.38271 | -0.41276 | -0.44548 | -0.47852 | -0.50746
Sorell | 41513 | 97.3826 | 117.427 | 117.427 | 119.2154 | 123.454 | 126.4228 | 127.0678 | 127.7421 | 128.7563 | 132.8529 | 141.379 | 149.9132 | 154.0362 | 145.4677 | 145.4677 | 149.9989 | 152.9275 | 155.7079 | 156.7093 | 157.9334 | 159.6815 | 162.8734 | 170.8927 | 178.1638 | 0.064052 | 0.12783 | 0.20246 | 0.28562 | 0.37076 | 0.46454 | 0.56918 | 0.79265 | 0.98322 | 1.1629 | -0.60503 | -0.74871 | -0.90434 | -1.0547 | -1.1856 | -1.3026 | -1.4115 | -1.5286 | -1.6486 | -1.7538
Sorell | 41514 | 46.289 | 64.998 | 64.998 | 65.9879 | 68.3341 | 69.9774 | 70.3344 | 70.7077 | 71.269 | 73.5366 | 78.256 | 82.9797 | 65.7428 | 72.8895 | 72.8895 | 75.16 | 76.6275 | 78.0206 | 78.5224 | 79.1357 | 80.0116 | 81.611 | 85.6293 | 89.2726 | 0.035822 | 0.073828 | 0.11888 | 0.17017 | 0.22372 | 0.28376 | 0.3516 | 0.49872 | 0.62352 | 0.74152 | -0.35548 | -0.44072 | -0.53347 | -0.62314 | -0.70122 | -0.77063 | -0.83482 | -0.89994 | -0.96822 | -1.0278
Sorell | 41515 | 79.2186 | 106.9281 | 106.9281 | 108.5566 | 112.4163 | 115.1197 | 115.707 | 116.3211 | 117.2445 | 120.9749 | 128.7387 | 136.5098 | 130.4681 | 129.5001 | 129.5001 | 133.5339 | 136.1411 | 138.6163 | 139.5078 | 140.5975 | 142.1537 | 144.9953 | 152.1343 | 158.6073 | 0.11607 | 0.22624 | 0.35913 | 0.5153 | 0.68307 | 0.87632 | 1.0987 | 1.5925 | 2.0081 | 2.4032 | -0.96905 | -1.2114 | -1.4753 | -1.7287 | -1.9471 | -2.1373 | -2.3093 | -2.4589 | -2.627 | -2.7689
Sorell | 41516 | 81.3906 | 163.8557 | 163.8557 | 166.3511 | 172.2657 | 176.4082 | 177.3084 | 178.2493 | 179.6644 | 185.3807 | 197.278 | 209.1863 | 130.5825 | 140.9505 | 140.9505 | 145.341 | 148.1787 | 150.8728 | 151.8431 | 153.0291 | 154.7229 | 157.8157 | 165.586 | 172.6313 | 0.081337 | 0.16157 | 0.25841 | 0.37345 | 0.49854 | 0.64471 | 0.81477 | 1.1981 | 1.5198 | 1.8274 | -0.75453 | -0.92555 | -1.1091 | -1.2815 | -1.4258 | -1.5466 | -1.6507 | -1.7197 | -1.8051 | -1.873
Sorell | 41517 | 73.5172 | 94.1657 | 94.1657 | 95.5999 | 98.9989 | 101.3795 | 101.8968 | 102.4375 | 103.2508 | 106.5359 | 113.3731 | 120.2167 | 126.0728 | 119.7774 | 119.7774 | 123.5084 | 125.9198 | 128.2092 | 129.0337 | 130.0416 | 131.481 | 134.1092 | 140.7122 | 146.6992 | 0.092548 | 0.18861 | 0.2997 | 0.42015 | 0.53998 | 0.66787 | 0.8071 | 1.0975 | 1.3476 | 1.5807 | -0.8823 | -1.1037 | -1.3446 | -1.5802 | -1.7886 | -1.9791 | -2.161 | -2.3785 | -2.5941 | -2.7864
Sorell | 41518 | 77.4235 | 133.1709 | 133.1709 | 135.199 | 140.006 | 143.3728 | 144.1043 | 144.869 | 146.0191 | 150.665 | 160.3343 | 170.0126 | 144.6642 | 123.1853 | 123.1853 | 127.0224 | 129.5025 | 131.857 | 132.705 | 133.7415 | 135.2219 | 137.9249 | 144.7158 | 150.8731 | 0.097933 | 0.19903 | 0.31603 | 0.44307 | 0.56965 | 0.70498 | 0.85252 | 1.1605 | 1.4258 | 1.6732 | -0.93085 | -1.1636 | -1.4168 | -1.6643 | -1.883 | -2.0828 | -2.2733 | -2.5 | -2.7251 | -2.9257
St Leonards | 66101 | 29.1552 | 35.8892 | 35.8892 | 36.4358 | 37.7312 | 38.6386 | 38.8357 | 39.0418 | 39.3518 | 40.6038 | 43.2096 | 45.8179 | 56.9214 | 56.0902 | 56.0902 | 57.8374 | 58.9667 | 60.0387 | 60.4249 | 60.8968 | 61.5709 | 62.8017 | 65.8938 | 68.6974 | 0.027116 | 0.052079 | 0.081358 | 0.11391 | 0.14706 | 0.1832 | 0.22311 | 0.30862 | 0.38012 | 0.44633 | -0.25842 | -0.31543 | -0.37763 | -0.43823 | -0.49163 | -0.53999 | -0.5856 | -0.63739 | -0.68851 | -0.73323
St Leonards | 66102 | 71.2726 | 145.4878 | 145.4878 | 147.7036 | 152.9552 | 156.6333 | 157.4325 | 158.268 | 159.5244 | 164.6 | 175.1636 | 185.7371 | 181.1835 | 159.9146 | 159.9146 | 164.8958 | 168.1154 | 171.1719 | 172.2727 | 173.6183 | 175.54 | 179.049 | 187.8647 | 195.8579 | 0.075664 | 0.14536 | 0.22708 | 0.31789 | 0.41028 | 0.51095 | 0.6221 | 0.85999 | 1.059 | 1.2431 | -0.72217 | -0.88145 | -1.0553 | -1.2247 | -1.374 | -1.5094 | -1.6372 | -1.7827 | -1.9262 | -2.0518
St Leonards | 66103 | 80.0222 | 119.4524 | 119.4524 | 121.2717 | 125.5835 | 128.6034 | 129.2596 | 129.9455 | 130.9771 | 135.1444 | 143.8176 | 152.499 | 197.898 | 189.8475 | 189.8475 | 195.7611 | 199.5833 | 203.2119 | 204.5188 | 206.1163 | 208.3977 | 212.5635 | 223.0293 | 232.5187 | 0.063744 | 0.12291 | 0.19246 | 0.26996 | 0.34899 | 0.43526 | 0.53092 | 0.73542 | 0.90644 | 1.0647 | -0.6277 | -0.76321 | -0.91145 | -1.0564 | -1.1846 | -1.3011 | -1.4115 | -1.5378 | -1.6623 | -1.7719
St Leonards | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | 66105 | 52.8 | 91.8403 | 91.8403 | 93.239 | 96.5541 | 98.876 | 99.3805 | 99.9079 | 100.701 | 103.905 | 110.5734 | 117.2479 | 107.0744 | 101.7094 | 101.7094 | 104.8775 | 106.9252 | 108.8692 | 109.5694 | 110.4252 | 111.6475 | 113.8793 | 119.4863 | 124.5701 | 0.051841 | 0.099584 | 0.15557 | 0.21777 | 0.28105 | 0.35001 | 0.42614 | 0.58908 | 0.72535 | 0.85146 | -0.49454 | -0.60365 | -0.72271 | -0.83876 | -0.94107 | -1.0338 | -1.1213 | -1.2209 | -1.3192 | -1.4052
St Leonards | 66106 | 158.1003 | 140.5378 | 140.5378 | 142.6781 | 147.751 | 151.304 | 152.076 | 152.883 | 154.0968 | 158.9996 | 169.2038 | 179.4175 | 160.5713 | 170.5078 | 170.5078 | 175.8189 | 179.2517 | 182.5107 | 183.6845 | 185.1192 | 187.1682 | 190.9097 | 200.3093 | 208.832 | 0.060195 | 0.11666 | 0.18324 | 0.25771 | 0.33389 | 0.41724 | 0.51019 | 0.70859 | 0.87449 | 1.0281 | -0.61772 | -0.74741 | -0.88974 | -1.0294 | -1.1535 | -1.2668 | -1.3747 | -1.4987 | -1.621 | -1.7293
St Leonards | 66107 | 44.7893 | 93.8911 | 93.8911 | 95.321 | 98.7102 | 101.0839 | 101.5997 | 102.1388 | 102.9497 | 106.2252 | 113.0425 | 119.8661 | 99.5743 | 96.8705 | 96.8705 | 99.888 | 101.8383 | 103.6898 | 104.3566 | 105.1717 | 106.3358 | 108.4615 | 113.8017 | 118.6437 | 0.023347 | 0.044848 | 0.07006 | 0.098074 | 0.12657 | 0.15763 | 0.19191 | 0.26529 | 0.32666 | 0.38346 | -0.22272 | -0.27185 | -0.32547 | -0.37774 | -0.42381 | -0.46556 | -0.50497 | -0.54985 | -0.5941 | -0.63285
St Leonards | 66108 | 3.2 | 4.1191 | 4.1191 | 4.1819 | 4.3306 | 4.4347 | 4.4573 | 4.481 | 4.5165 | 4.6603 | 4.9593 | 5.2587 | 3.6827 | 4.3717 | 4.3717 | 4.5079 | 4.5959 | 4.6794 | 4.7095 | 4.7463 | 4.7988 | 4.8948 | 5.1358 | 5.3543 | 8.1065e-05 | 0.00015572 | 0.00024327 | 0.00034053 | 0.00043949 | 0.00054732 | 0.00066637 | 0.00092115 | 0.0011342 | 0.0013314 | -0.00077332 | -0.00094393 | -0.0011301 | -0.0013116 | -0.0014716 | -0.0016165 | -0.0017534 | -0.0019092 | -0.0020629 | -0.0021974
St Leonards | 66109 | 26.9479 | 32.8257 | 32.8257 | 33.3256 | 34.5105 | 35.3404 | 35.5207 | 35.7092 | 35.9927 | 37.1379 | 39.5213 | 41.9069 | 57.3 | 55.954 | 55.954 | 57.697 | 58.8235 | 59.893 | 60.2781 | 60.749 | 61.4214 | 62.6492 | 65.7338 | 68.5306 | 0.025738 | 0.049442 | 0.077237 | 0.10812 | 0.13954 | 0.17377 | 0.21157 | 0.29247 | 0.36012 | 0.42274 | -0.24553 | -0.2997 | -0.35881 | -0.41643 | -0.46722 | -0.51324 | -0.55669 | -0.60617 | -0.65496 | -0.69767
St Leonards | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | 57003 | 26 | 35.2379 | 35.2379 | 35.7745 | 37.0465 | 37.9374 | 38.1309 | 38.3333 | 38.6376 | 39.8669 | 42.4255 | 44.9864 | 35.3797 | 39.2482 | 39.2482 | 40.4707 | 41.2609 | 42.011 | 42.2812 | 42.6115 | 43.0831 | 43.9443 | 46.108 | 48.0698 | 0.02466 | 0.049441 | 0.079589 | 0.11593 | 0.15594 | 0.20322 | 0.25861 | 0.38459 | 0.4898 | 0.59053 | -0.21612 | -0.26843 | -0.32445 | -0.37651 | -0.4195 | -0.45455 | -0.48371 | -0.49789 | -0.51811 | -0.53265
St Marys | 57004 | 127 | 157.1677 | 157.1677 | 159.5613 | 165.2345 | 169.2079 | 170.0713 | 170.9738 | 172.3311 | 177.8142 | 189.2258 | 200.6481 | 168.4184 | 156.1173 | 156.1173 | 160.9802 | 164.1233 | 167.1072 | 168.182 | 169.4956 | 171.3717 | 174.7973 | 183.4037 | 191.2071 | 0.094146 | 0.1887 | 0.30376 | 0.44251 | 0.59533 | 0.77594 | 0.98757 | 1.4691 | 1.8712 | 2.2562 | -0.82452 | -1.0241 | -1.2378 | -1.4364 | -1.6004 | -1.7341 | -1.8453 | -1.8991 | -1.976 | -2.0313
St Marys | 57005 | 58.0021 | 91.1552 | 91.1552 | 92.5434 | 95.8338 | 98.1383 | 98.6391 | 99.1625 | 99.9498 | 103.1298 | 109.7485 | 116.3732 | 60.4225 | 81.8281 | 81.8281 | 84.377 | 86.0244 | 87.5884 | 88.1517 | 88.8403 | 89.8236 | 91.6192 | 96.1301 | 100.2202 | 0.012056 | 0.024197 | 0.038981 | 0.056836 | 0.076529 | 0.099831 | 0.12716 | 0.1894 | 0.24136 | 0.29113 | -0.1052 | -0.13079 | -0.15817 | -0.1836 | -0.20457 | -0.22161 | -0.23574 | -0.24231 | -0.25191 | -0.25872
St Marys | 57006 | 131 | 165.2478 | 165.2478 | 167.7645 | 173.7293 | 177.9071 | 178.8148 | 179.7637 | 181.1908 | 186.9557 | 198.9541 | 210.9636 | 194.7492 | 212.9991 | 212.9991 | 219.6338 | 223.9221 | 227.9933 | 229.4595 | 231.2518 | 233.8114 | 238.4852 | 250.2274 | 260.8739 | 0.14392 | 0.29403 | 0.47077 | 0.67068 | 0.87845 | 1.1108 | 1.3728 | 1.9406 | 2.42 | 2.8721 | -1.5983 | -1.9306 | -2.2883 | -2.6287 | -2.9198 | -3.173 | -3.4014 | -3.6189 | -3.8463 | -4.0374
Summerleas Zone | 32374 | 103.6504 | 143.3019 | 143.3019 | 145.4843 | 150.657 | 154.2799 | 155.0671 | 155.8899 | 157.1275 | 162.1268 | 172.5317 | 182.9463 | 247.3439 | 225.4492 | 225.4492 | 232.4717 | 237.0107 | 241.3198 | 242.8718 | 244.7688 | 247.478 | 252.425 | 264.8535 | 276.1224 | 0.0488 | 0.096863 | 0.1533 | 0.21622 | 0.28051 | 0.35101 | 0.42933 | 0.59685 | 0.7396 | 0.87343 | -0.45729 | -0.5673 | -0.68757 | -0.80524 | -0.90928 | -1.0039 | -1.0936 | -1.1953 | -1.298 | -1.389
Summerleas Zone | 32377 | 123.3333 | 128.6083 | 128.6083 | 130.567 | 135.2092 | 138.4606 | 139.1671 | 139.9056 | 141.0163 | 145.503 | 154.841 | 164.1878 | 160.1844 | 155.6702 | 155.6702 | 160.5191 | 163.6532 | 166.6286 | 167.7003 | 169.0101 | 170.8808 | 174.2967 | 182.8784 | 190.6594 | 0.015577 | 0.030919 | 0.048935 | 0.069017 | 0.089539 | 0.11204 | 0.13704 | 0.19052 | 0.23608 | 0.2788 | -0.14597 | -0.18108 | -0.21947 | -0.25704 | -0.29025 | -0.32044 | -0.34908 | -0.38154 | -0.41433 | -0.44336
Summerleas Zone | 32379 | 132.7569 | 169.0052 | 169.0052 | 171.5791 | 177.6796 | 181.9523 | 182.8807 | 183.8512 | 185.3108 | 191.2067 | 203.4779 | 215.7605 | 278.6 | 254.8663 | 254.8663 | 262.8052 | 267.9364 | 272.8077 | 274.5622 | 276.7068 | 279.7695 | 285.362 | 299.4122 | 312.1515 | 0.063507 | 0.1261 | 0.19954 | 0.28131 | 0.36477 | 0.4562 | 0.55769 | 0.77467 | 0.95949 | 1.1327 | -0.59364 | -0.73689 | -0.89342 | -1.0465 | -1.1819 | -1.3049 | -1.4216 | -1.5542 | -1.688 | -1.8064
Trevallyn | 61021 | 73.4555 | 157.1077 | 157.1077 | 159.5004 | 165.1714 | 169.1433 | 170.0064 | 170.9085 | 172.2654 | 177.7463 | 189.1536 | 200.5715 | 152.0531 | 158.5757 | 158.5757 | 163.5152 | 166.7077 | 169.7387 | 170.8303 | 172.1646 | 174.0702 | 177.5498 | 186.2917 | 194.218 | 0.09926 | 0.17682 | 0.26634 | 0.36452 | 0.46368 | 0.57162 | 0.69081 | 0.94311 | 1.1554 | 1.3532 | -0.87905 | -1.0491 | -1.2302 | -1.4015 | -1.5477 | -1.6755 | -1.7918 | -1.9147 | -2.0364 | -2.1403
Trevallyn | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61023 | 77.4793 | 97.0783 | 97.0783 | 98.5568 | 102.0609 | 104.5152 | 105.0485 | 105.6059 | 106.4443 | 109.8311 | 116.8797 | 123.935 | 135.991 | 136.7606 | 136.7606 | 141.0206 | 143.774 | 146.388 | 147.3294 | 148.4802 | 150.1236 | 153.1246 | 160.6638 | 167.4997 | 0.11482 | 0.21081 | 0.3216 | 0.44368 | 0.56782 | 0.70419 | 0.85602 | 1.1811 | 1.4553 | 1.7127 | -1.0474 | -1.2553 | -1.4751 | -1.6804 | -1.8528 | -2.0003 | -2.1311 | -2.2575 | -2.3862 | -2.4929
Trevallyn | 61024 | 149 | 142.0229 | 157.2066 | 144.1858 | 149.3123 | 152.9029 | 153.6831 | 154.4986 | 155.7251 | 160.6798 | 170.9918 | 181.3135 | 162.0917 | 163.4328 | 176.7889 | 168.5236 | 171.814 | 174.9377 | 176.0628 | 177.438 | 179.402 | 182.9882 | 191.9978 | 200.1668 | 0.013862 | 0.026629 | 0.041598 | 0.058231 | 0.075153 | 0.093592 | 0.11395 | 0.15752 | 0.19396 | 0.22768 | -0.13224 | -0.16141 | -0.19325 | -0.22428 | -0.25164 | -0.27642 | -0.29982 | -0.32647 | -0.35275 | -0.37575
Trevallyn | 61025 | 71.2568 | 89.6829 | 89.6829 | 162.343 | 94.286 | 96.5533 | 97.046 | 97.561 | 98.3355 | 101.4642 | 107.9759 | 114.4937 | 160.0595 | 170.5526 | 170.5526 | 239.5615 | 179.2989 | 182.5587 | 183.7328 | 185.1679 | 187.2174 | 190.9598 | 200.362 | 208.8869 | 0.068739 | 0.13217 | 0.20659 | 0.28933 | 0.37356 | 0.46538 | 0.56686 | 0.78399 | 0.96559 | 1.1337 | -0.66087 | -0.8059 | -0.96425 | -1.1187 | -1.255 | -1.3786 | -1.4953 | -1.6285 | -1.7597 | -1.8748
Trevallyn | 61026 | 118.3333 | 122.5307 | 122.5307 | 124.3969 | 128.8198 | 131.9175 | 132.5906 | 133.2942 | 134.3524 | 138.6271 | 147.5238 | 156.4289 | 106 | 103.1198 | 103.1198 | 106.3319 | 108.408 | 110.379 | 111.0888 | 111.9565 | 113.1957 | 115.4585 | 121.1432 | 126.2976 | 0.0087478 | 0.016805 | 0.026254 | 0.036753 | 0.047435 | 0.059075 | 0.071927 | 0.099432 | 0.12244 | 0.14373 | -0.083503 | -0.10192 | -0.12201 | -0.1416 | -0.15887 | -0.17452 | -0.1893 | -0.20612 | -0.22271 | -0.23724
Trevallyn | 61027 | 83.632 | 111.6159 | 111.6159 | 113.3158 | 117.3448 | 120.1666 | 120.7797 | 121.4206 | 122.3846 | 126.2785 | 134.3827 | 142.4945 | 239 | 196.3538 | 196.3538 | 202.4701 | 206.4232 | 210.1762 | 211.5279 | 213.1801 | 215.5397 | 219.8483 | 230.6728 | 240.4874 | 0.093281 | 0.17926 | 0.2801 | 0.39217 | 0.50622 | 0.63052 | 0.7678 | 1.0616 | 1.3073 | 1.5347 | -0.89274 | -1.0893 | -1.3038 | -1.5129 | -1.6974 | -1.8645 | -2.0224 | -2.2023 | -2.3796 | -2.535
Trevallyn | 61028 | 99.3333 | 128.8617 | 128.8617 | 130.8243 | 135.4757 | 138.7335 | 139.4414 | 140.1814 | 141.2943 | 145.7898 | 155.1462 | 164.5114 | 193.6667 | 200.182 | 200.182 | 206.4175 | 210.4477 | 214.2739 | 215.6519 | 217.3363 | 219.7419 | 224.1345 | 235.17 | 245.176 | 0.15497 | 0.27836 | 0.41899 | 0.57 | 0.71953 | 0.87925 | 1.0532 | 1.4149 | 1.721 | 2.0053 | -1.4087 | -1.6789 | -1.9647 | -2.2336 | -2.462 | -2.6615 | -2.8427 | -3.0418 | -3.2358 | -3.4013
Trevallyn | 61029 | 51 | 63.1485 | 63.1485 | 64.1102 | 66.3896 | 67.9861 | 68.333 | 68.6956 | 69.241 | 71.444 | 76.0291 | 80.6185 | 98.3626 | 110.7748 | 110.7748 | 114.2254 | 116.4556 | 118.5729 | 119.3355 | 120.2676 | 121.5987 | 124.0295 | 130.1362 | 135.6732 | 0.030568 | 0.061897 | 0.099079 | 0.14102 | 0.18425 | 0.23186 | 0.28514 | 0.3994 | 0.49538 | 0.58465 | -0.3273 | -0.39953 | -0.47926 | -0.55799 | -0.62835 | -0.69297 | -0.75482 | -0.82584 | -0.89684 | -0.96027
Trevallyn | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61037 | 50.3333 | 72.0821 | 72.0821 | 73.1799 | 75.7818 | 77.6041 | 78.0001 | 78.414 | 79.0365 | 81.5512 | 86.785 | 92.0236 | 95.7018 | 84.319 | 84.319 | 86.9454 | 88.643 | 90.2547 | 90.8351 | 91.5446 | 92.5579 | 94.4081 | 99.0564 | 103.271 | 0.036439 | 0.069997 | 0.10935 | 0.15307 | 0.19755 | 0.24602 | 0.29953 | 0.41406 | 0.50984 | 0.59849 | -0.34761 | -0.4243 | -0.50799 | -0.58956 | -0.66147 | -0.72663 | -0.78813 | -0.85818 | -0.92725 | -0.98772
Trevallyn | 61039 | 122 | 138.0961 | 138.0961 | 140.1993 | 145.184 | 148.6753 | 149.4339 | 150.2269 | 151.4195 | 156.2372 | 166.2641 | 176.3004 | 148.0539 | 155.0387 | 155.0387 | 159.868 | 162.9894 | 165.9527 | 167.02 | 168.3245 | 170.1876 | 173.5896 | 182.1365 | 189.886 | 0.026062 | 0.050065 | 0.07821 | 0.10948 | 0.1413 | 0.17596 | 0.21424 | 0.29615 | 0.36466 | 0.42806 | -0.24862 | -0.30347 | -0.36333 | -0.42167 | -0.47311 | -0.51971 | -0.5637 | -0.6138 | -0.66321 | -0.70646
Trevallyn | 61040 | 115.6667 | 125.7604 | 125.7604 | 127.6757 | 132.2152 | 135.3946 | 136.0854 | 136.8076 | 137.8937 | 142.281 | 151.4122 | 160.552 | 168.5095 | 177.5642 | 177.5642 | 183.0952 | 186.6701 | 190.0639 | 191.2863 | 192.7804 | 194.9142 | 198.8104 | 208.5991 | 217.4745 | 0.04655 | 0.089425 | 0.1397 | 0.19556 | 0.2524 | 0.31433 | 0.38271 | 0.52905 | 0.65144 | 0.76471 | -0.44423 | -0.54221 | -0.64913 | -0.75336 | -0.84524 | -0.9285 | -1.0071 | -1.0966 | -1.1849 | -1.2622
Trevallyn | 61041 | 70.1037 | 82.2541 | 82.2541 | 83.5068 | 86.4758 | 88.5554 | 89.0072 | 89.4795 | 90.1899 | 93.0594 | 99.0318 | 105.0097 | 160.7499 | 144.4567 | 144.4567 | 148.9564 | 151.8647 | 154.6258 | 155.6202 | 156.8357 | 158.5717 | 161.7415 | 169.705 | 176.9255 | 0.069776 | 0.13432 | 0.2101 | 0.29444 | 0.38035 | 0.47406 | 0.57776 | 0.79958 | 0.98509 | 1.1568 | -0.67749 | -0.82516 | -0.98653 | -1.1441 | -1.2832 | -1.4095 | -1.529 | -1.6654 | -1.7999 | -1.918
Trevallyn | 61043 | 111 | 137.5106 | 137.5106 | 139.6048 | 144.5684 | 148.0449 | 148.8003 | 149.5899 | 150.7775 | 155.5748 | 165.5591 | 175.5529 | 298.4291 | 241.0118 | 241.0118 | 248.5191 | 253.3714 | 257.978 | 259.6371 | 261.665 | 264.5613 | 269.8498 | 283.1362 | 295.183 | 0.14013 | 0.25832 | 0.39654 | 0.5513 | 0.71061 | 0.88713 | 1.0846 | 1.5092 | 1.8655 | 2.199 | -1.2734 | -1.5336 | -1.8127 | -2.0779 | -2.3049 | -2.503 | -2.6828 | -2.8633 | -3.0463 | -3.2015
Triabunna | 43505 | 0 | 20.2866 | 20.2866 | 20.5956 | 21.3278 | 21.8407 | 21.9522 | 22.0687 | 22.2439 | 22.9516 | 24.4246 | 25.8989 | 0 | 20.9097 | 20.9097 | 21.561 | 21.982 | 22.3817 | 22.5256 | 22.7015 | 22.9528 | 23.4116 | 24.5643 | 25.6095 | 0.012076 | 0.023776 | 0.038117 | 0.055604 | 0.075039 | 0.098194 | 0.1255 | 0.18802 | 0.24046 | 0.29092 | -0.10964 | -0.13436 | -0.16096 | -0.1859 | -0.20666 | -0.22375 | -0.23817 | -0.24535 | -0.25578 | -0.26374
Triabunna | 43506 | 68.6206 | 54.6538 | 54.6538 | 55.4862 | 57.459 | 58.8407 | 59.1409 | 59.4548 | 59.9268 | 61.8334 | 65.8018 | 69.7738 | 94.8244 | 71.1202 | 71.1202 | 73.3356 | 74.7674 | 76.1268 | 76.6164 | 77.2148 | 78.0695 | 79.63 | 83.5507 | 87.1056 | 0.06503 | 0.12803 | 0.20526 | 0.29942 | 0.40408 | 0.52876 | 0.67582 | 1.0125 | 1.2948 | 1.5666 | -0.59039 | -0.72349 | -0.86677 | -1.0011 | -1.1128 | -1.2049 | -1.2825 | -1.3212 | -1.3774 | -1.4202
Triabunna | 43507 | 83.3138 | 108.1767 | 108.1767 | 109.8242 | 113.7289 | 116.4638 | 117.0581 | 117.6792 | 118.6135 | 122.3874 | 130.2419 | 138.1037 | 118.3747 | 96.0948 | 96.0948 | 99.0881 | 101.0228 | 102.8595 | 103.521 | 104.3296 | 105.4843 | 107.5929 | 112.8904 | 117.6936 | 0.064906 | 0.12779 | 0.20486 | 0.29885 | 0.4033 | 0.52775 | 0.67453 | 1.0105 | 1.2924 | 1.5636 | -0.58926 | -0.7221 | -0.86511 | -0.99915 | -1.1107 | -1.2025 | -1.2801 | -1.3187 | -1.3747 | -1.4175
Trial Harbour Zone | 99981 | 31.1818 | 38.8774 | 38.8774 | 39.4695 | 40.8728 | 41.8557 | 42.0693 | 42.2925 | 42.6283 | 43.9846 | 46.8074 | 49.6328 | 44.543 | 44.0288 | 44.0288 | 45.4002 | 46.2866 | 47.1282 | 47.4313 | 47.8018 | 48.3309 | 49.297 | 51.7242 | 53.9249 | 0.061011 | 0.1021 | 0.17688 | 0.32628 | 0.5477 | 0.87131 | 1.3001 | 2.4108 | 3.3154 | 4.2165 | -0.059888 | -0.069869 | -0.064775 | -0.016832 | 0.021276 | 0.02696 | 0.033489 | 0.04714 | 0.059035 | 0.070387
Trial Harbour Zone | 99982 | 23.6667 | 220.2717 | 184.2104 | 223.6264 | 231.5774 | 237.1462 | 238.3562 | 239.6211 | 241.5234 | 249.2079 | 265.2014 | 281.2099 | 28.7912 | 57.7178 | 25.997 | 59.5157 | 60.6777 | 61.7809 | 62.1782 | 62.6639 | 63.3575 | 64.624 | 67.8058 | 70.6908 | 9.4419e-05 | 0.00015798 | 0.00027371 | 0.00050508 | 0.00084804 | 0.0013493 | 0.0020136 | 0.0037344 | 0.0051358 | 0.0065318 | -9.1318e-05 | -0.00010645 | -9.8186e-05 | -2.3535e-05 | 3.2727e-05 | 4.1484e-05 | 5.1548e-05 | 7.26e-05 | 9.0941e-05 | 0.00010845
Trial Harbour Zone | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00018884 | 0.00031595 | 0.00054742 | 0.0010102 | 0.0016961 | 0.0026987 | 0.0040271 | 0.0074689 | 0.010272 | 0.013064 | -0.00018264 | -0.0002129 | -0.00019637 | -4.707e-05 | 6.5453e-05 | 8.2968e-05 | 0.0001031 | 0.0001452 | 0.00018188 | 0.00021689
Tungatinah | 49302 | 11.0667 | 9.788 | 9.788 | 9.937 | 10.2903 | 10.5378 | 10.5916 | 10.6478 | 10.7323 | 11.0738 | 11.7844 | 12.4958 | 11.0774 | 7.6672 | 7.6672 | 7.906 | 8.0604 | 8.207 | 8.2597 | 8.3242 | 8.4164 | 8.5846 | 9.0073 | 9.3905 | 3.7539e-05 | 7.4867e-05 | 0.00012259 | 0.00018502 | 0.00025832 | 0.00034971 | 0.00046066 | 0.00072308 | 0.00094143 | 0.0011534 | -0.0003157 | -0.00038994 | -0.00046959 | -0.00054225 | -0.00060003 | -0.00064324 | -0.00067487 | -0.0006594 | -0.00066255 | -0.00065806
Tungatinah | 49303 | 22.6651 | 24.4543 | 24.4543 | 24.8267 | 25.7094 | 26.3277 | 26.462 | 26.6024 | 26.8136 | 27.6668 | 29.4423 | 31.2196 | 23.1627 | 22.9596 | 22.9596 | 23.6748 | 24.137 | 24.5758 | 24.7339 | 24.9271 | 25.203 | 25.7068 | 26.9725 | 28.1201 | 0.010548 | 0.021038 | 0.034448 | 0.05199 | 0.072587 | 0.098269 | 0.12944 | 0.20319 | 0.26454 | 0.32412 | -0.088712 | -0.10957 | -0.13196 | -0.15237 | -0.16861 | -0.18075 | -0.18964 | -0.18529 | -0.18618 | -0.18491
Tungatinah | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7539e-05 | 7.4867e-05 | 0.00012259 | 0.00018502 | 0.00025832 | 0.00034971 | 0.00046066 | 0.00072308 | 0.00094143 | 0.0011534 | -0.0003157 | -0.00038994 | -0.00046959 | -0.00054225 | -0.00060003 | -0.00064324 | -0.00067487 | -0.0006594 | -0.00066255 | -0.00065806
Tungatinah | 49307 | 0 | 13.0506 | 13.0506 | 13.2494 | 13.7204 | 14.0504 | 14.1221 | 14.197 | 14.3097 | 14.765 | 15.7126 | 16.6611 | 0 | 5.7399 | 5.7399 | 5.9187 | 6.0342 | 6.144 | 6.1835 | 6.2318 | 6.3007 | 6.4267 | 6.7431 | 7.03 | 0.000488 | 0.00097327 | 0.0015937 | 0.0024052 | 0.0033581 | 0.0045463 | 0.0059885 | 0.0094 | 0.012239 | 0.014995 | -0.0041041 | -0.0050692 | -0.0061047 | -0.0070493 | -0.0078004 | -0.0083621 | -0.0087733 | -0.0085722 | -0.0086132 | -0.0085548
Ulverstone | 82001 | 106.7451 | 129.3098 | 129.3098 | 131.2792 | 135.9468 | 139.2159 | 139.9263 | 140.6688 | 141.7856 | 146.2967 | 155.6857 | 165.0834 | 68.4772 | 85.5925 | 85.5925 | 88.2586 | 89.9818 | 91.6178 | 92.207 | 92.9272 | 93.9558 | 95.8339 | 100.5524 | 104.8307 | 0.018071 | 0.03737 | 0.060201 | 0.085821 | 0.11211 | 0.14096 | 0.17293 | 0.24143 | 0.29934 | 0.35332 | -0.18642 | -0.23098 | -0.28008 | -0.32846 | -0.37161 | -0.41113 | -0.44887 | -0.49208 | -0.53554 | -0.5743
Ulverstone | 82002 | 85.4201 | 144.9598 | 144.9598 | 147.1675 | 152.4 | 156.0648 | 156.8611 | 157.6935 | 158.9454 | 164.0026 | 174.5278 | 185.0629 | 170.9505 | 164.1856 | 164.1856 | 169.2998 | 172.6054 | 175.7435 | 176.8738 | 178.2553 | 180.2283 | 183.831 | 192.8822 | 201.0889 | 0.090344 | 0.18231 | 0.29005 | 0.40932 | 0.5303 | 0.66174 | 0.80648 | 1.1119 | 1.3718 | 1.6137 | -0.94812 | -1.1594 | -1.3904 | -1.6159 | -1.815 | -1.9958 | -2.1668 | -2.3617 | -2.5554 | -2.7274
Ulverstone | 82003 | 102.4817 | 207.5455 | 207.5455 | 210.7064 | 218.198 | 223.4451 | 224.5852 | 225.777 | 227.5694 | 234.8099 | 249.8794 | 264.963 | 181.1676 | 204.4035 | 204.4035 | 210.7705 | 214.8858 | 218.7926 | 220.1997 | 221.9197 | 224.376 | 228.8612 | 240.1295 | 250.3464 | 0.10638 | 0.20399 | 0.31817 | 0.44492 | 0.57404 | 0.71522 | 0.87151 | 1.2021 | 1.4821 | 1.7438 | -1.0031 | -1.2244 | -1.4646 | -1.6967 | -1.8992 | -2.0805 | -2.2493 | -2.4336 | -2.6183 | -2.7799
Ulverstone | 82004 | 53.9248 | 63.7305 | 63.7305 | 64.7011 | 67.0015 | 68.6127 | 68.9628 | 69.3288 | 69.8792 | 72.1025 | 76.7299 | 81.3615 | 53.8737 | 30.8464 | 30.8464 | 31.8072 | 32.4282 | 33.0178 | 33.2301 | 33.4897 | 33.8604 | 34.5372 | 36.2377 | 37.7795 | 0.034309 | 0.069294 | 0.11028 | 0.15564 | 0.20166 | 0.25165 | 0.30669 | 0.42283 | 0.52169 | 0.61367 | -0.36067 | -0.44107 | -0.52894 | -0.61476 | -0.69056 | -0.75939 | -0.82449 | -0.89877 | -0.97254 | -1.0381
Ulverstone | 82005 | 87.836 | 94.935 | 94.935 | 96.3808 | 99.8076 | 102.2077 | 102.7292 | 103.2744 | 104.0943 | 107.4062 | 114.2993 | 121.1988 | 165.1723 | 155.9156 | 155.9156 | 160.7723 | 163.9113 | 166.8914 | 167.9647 | 169.2766 | 171.1503 | 174.5715 | 183.1668 | 190.9601 | 0.075084 | 0.15165 | 0.24133 | 0.34061 | 0.44132 | 0.55072 | 0.67118 | 0.92533 | 1.1417 | 1.343 | -0.78931 | -0.96525 | -1.1576 | -1.3454 | -1.5113 | -1.6619 | -1.8044 | -1.9669 | -2.1283 | -2.2718
Ulverstone | 82006 | 96.5115 | 135.5406 | 135.5406 | 137.6048 | 142.4973 | 145.924 | 146.6686 | 147.4469 | 148.6175 | 153.346 | 163.1873 | 173.0379 | 107.7824 | 111.928 | 111.928 | 115.4144 | 117.6679 | 119.8072 | 120.5777 | 121.5195 | 122.8646 | 125.3206 | 131.4909 | 137.0855 | 0.0086467 | 0.017464 | 0.027792 | 0.039226 | 0.050822 | 0.063422 | 0.077294 | 0.10656 | 0.13148 | 0.15466 | -0.090898 | -0.11116 | -0.13331 | -0.15493 | -0.17404 | -0.19138 | -0.20779 | -0.22651 | -0.2451 | -0.26163
Ulverstone | 82007 | 43.18 | 46.2209 | 46.2209 | 46.9249 | 48.5933 | 49.7618 | 50.0157 | 50.2811 | 50.6803 | 52.2928 | 55.6488 | 59.0079 | 24.1218 | 64.7854 | 64.7854 | 66.8035 | 68.1078 | 69.346 | 69.792 | 70.3372 | 71.1157 | 72.5373 | 76.1087 | 79.347 | 0.020454 | 0.04146 | 0.066105 | 0.093447 | 0.12123 | 0.15147 | 0.18479 | 0.25528 | 0.31522 | 0.37101 | -0.21441 | -0.26272 | -0.31559 | -0.36729 | -0.41304 | -0.45463 | -0.49404 | -0.53902 | -0.58378 | -0.62359
Ulverstone | 82008 | 158.272 | 188.9537 | 188.9537 | 191.8315 | 198.652 | 203.429 | 204.467 | 205.552 | 207.1839 | 213.7758 | 227.4954 | 241.2278 | 173.7736 | 170.0912 | 170.0912 | 175.3894 | 178.8138 | 182.0649 | 183.2358 | 184.667 | 186.711 | 190.4433 | 199.82 | 208.3218 | 0.075362 | 0.15221 | 0.24222 | 0.34187 | 0.44295 | 0.55276 | 0.67366 | 0.92876 | 1.1459 | 1.348 | -0.79223 | -0.96882 | -1.1618 | -1.3503 | -1.5168 | -1.668 | -1.811 | -1.9742 | -2.1362 | -2.2802
Waddamana | 49202 | 0 | 18.2804 | 18.2804 | 18.5589 | 19.2187 | 19.6809 | 19.7813 | 19.8863 | 20.0441 | 20.6819 | 22.0092 | 23.3377 | 19.4535 | 17.7252 | 17.7252 | 18.2773 | 18.6342 | 18.973 | 19.095 | 19.2441 | 19.4571 | 19.8461 | 20.8232 | 21.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wayatinah | 49411 | 7.9901 | 18.4616 | 18.4616 | 18.7428 | 19.4092 | 19.8759 | 19.9773 | 20.0833 | 20.2428 | 20.8868 | 22.2273 | 23.569 | 12.3661 | 17.2197 | 17.2197 | 17.7561 | 18.1027 | 18.4319 | 18.5504 | 18.6953 | 18.9022 | 19.2801 | 20.2294 | 21.0901 | 0.0023649 | 0.0047166 | 0.0077232 | 0.011656 | 0.016274 | 0.022032 | 0.029021 | 0.045554 | 0.05931 | 0.072667 | -0.019889 | -0.024566 | -0.029584 | -0.034162 | -0.037802 | -0.040524 | -0.042517 | -0.041542 | -0.041741 | -0.041458
Wayatinah | 49412 | 27 | 35.8892 | 35.8892 | 36.4358 | 37.7312 | 38.6386 | 38.8357 | 39.0418 | 39.3518 | 40.6038 | 43.2096 | 45.8179 | 26 | 28.6995 | 28.6995 | 29.5934 | 30.1712 | 30.7198 | 30.9174 | 31.1588 | 31.5037 | 32.1335 | 33.7156 | 35.1501 | 0.00097601 | 0.0019465 | 0.0031873 | 0.0048105 | 0.0067162 | 0.0090925 | 0.011977 | 0.0188 | 0.024477 | 0.029989 | -0.0082082 | -0.010138 | -0.012209 | -0.014099 | -0.015601 | -0.016724 | -0.017547 | -0.017144 | -0.017226 | -0.01711
Wesley Vale | 81001 | 32.1937 | 39.1518 | 58.1315 | 39.7481 | 41.1613 | 42.1512 | 42.3662 | 42.5911 | 42.9292 | 44.2951 | 47.1378 | 49.9832 | 43.0834 | 45.1675 | 61.8627 | 46.5745 | 47.4838 | 48.3471 | 48.6581 | 49.0381 | 49.5809 | 50.572 | 53.062 | 55.3196 | 0.016094 | 0.033468 | 0.054053 | 0.07721 | 0.10102 | 0.12721 | 0.15627 | 0.21868 | 0.27139 | 0.32054 | -0.16608 | -0.20619 | -0.25042 | -0.29405 | -0.33298 | -0.36867 | -0.40276 | -0.44172 | -0.48099 | -0.51601
Wesley Vale | 81002 | 55.5342 | 70.4102 | 70.4102 | 71.4826 | 74.0241 | 75.8042 | 76.191 | 76.5953 | 77.2034 | 79.6597 | 84.7721 | 89.8892 | 57.5358 | 67.2005 | 67.2005 | 69.2938 | 70.6467 | 71.9312 | 72.3938 | 72.9592 | 73.7668 | 75.2414 | 78.9459 | 82.3049 | 0.032284 | 0.067555 | 0.10886 | 0.15491 | 0.20205 | 0.25388 | 0.31152 | 0.43426 | 0.53799 | 0.63507 | -0.36735 | -0.44676 | -0.53271 | -0.61538 | -0.68711 | -0.75081 | -0.80964 | -0.87193 | -0.9347 | -0.98901
Wesley Vale | 81003 | 100.203 | 130.7197 | 130.7197 | 132.7106 | 137.4291 | 140.7338 | 141.4519 | 142.2026 | 143.3315 | 147.8918 | 157.3832 | 166.8833 | 180.4304 | 179.2214 | 179.2214 | 184.8039 | 188.4122 | 191.8377 | 193.0715 | 194.5795 | 196.7332 | 200.6659 | 210.5459 | 219.5041 | 0.097217 | 0.20343 | 0.32781 | 0.46647 | 0.6084 | 0.76447 | 0.93802 | 1.3076 | 1.6199 | 1.9123 | -1.1065 | -1.3456 | -1.6044 | -1.8533 | -2.0692 | -2.261 | -2.438 | -2.6255 | -2.8143 | -2.9777
West Hobart Zone | 13043 | 38.2004 | 49.3988 | 49.3988 | 50.1511 | 51.9343 | 53.1831 | 53.4545 | 53.7382 | 54.1648 | 55.8881 | 59.4749 | 63.065 | 92.0173 | 82.7647 | 82.7647 | 85.3427 | 87.009 | 88.5909 | 89.1607 | 89.8571 | 90.8517 | 92.6678 | 97.2304 | 101.3673 | 0.012229 | 0.024807 | 0.039716 | 0.056722 | 0.07446 | 0.094601 | 0.11739 | 0.1675 | 0.20894 | 0.24734 | -0.10947 | -0.1376 | -0.16824 | -0.19802 | -0.22414 | -0.24763 | -0.26967 | -0.29385 | -0.3177 | -0.33764
West Hobart Zone | 13044 | 118.7779 | 120.7305 | 120.7305 | 122.5692 | 126.9271 | 129.9794 | 130.6426 | 131.3359 | 132.3785 | 136.5904 | 145.3564 | 154.1306 | 189.2983 | 173.9883 | 173.9883 | 179.4079 | 182.9107 | 186.2363 | 187.434 | 188.898 | 190.9888 | 194.8066 | 204.3982 | 213.0948 | 0.0092304 | 0.018118 | 0.028814 | 0.041331 | 0.054686 | 0.070192 | 0.087943 | 0.12773 | 0.16037 | 0.19071 | -0.095016 | -0.11474 | -0.13631 | -0.15731 | -0.17573 | -0.19221 | -0.20758 | -0.22338 | -0.2392 | -0.25231
West Hobart Zone | 13045 | 160.9404 | 159.747 | 159.747 | 162.18 | 167.9462 | 171.9849 | 172.8624 | 173.7797 | 175.1594 | 180.7324 | 192.3313 | 203.9411 | 249.2388 | 248.3748 | 248.3748 | 256.1115 | 261.112 | 265.8593 | 267.5691 | 269.659 | 272.6438 | 278.0938 | 291.7861 | 304.2009 | 0.040597 | 0.082379 | 0.13204 | 0.18897 | 0.24862 | 0.31669 | 0.39391 | 0.56443 | 0.70515 | 0.83558 | -0.37959 | -0.47282 | -0.57433 | -0.67296 | -0.75938 | -0.83697 | -0.90958 | -0.98793 | -1.0656 | -1.1303
West Hobart Zone | 13046 | 55.5412 | 65.2693 | 65.2693 | 66.2634 | 68.6194 | 70.2695 | 70.628 | 71.0028 | 71.5665 | 73.8435 | 78.5826 | 83.3261 | 72.238 | 79.961 | 79.961 | 82.4517 | 84.0616 | 85.5899 | 86.1404 | 86.8132 | 87.7741 | 89.5286 | 93.9367 | 97.9335 | 0.00020925 | 0.00041074 | 0.00065322 | 0.00093698 | 0.0012397 | 0.0015913 | 0.0019937 | 0.0028956 | 0.0036355 | 0.0043233 | -0.002154 | -0.0026012 | -0.0030902 | -0.0035663 | -0.0039838 | -0.0043574 | -0.0047059 | -0.005064 | -0.0054226 | -0.0057199
West Hobart Zone | 13047 | 48.1803 | 48.9401 | 48.9401 | 49.6854 | 51.452 | 52.6892 | 52.9581 | 53.2391 | 53.6618 | 55.3691 | 58.9226 | 62.4793 | 94.3948 | 68.742 | 68.742 | 70.8832 | 72.2672 | 73.5811 | 74.0543 | 74.6327 | 75.4588 | 76.9672 | 80.7568 | 84.1928 | 0.0041646 | 0.0084724 | 0.013588 | 0.019443 | 0.02557 | 0.032552 | 0.040466 | 0.057922 | 0.072335 | 0.085691 | -0.038631 | -0.048247 | -0.058714 | -0.068882 | -0.077791 | -0.085791 | -0.09328 | -0.10139 | -0.10942 | -0.11611
West Hobart Zone | 13048 | 87.6615 | 93.2848 | 93.2848 | 94.7055 | 98.0728 | 100.4311 | 100.9436 | 101.4792 | 102.2849 | 105.5393 | 112.3125 | 119.0921 | 144.5496 | 127.3786 | 127.3786 | 131.3464 | 133.9108 | 136.3455 | 137.2224 | 138.2942 | 139.8249 | 142.62 | 149.642 | 156.0089 | 0.0091374 | 0.017936 | 0.028524 | 0.040915 | 0.054135 | 0.069485 | 0.087057 | 0.12644 | 0.15875 | 0.18878 | -0.094059 | -0.11359 | -0.13494 | -0.15573 | -0.17396 | -0.19027 | -0.20549 | -0.22113 | -0.23679 | -0.24977
West Hobart Zone | 13049 | 78.8052 | 110.0551 | 110.0551 | 111.7313 | 115.7038 | 118.4862 | 119.0908 | 119.7227 | 120.6732 | 124.5126 | 132.5035 | 140.5019 | 176.7507 | 155.4978 | 155.4978 | 160.3414 | 163.472 | 166.4441 | 167.5146 | 168.823 | 170.6916 | 174.1037 | 182.6759 | 190.4483 | 0.023367 | 0.045866 | 0.072943 | 0.10463 | 0.13844 | 0.17769 | 0.22263 | 0.32335 | 0.40597 | 0.48277 | -0.24053 | -0.29047 | -0.34507 | -0.39824 | -0.44485 | -0.48658 | -0.52549 | -0.56548 | -0.60552 | -0.63872
West Hobart Zone | 13050 | 43.4961 | 56.8438 | 56.8438 | 57.7096 | 59.7614 | 61.1985 | 61.5108 | 61.8372 | 62.3281 | 64.3112 | 68.4385 | 72.5697 | 83.9348 | 74.9412 | 74.9412 | 77.2756 | 78.7843 | 80.2167 | 80.7326 | 81.3632 | 82.2638 | 83.9082 | 88.0395 | 91.7854 | 0.010047 | 0.018988 | 0.029675 | 0.041988 | 0.054938 | 0.069735 | 0.086552 | 0.12365 | 0.15438 | 0.18294 | -0.084725 | -0.10488 | -0.12698 | -0.14865 | -0.16782 | -0.1852 | -0.20164 | -0.21964 | -0.23767 | -0.25293
West Hobart Zone | 13052 | 141.5298 | 158.8494 | 158.8494 | 161.2686 | 167.0025 | 171.0185 | 171.8911 | 172.8032 | 174.1751 | 179.7168 | 191.2506 | 202.7951 | 250.2033 | 218.3378 | 218.3378 | 225.1388 | 229.5346 | 233.7078 | 235.2108 | 237.048 | 239.6718 | 244.4627 | 256.4992 | 267.4126 | 0.021263 | 0.043392 | 0.069574 | 0.099349 | 0.13032 | 0.1654 | 0.20503 | 0.29195 | 0.36391 | 0.43054 | -0.18755 | -0.23708 | -0.29097 | -0.34334 | -0.38926 | -0.43058 | -0.46935 | -0.51218 | -0.5543 | -0.58956
West Hobart Zone | 13053 | 79.6684 | 103.5301 | 103.5301 | 105.1069 | 108.8439 | 111.4613 | 112.03 | 112.6245 | 113.5187 | 117.1304 | 124.6476 | 132.1717 | 152.2141 | 142.5538 | 142.5538 | 146.9943 | 149.8643 | 152.589 | 153.5703 | 154.7698 | 156.4829 | 159.6109 | 167.4696 | 174.595 | 0.022628 | 0.046619 | 0.074981 | 0.1072 | 0.1407 | 0.1786 | 0.22142 | 0.31529 | 0.39299 | 0.46491 | -0.20157 | -0.25523 | -0.31354 | -0.37015 | -0.41974 | -0.46431 | -0.50609 | -0.55221 | -0.59751 | -0.63535
West Hobart Zone | 13054 | 84.6502 | 65.0551 | 65.0551 | 66.0459 | 68.3942 | 70.0389 | 70.3962 | 70.7698 | 71.3316 | 73.6012 | 78.3247 | 83.0527 | 113.1705 | 76.9453 | 76.9453 | 79.342 | 80.8912 | 82.3618 | 82.8915 | 83.539 | 84.4636 | 86.152 | 90.3938 | 94.2399 | 0.0052897 | 0.010594 | 0.016929 | 0.024249 | 0.031974 | 0.040851 | 0.050956 | 0.073407 | 0.091889 | 0.10904 | -0.051448 | -0.063259 | -0.076141 | -0.088668 | -0.099647 | -0.10949 | -0.11869 | -0.12843 | -0.13814 | -0.1462
West Hobart Zone | 13055 | 110.075 | 179.0567 | 179.0567 | 181.7837 | 188.247 | 192.7738 | 193.7574 | 194.7856 | 196.332 | 202.5787 | 215.5797 | 228.5928 | 207.6147 | 195.0221 | 195.0221 | 201.0969 | 205.0232 | 208.7508 | 210.0933 | 211.7343 | 214.0779 | 218.3572 | 229.1083 | 238.8563 | 0.028011 | 0.057751 | 0.0929 | 0.13281 | 0.17428 | 0.22119 | 0.27417 | 0.39028 | 0.48639 | 0.57535 | -0.2488 | -0.31532 | -0.38761 | -0.45779 | -0.51926 | -0.57452 | -0.62632 | -0.68358 | -0.73978 | -0.78675
West Hobart Zone | 13056 | 43.9845 | 57.0556 | 57.0556 | 57.9246 | 59.9841 | 61.4265 | 61.74 | 62.0676 | 62.5603 | 64.5508 | 68.6935 | 72.8401 | 95.7451 | 89.3555 | 89.3555 | 92.1388 | 93.9378 | 95.6457 | 96.2608 | 97.0127 | 98.0865 | 100.0472 | 104.9731 | 109.4395 | 0.020135 | 0.038564 | 0.06055 | 0.085823 | 0.11235 | 0.14262 | 0.17699 | 0.25273 | 0.31546 | 0.37371 | -0.17132 | -0.2128 | -0.25822 | -0.30268 | -0.34195 | -0.37749 | -0.41106 | -0.44787 | -0.4846 | -0.51564
West Hobart Zone | 13057 | 97.9579 | 166.8314 | 166.8314 | 169.3722 | 175.3942 | 179.6119 | 180.5284 | 181.4864 | 182.9272 | 188.7473 | 200.8606 | 212.9853 | 176.8721 | 211.6047 | 211.6047 | 218.196 | 222.4562 | 226.5007 | 227.9574 | 229.7379 | 232.2808 | 236.924 | 248.5892 | 259.1661 | 0.04845 | 0.097909 | 0.15544 | 0.21899 | 0.28344 | 0.35374 | 0.43159 | 0.59931 | 0.73985 | 0.87064 | -0.47562 | -0.58667 | -0.70666 | -0.82263 | -0.92388 | -1.0149 | -1.1003 | -1.197 | -1.2928 | -1.3757
West Hobart Zone | 13058 | 65.2442 | 70.1314 | 70.1314 | 71.1994 | 73.7309 | 75.504 | 75.8892 | 76.2919 | 76.8976 | 79.3442 | 84.4363 | 89.5332 | 91.6599 | 57.4748 | 57.4748 | 59.2651 | 60.4222 | 61.5208 | 61.9164 | 62.4 | 63.0907 | 64.3519 | 67.5203 | 70.3931 | 0.00062776 | 0.0012322 | 0.0019597 | 0.0028109 | 0.0037192 | 0.0047738 | 0.005981 | 0.0086869 | 0.010907 | 0.01297 | -0.0064621 | -0.0078036 | -0.0092706 | -0.010699 | -0.011951 | -0.013072 | -0.014118 | -0.015192 | -0.016268 | -0.01716

## T-D info
KEY
Hardcoded data
| In sheet calculation | [9 empty] | Used data>>>
| Lookup data | [10 empty] | Hrs above 95% load |  | Load Transfers |  | Embedded Generation |  |  |  | Peak and non-peak
|  | General info | [6 empty] | General info cont. |  |  |  |  | Sub | Load transfer point
|  | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Non-Peaking season | Substation | Comment |  | Substation | Hours above 95% load | ALLoad transfer capacity (MVA)1 | Wayatinah | Substation | <100kVA | >100kVA |  | Substation | Winter | Summer | Peak | Non-peak
| AL | Arthurs Lake[1] | Central | Distribution lines | 110/6.6 kV | 1 | Winter | Summer | Arthurs Lake[1] | [1] Arthurs Lake Substation supplies both distribution and generation-pump load customers. The distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. |  | AL | 4.5 | ALLoad transfer capacity (MVA)2 |  | AL | 0.36324 | 1.6 | AL | Arthurs Lake[1] | 0.14792 | 0.4652 | Summer | Winter
| AV | Avoca | Eastern | Distribution lines | 110/22 kV | 1 | Summer | Winter | Burnie | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 4.9 of this APR. |  | AV | 4 | ALLoad transfer capacity (MVA)3 |  | AV | 1.2114 | 5 | AV | Avoca | 6.6818 | 9.5648 | Summer | Winter
| BW | Bridgewater | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Summer | Knights Road | [1] We propose to replace the supply transformers due to asset condition in 2030 with new units of standard size, as detailed in Section 4.9 of this APR. |  | BU | 11.5 | ALLoad transfer capacity (MVA)4 |  | BU | 13.9754 | 4.1353 | BW | Bridgewater | 34.8274 | 21.775 | Winter | Summer
| BU | Burnie | North West | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | BW | 7.5 | ALLoad transfer capacity (MVA)5 |  | BW | 10.2075 | 0.32 | BU | Burnie | 60.3722 | 39.7586 | Winter | Summer
| CS | Chapel Street | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Summer | Port Latta[1] | [1] Port Latta Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2027, with new standard units, as detailed in Section 4.9 of this APR. |  | CR | 1 | AVLoad transfer capacity (MVA)1 | Palmerston | CR | 15.6436 | 1.065 | CS | Chapel Street | 40.1666 | 22.161 | Winter | Summer
| CR | Creek Road | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter | Summer | Railton | [1] From summer 2022, load is forecast to exceed the firm rating of the substation, however will be addressed by the connection point at Sheffield Substation. Note: AEMO did not prepare a forecast for the proposed connection point. |  | CS | 2 | AVLoad transfer capacity (MVA)2 | St Marys | CS | 7.4504 | 1.69 | CR | Creek Road | 92.304 | 58.7122 | Winter | Summer
| DE | Derby | Northern | Distribution lines | 110/22 kV | 1 | Summer | Winter | Rosebery (44 kV)[1] | [1] Rosebery Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. |  | DB | 0.5 | AVLoad transfer capacity (MVA)3 |  | DB | 0 | 0 | DE | Derby | 6.0374 | 8.9534 | Summer | Winter
| DB | Derwent Bridge | Central | Distribution lines | 110/22 kV | 1 | Winter | Summer | Savage River[1] | [1] Savage River Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2029, with new standard units, as detailed in Section 4.9 of this APR. |  | DE | 1.5 | AVLoad transfer capacity (MVA)4 |  | DE | 1.3562 | 2.02 | DB | Derwent Bridge | 0.3368 | 0.293 | Winter | Summer
| DP | Devonport | North West | Distribution lines | 110/22 kV | 3 | Winter | Summer | St Marys | [1] Load exceeds substation firm rating, as detailed in Section 4.6.2 of this APR. However, we propose to replace the supply transformers due to condition in 2027, with new standard units providing sufficient capacity for the substation forecast load, detailed in Section 4.9 of this APR. |  | DP | 4.5 | AVLoad transfer capacity (MVA)5 |  | DP | 11.2123 | 0.95333 | DP | Devonport | 54.7438 | 32.6326 | Winter | Summer
| EL | Electrona | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Summer | Tungatinah | [1] Supply transformer is rated to 25 MVA, but substation is limited to 13 MVA by bay conductor. |  | EB | 7.5 | BULoad transfer capacity (MVA)1 | Port Latta | EB | 0.70338 | 0 | EL | Electrona | 16.437 | 11.3214 | Winter | Summer
| EB | Emu Bay | North West | Distribution lines | 110/11 kV | 2 | Winter | Summer | Waddamana | [1] Waddamana transformer rated to 5 MVA, but substation is limited to 3.8 MVA by 22 kV combined voltage-current transformer. [2] We propose to replace the supply transformer due to asset condition in 2029 with new units of standard size, as detailed in Section 4.9 of this APR. |  | EL | 2 | BULoad transfer capacity (MVA)2 | Ulverstone | EL | 8.7161 | 0.1298 | EB | Emu Bay | 9.0024 | 6.947 | Winter | Summer
| GT | George Town | Northern | Distribution lines | 110/22 kV | 2 | Winter | Summer | Rosebery (44 kV)[1] | [1] We propose to replace the supply transformers due to asset condition in 2029 with new units of standard size, as detailed in Section 4.9 of this APR. |  | GT | 6 | BULoad transfer capacity (MVA)3 |  | GO | 0 | 0 | GT | George Town | 19.3628 | 12.9618 | Winter | Summer
| HA | Hadspen | Northern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | HA | 9 | BULoad transfer capacity (MVA)4 |  | GT | 7.5015 | 0.30292 | HA | Hadspen | 57.6294 | 34.2602 | Winter | Summer
| HR | Huon River | Kingston-South | Distribution lines | 110/11 kV | 1 | Winter | Summer |  |  |  | HR | 0.5 | BULoad transfer capacity (MVA)5 |  | HA | 15.1834 | 1.0487 | HR | Huon River | 0.5824 | 0.574 | Winter | Summer
| KE | Kermandie | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Summer |  |  |  | KE | 2 | BWLoad transfer capacity (MVA)1 | Claremont | HR | 0.01525 | 0 | KE | Kermandie | 8.714 | 6.4904 | Winter | Summer
| KI11 | Kingston (11 kV) | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Summer |  |  |  | KI11 | 2 | BWLoad transfer capacity (MVA)2 | Derwent Park | KE | 3.2869 | 0 | KI11 | Kingston (11 kV) | 27.5044 | 17.5614 | Winter | Summer
| KI33 | Kingston (33 kV) | Kingston-South | Sub-transmission lines | 110/33 kV | 2 | Winter | Summer |  |  |  | KI33 | 2 | BWLoad transfer capacity (MVA)3 | New Norfolk | KI11 | 9.0801 | 0.30004 | KI33 | Kingston (33 kV) | 10.9406 | 6.721 | Winter | Summer
| KR | Knights Road | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Summer |  |  |  | KR | 10 | BWLoad transfer capacity (MVA)4 |  | KI33 | 2.8651 | 0 | KR | Knights Road | 19.9056 | 15.079 | Winter | Summer
| LF | Lindisfarne | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter | Summer |  |  |  | LF | 2 | BWLoad transfer capacity (MVA)5 |  | KR | 6.9122 | 0.1992 | LF | Lindisfarne | 36.0208 | 23.439 | Winter | Summer
| MB | Meadowbank | Central | Distribution lines | 110/22 kV | 1 | Summer | Winter |  |  |  | MB | 10.5 | CRLoad transfer capacity (MVA)1 | Claremont | LF | 5.6014 | 0 | MB | Meadowbank | 5.4732 | 7.7741 | Summer | Winter
| MT | Mornington | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter | Summer |  |  |  | MT | 2 | CRLoad transfer capacity (MVA)2 | Derwent Park | MB | 0.91829 | 0.2 | MT | Mornington | 41.022 | 26.5588 | Winter | Summer
| MY | Mowbray | Northern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | MY | 13 | CRLoad transfer capacity (MVA)3 | New Town | MT | 11.4925 | 0 | MY | Mowbray | 37.2896 | 19.8134 | Winter | Summer
| NN | New Norfolk | Central | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | NH | 17.5 | CRLoad transfer capacity (MVA)4 | North Hobart | MY | 6.4748 | 2.2 | NN | New Norfolk | 14.1572 | 16.0744 | Summer | Winter
| NT | Newton | West Cost | Distribution lines | 110/22 kV | 1 | Summer | Winter |  |  |  | NN | 6 | CRLoad transfer capacity (MVA)5 |  | NH | 5.5279 | 0 | NT | Newton | 4.1194 | 3.9998 | Winter | Summer
| NH | North Hobart | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Summer |  |  |  | NT | 15 | CSLoad transfer capacity (MVA)1 | Claremont | NN | 4.4486 | 0.56 | NH | North Hobart | 34.7508 | 22.868 | Winter | Summer
| NW | Norwood | Northern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | NW | 4 | CSLoad transfer capacity (MVA)2 | Derwent Park | NT | 0 | 0 | NW | Norwood | 29.3684 | 16.4816 | Winter | Summer
| PM | Palmerston | Northern | Distribution lines | 110/22 kV | 2 | Summer | Winter |  |  |  | PL | 5.5 | CSLoad transfer capacity (MVA)3 | New Town | NW | 7.5109 | 0.58708 | PM | Palmerston | 9.5356 | 11.885 | Summer | Winter
| PL | Port Latta[1] | North West | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Summer | Winter |  |  |  | PM | 14 | CSLoad transfer capacity (MVA)4 | North Hobart | PL | 2.3477 | 0.45 | PL | Port Latta[1] | 6.9284 | 10.8116 | Summer | Winter
| QT | Queenstown | West Coast | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | QT | 7 | CSLoad transfer capacity (MVA)5 |  | PM | 1.026 | 0 | QT | Queenstown | 6.2474 | 4.7624 | Winter | Summer
| RA | Railton | North West | Distribution lines | 110/22 kV | 2 | Summer | Winter |  |  |  | RA | 13.5 | DBLoad transfer capacity (MVA)1 |  | QT | 0.88118 | 0 | RA | Railton | 47.363 | 43.2732 | Winter | Summer
| RI | Risdon | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter | Summer |  |  |  | RB22 | 1.5 | DBLoad transfer capacity (MVA)2 |  | RA | 11.638 | 3.2592 | RI | Risdon | 67.0022 | 47.4472 | Winter | Summer
| RK | Rokeby | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Summer |  |  |  | RB44 | 154 | DBLoad transfer capacity (MVA)3 |  | RB22 | 0 | 0 | RK | Rokeby | 24.5824 | 15.7372 | Winter | Summer
| RB22 | Rosebery (22 kV) | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Summer |  |  |  | RI | 23.5 | DBLoad transfer capacity (MVA)4 |  | RB44 | 0.57149 | 0 | RB22 | Rosebery (22 kV) | 2.3877 | 1.9462 | Winter | Summer
| RB44 | Rosebery (44 kV)[1] | West Coast | Distribution lines and transmission-connected customer | 110/44 kV | 2 | Winter | Summer |  |  |  | RK | 1.5 | DBLoad transfer capacity (MVA)5 |  | RI | 5.8486 | 0.59998 | RB44 | Rosebery (44 kV)[1] | 30.9933 | 21.0224 | Winter | Summer
| SR | Savage River[1] | West Coast | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Winter | Summer |  |  |  | SD | 20 | DELoad transfer capacity (MVA)1 | Scottsdale | RK | 7.1907 | 0 | SR | Savage River[1] | 1.0938 | 0.8846 | Winter | Summer
| SD | Scottsdale | Northern | Distribution lines | 110/22 kV | 2 | Summer | Winter |  |  |  | SH | 1.8 | DELoad transfer capacity (MVA)2 | St Marys | SD | 4.8918 | 1.89 | SD | Scottsdale | 12.1064 | 11.0298 | Winter | Summer
| SH | Sheffield | North West | Distribution lines | 110/22 kV | 1 | Winter | Summer |  |  |  | SL | 5.5 | DELoad transfer capacity (MVA)3 |  | SH | 1.1198 | 0 | SH | Sheffield |  |  | Winter | Summer
| ST | Smithton | North West | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | SM | 6 | DELoad transfer capacity (MVA)4 |  | SL | 5.9534 | 0 | ST | Smithton | 21.9034 | 22.0882 | Summer | Winter
| SO | Sorell | Eastern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | SO | 1.5 | DELoad transfer capacity (MVA)5 |  | SM | 6.2124 | 0 | SO | Sorell | 36.398 | 24.4326 | Winter | Summer
| SL | St Leonards | Northern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | SR | 3 | DPLoad transfer capacity (MVA)1 | Railton | SO | 12.6619 | 1.067 | SL | St Leonards | 31.1972 | 15.0016 | Winter | Summer
| SM | St Marys | Eastern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | ST | 5.5 | DPLoad transfer capacity (MVA)2 | Ulverstone | SR | 0.19812 | 0 | SM | St Marys | 16.3176 | 11.2984 | Winter | Summer
| TR | Trevallyn | Northern | Distribution lines | 110/22 kV | 3 | Winter | Summer |  |  |  | TB | 1.5 | DPLoad transfer capacity (MVA)3 |  | ST | 3.3141 | 1.1333 | TR | Trevallyn | 72.4356 | 38.9748 | Winter | Summer
| TB | Triabunna | Eastern | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | TR | 13.5 | DPLoad transfer capacity (MVA)4 |  | TB | 2.9445 | 0 | TB | Triabunna | 9.517 | 5.7406 | Winter | Summer
| TU | Tungatinah | Central | Distribution lines | 110/22 kV | 1 | Winter | Summer |  |  |  | TU | 11.5 | DPLoad transfer capacity (MVA)5 |  | TR | 20.6073 | 2 | TU | Tungatinah | 1.1416 | 0.8434 | Winter | Summer
| UL | Ulverstone | North West | Distribution lines | 110/22 kV | 2 | Winter | Summer |  |  |  | UL | 2.5 | EBLoad transfer capacity (MVA)1 |  | TU | 0.0657 | 0 | UL | Ulverstone | 29.898 | 20.5622 | Winter | Summer
| WA | Waddamana | Central | Distribution lines | 110/22 kV | 1 | Winter | Summer |  |  |  | WA | 1.5 | EBLoad transfer capacity (MVA)2 |  | UL | 10.809 | 8.805 | WA | Waddamana | 0.6644 | 0.446 | Winter | Summer
| WV | Wesley Vale | North West | Distribution lines | 110/22 kV [1] | 2 | Winter | Summer |  |  |  | WV | 9 | EBLoad transfer capacity (MVA)3 |  | WA | 0 | 0 | WV | Wesley Vale | 11.5794 | 7.8386 | Winter | Summer
[14 empty] | EBLoad transfer capacity (MVA)4 |  | WV | 4.0988 | 0.265
[14 empty] | EBLoad transfer capacity (MVA)5 |  | WY | 0.00304 | 0.9
[14 empty] | ELLoad transfer capacity (MVA)1 | Kingston
| Arthurs Lake[1] | AL | [11 empty] | ELLoad transfer capacity (MVA)2 | Knights Road
| Avoca | AV | [11 empty] | ELLoad transfer capacity (MVA)3
| Bridgewater | BW | [11 empty] | ELLoad transfer capacity (MVA)4
| Burnie | BU | [11 empty] | ELLoad transfer capacity (MVA)5
| Chapel Street | CS | [11 empty] | GTLoad transfer capacity (MVA)1 | Mowbray
| Creek Road | CR | [11 empty] | GTLoad transfer capacity (MVA)2 | Scottsdale
| Derby | DE | [11 empty] | GTLoad transfer capacity (MVA)3 | Trevallyn
| Derwent Bridge | DB | [11 empty] | GTLoad transfer capacity (MVA)4
| Devonport | DP | [11 empty] | GTLoad transfer capacity (MVA)5
| Electrona | EL | [11 empty] | HALoad transfer capacity (MVA)1 | Norwood
| Emu Bay | EB | [11 empty] | HALoad transfer capacity (MVA)2 | Palmerston
| George Town | GT | [11 empty] | HALoad transfer capacity (MVA)3 | Railton
| Hadspen | HA | [11 empty] | HALoad transfer capacity (MVA)4 | Trevallyn
| Huon River | HR | [11 empty] | HALoad transfer capacity (MVA)5
| Kermandie | KE | [11 empty] | HRLoad transfer capacity (MVA)1
| Kingston (11 kV) | KI11 | [11 empty] | HRLoad transfer capacity (MVA)2
| Kingston (33 kV) | KI33 | [11 empty] | HRLoad transfer capacity (MVA)3
| Knights Road | KR | [11 empty] | HRLoad transfer capacity (MVA)4
| Lindisfarne | LF | [11 empty] | HRLoad transfer capacity (MVA)5
| Meadowbank | MB | [11 empty] | KELoad transfer capacity (MVA)1 | Knights Road
| Mornington | MT | [11 empty] | KELoad transfer capacity (MVA)2
| Mowbray | MY | [11 empty] | KELoad transfer capacity (MVA)3
| New Norfolk | NN | [11 empty] | KELoad transfer capacity (MVA)4
| Newton | NT | [11 empty] | KELoad transfer capacity (MVA)5
| North Hobart | NH | [11 empty] | KI11Load transfer capacity (MVA)1 | Electrona
| Norwood | NW | [11 empty] | KI11Load transfer capacity (MVA)2 | Knights Road
| Palmerston | PM | [11 empty] | KI11Load transfer capacity (MVA)3 | Sandy Bay
| Port Latta[1] | PL | [11 empty] | KI11Load transfer capacity (MVA)4
| Queenstown | QT | [11 empty] | KI11Load transfer capacity (MVA)5
| Railton | RA | [11 empty] | KI33Load transfer capacity (MVA)1
| Risdon | RI | [11 empty] | KI33Load transfer capacity (MVA)2
| Rokeby | RK | [11 empty] | KI33Load transfer capacity (MVA)3
| Rosebery (22 kV) | RB22 | [11 empty] | KI33Load transfer capacity (MVA)4
| Rosebery (44 kV)[1] | RB44 | [11 empty] | KI33Load transfer capacity (MVA)5
| Savage River[1] | SR | [11 empty] | KRLoad transfer capacity (MVA)1 | Electrona
| Scottsdale | SD | [11 empty] | KRLoad transfer capacity (MVA)2 | Kermandie
| Sheffield | SH
| Smithton | ST | [11 empty] | KRLoad transfer capacity (MVA)3 | Kingston
| Sorell | SO | [11 empty] | KRLoad transfer capacity (MVA)4
| St Leonards | SL | [11 empty] | KRLoad transfer capacity (MVA)5
| St Marys | SM | [11 empty] | LFLoad transfer capacity (MVA)1
| Trevallyn | TR | [11 empty] | LFLoad transfer capacity (MVA)2
| Triabunna | TB | [11 empty] | LFLoad transfer capacity (MVA)3
| Tungatinah | TU | [11 empty] | LFLoad transfer capacity (MVA)4
| Ulverstone | UL | [11 empty] | LFLoad transfer capacity (MVA)5
| Waddamana | WA | [11 empty] | MBLoad transfer capacity (MVA)1 | New Norfolk
| Wesley Vale | WV | [11 empty] | MBLoad transfer capacity (MVA)2 | Wayatinah
[14 empty] | MBLoad transfer capacity (MVA)3 | Sorell
MBLoad transfer capacity (MVA)4
MBLoad transfer capacity (MVA)5
MTLoad transfer capacity (MVA)1
MTLoad transfer capacity (MVA)2
MTLoad transfer capacity (MVA)3
MTLoad transfer capacity (MVA)4
MTLoad transfer capacity (MVA)5
[14 empty] | MYLoad transfer capacity (MVA)1 | Norwood
[14 empty] | MYLoad transfer capacity (MVA)2 | Trevallyn
MYLoad transfer capacity (MVA)3
MYLoad transfer capacity (MVA)4
MYLoad transfer capacity (MVA)5
[14 empty] | NHLoad transfer capacity (MVA)1 | Chapel Street
[14 empty] | NHLoad transfer capacity (MVA)2 | East Hobart
[14 empty] | NHLoad transfer capacity (MVA)3 | New Town
[14 empty] | NHLoad transfer capacity (MVA)4 | West Hobart
NHLoad transfer capacity (MVA)5
[14 empty] | NNLoad transfer capacity (MVA)1 | Meadowbank
NNLoad transfer capacity (MVA)2
NNLoad transfer capacity (MVA)3
NNLoad transfer capacity (MVA)4
NNLoad transfer capacity (MVA)5
NTLoad transfer capacity (MVA)1
NTLoad transfer capacity (MVA)2
NTLoad transfer capacity (MVA)3
NTLoad transfer capacity (MVA)4
NTLoad transfer capacity (MVA)5
[14 empty] | NWLoad transfer capacity (MVA)1 | Hadspen
[14 empty] | NWLoad transfer capacity (MVA)2 | Mowbray
[14 empty] | NWLoad transfer capacity (MVA)3 | St Leonards
[14 empty] | NWLoad transfer capacity (MVA)4 | Trevallyn
NWLoad transfer capacity (MVA)5
[14 empty] | PLLoad transfer capacity (MVA)1 | Burnie
[14 empty] | PLLoad transfer capacity (MVA)2 | Smithton
PLLoad transfer capacity (MVA)3
PLLoad transfer capacity (MVA)4
PLLoad transfer capacity (MVA)5
[14 empty] | PMLoad transfer capacity (MVA)1 | Avoca
[14 empty] | PMLoad transfer capacity (MVA)2 | Hadspen
[14 empty] | PMLoad transfer capacity (MVA)3 | Norwood
[14 empty] | PMLoad transfer capacity (MVA)4 | Railton
PMLoad transfer capacity (MVA)5
QTLoad transfer capacity (MVA)1
QTLoad transfer capacity (MVA)2
QTLoad transfer capacity (MVA)3
QTLoad transfer capacity (MVA)4
QTLoad transfer capacity (MVA)5
[14 empty] | RALoad transfer capacity (MVA)1 | Devonport
[14 empty] | RALoad transfer capacity (MVA)2 | Ulverstone
RALoad transfer capacity (MVA)3
RALoad transfer capacity (MVA)4
RALoad transfer capacity (MVA)5
RB22Load transfer capacity (MVA)1
RB22Load transfer capacity (MVA)2
RB22Load transfer capacity (MVA)3
RB22Load transfer capacity (MVA)4
RB22Load transfer capacity (MVA)5
RB44Load transfer capacity (MVA)1
RB44Load transfer capacity (MVA)2
RB44Load transfer capacity (MVA)3
RB44Load transfer capacity (MVA)4
RB44Load transfer capacity (MVA)5
RILoad transfer capacity (MVA)1
RILoad transfer capacity (MVA)2
RILoad transfer capacity (MVA)3
RILoad transfer capacity (MVA)4
RILoad transfer capacity (MVA)5
[14 empty] | RKLoad transfer capacity (MVA)1 | Cambridge
[14 empty] | RKLoad transfer capacity (MVA)2 | Howrah
RKLoad transfer capacity (MVA)3
RKLoad transfer capacity (MVA)4
RKLoad transfer capacity (MVA)5
[14 empty] | SDLoad transfer capacity (MVA)1 | Derby
[14 empty] | SDLoad transfer capacity (MVA)2 | George Town
[14 empty] | SDLoad transfer capacity (MVA)3 | Trevallyn
SDLoad transfer capacity (MVA)4
SDLoad transfer capacity (MVA)5
[14 empty] | SHLoad transfer capacity (MVA)1 | Railton
SHLoad transfer capacity (MVA)2
SHLoad transfer capacity (MVA)3
SHLoad transfer capacity (MVA)4
SHLoad transfer capacity (MVA)5
[14 empty] | SLLoad transfer capacity (MVA)1 | Mowbray
[14 empty] | SLLoad transfer capacity (MVA)2 | Norwood
[14 empty] | SLLoad transfer capacity (MVA)3 | Trevallyn
SLLoad transfer capacity (MVA)4
SLLoad transfer capacity (MVA)5
[14 empty] | SMLoad transfer capacity (MVA)1 | Avoca
[14 empty] | SMLoad transfer capacity (MVA)2 | Derby
[14 empty] | SMLoad transfer capacity (MVA)3 | Triabunna
SMLoad transfer capacity (MVA)4
SMLoad transfer capacity (MVA)5
[14 empty] | SOLoad transfer capacity (MVA)1 | Avoca
[14 empty] | SOLoad transfer capacity (MVA)2 | Meadowbank
[14 empty] | SOLoad transfer capacity (MVA)3 | Triabunna
SOLoad transfer capacity (MVA)4
SOLoad transfer capacity (MVA)5
SRLoad transfer capacity (MVA)1
SRLoad transfer capacity (MVA)2
SRLoad transfer capacity (MVA)3
SRLoad transfer capacity (MVA)4
SRLoad transfer capacity (MVA)5
[14 empty] | STLoad transfer capacity (MVA)1 | Port Latta
STLoad transfer capacity (MVA)2
STLoad transfer capacity (MVA)3
STLoad transfer capacity (MVA)4
STLoad transfer capacity (MVA)5
[14 empty] | TBLoad transfer capacity (MVA)1 | St Marys
[14 empty] | TBLoad transfer capacity (MVA)2 | Sorell
TBLoad transfer capacity (MVA)3
TBLoad transfer capacity (MVA)4
TBLoad transfer capacity (MVA)5
[14 empty] | TRLoad transfer capacity (MVA)1 | George Town
[14 empty] | TRLoad transfer capacity (MVA)2 | Hadspen
[14 empty] | TRLoad transfer capacity (MVA)3 | Mowbray
[14 empty] | TRLoad transfer capacity (MVA)4 | Norwood
[14 empty] | TRLoad transfer capacity (MVA)5 | St Leonards
TULoad transfer capacity (MVA)1
TULoad transfer capacity (MVA)2
TULoad transfer capacity (MVA)3
TULoad transfer capacity (MVA)4
TULoad transfer capacity (MVA)5
[14 empty] | ULLoad transfer capacity (MVA)1 | Burnie
[14 empty] | ULLoad transfer capacity (MVA)2 | Devonport
[14 empty] | ULLoad transfer capacity (MVA)3 | Railton
ULLoad transfer capacity (MVA)4
ULLoad transfer capacity (MVA)5
[14 empty] | WALoad transfer capacity (MVA)1 | Arthurs Lake
WALoad transfer capacity (MVA)2
WALoad transfer capacity (MVA)3
WALoad transfer capacity (MVA)4
WALoad transfer capacity (MVA)5
WVLoad transfer capacity (MVA)1
WVLoad transfer capacity (MVA)2
WVLoad transfer capacity (MVA)3
WVLoad transfer capacity (MVA)4
WVLoad transfer capacity (MVA)5

## FORECAST
|  |  | Summer | [13 empty] | Winter
Code | Name | Non-peaking season | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF
AL | Arthurs Lake (DL) | Winter | 0.52501 | 0.54367 | 0.54367 | 0.55195 | 0.57158 | 0.58532 | 0.58831 | 0.59143 | 0.59612 | 0.61509 | 0.65457 | 0.69408 | 0.98881 | 0.80435 | 0.022543 | 0.2009 | 0.2009 | 0.20715 | 0.2112 | 0.21504 | 0.21642 | 0.21811 | 0.22053 | 0.22493 | 0.23601 | 0.24605 | 0.66721 | 0.5974
AV | Avoca | Winter | 13.2985 | 10.5902 | 10.5902 | 10.7515 | 11.1337 | 11.4015 | 11.4597 | 11.5205 | 11.6119 | 11.9814 | 12.7503 | 13.52 | 0.98493 | 0.43165 | 8.2335 | 6.4502 | 6.4502 | 6.6511 | 6.781 | 6.9043 | 6.9487 | 7.003 | 7.0805 | 7.222 | 7.5776 | 7.9 | 1 | 0.73008
BU | Burnie | Summer | 41.8144 | 43.7936 | 44.4027 | 44.4606 | 46.0414 | 47.1486 | 47.3891 | 47.6406 | 48.0188 | 49.5466 | 52.7264 | 55.9091 | 0.99845 | 0.93437 | 58.1268 | 59.8407 | 60.3765 | 61.7047 | 62.9095 | 64.0533 | 64.4652 | 64.9687 | 65.6878 | 67.0009 | 70.2998 | 73.2909 | 0.99835 | 0.92899
BW | Bridgewater | Summer | 19.096 | 24.486 | 24.3338 | 24.828 | 24.9425 | 25.5422 | 25.6726 | 25.8088 | 26.0137 | 26.8414 | 28.564 | 30.2882 | 0.99985 | 0.86038 | 34.895 | 35.4617 | 35.3278 | 36.5387 | 36.5763 | 37.2413 | 37.4808 | 37.7735 | 38.1916 | 38.9551 | 40.8731 | 42.6121 | 0.99976 | 0.93665
CR | Creek Road | Summer | 51.9611 | 64.5253 | 66.6569 | 65.5081 | 67.8372 | 69.4685 | 69.8229 | 70.1935 | 70.7507 | 73.0018 | 77.6869 | 82.3763 | 0.99501 | 0.8873 | 89.0875 | 92.548 | 94.423 | 95.4308 | 97.2941 | 99.063 | 99.7001 | 100.4788 | 101.591 | 103.6217 | 108.7237 | 113.3496 | 0.99089 | 0.9452
CS | Chapel Street | Summer | 20.2013 | 24.2412 | 24.2412 | 24.6104 | 25.4854 | 26.0983 | 26.2314 | 26.3706 | 26.58 | 27.4257 | 29.1858 | 30.9475 | 0.99997 | 0.92902 | 38.759 | 40.3611 | 40.3611 | 41.6183 | 42.4309 | 43.2024 | 43.4802 | 43.8198 | 44.3048 | 45.1905 | 47.4155 | 49.4329 | 0.99999 | 0.90185
DB | Derwent Bridge | Summer | 0.28717 | 0.33268 | 0.33268 | 0.33774 | 0.34975 | 0.35816 | 0.35999 | 0.3619 | 0.36477 | 0.37638 | 0.40053 | 0.42471 | 0.98969 | 0.76923 | 0.33494 | 0.33628 | 0.33628 | 0.34676 | 0.35353 | 0.35996 | 0.36227 | 0.3651 | 0.36914 | 0.37652 | 0.39506 | 0.41187 | 1 | 0.71875
DE | Derby | Winter | 7.8275 | 6.8909 | 6.8909 | 6.9959 | 7.2446 | 7.4188 | 7.4567 | 7.4963 | 7.5558 | 7.7962 | 8.2965 | 8.7973 | 0.99287 | 0.71111 | 7.0036 | 5.8108 | 5.8108 | 5.9918 | 6.1088 | 6.2198 | 6.2598 | 6.3087 | 6.3786 | 6.5061 | 6.8264 | 7.1169 | 0.96015 | 0.32805
DP | Devonport | Summer | 36.0101 | 36.5976 | 36.9782 | 41.0194 | 37.6757 | 38.5816 | 38.7785 | 38.9843 | 39.2938 | 40.544 | 43.146 | 45.7504 | 0.99065 | 0.86328 | 52.515 | 53.2265 | 53.5613 | 58.337 | 55.2521 | 56.2566 | 56.6184 | 57.0607 | 57.6922 | 58.8455 | 61.7428 | 64.3698 | 0.99697 | 0.95374
EB | Emu Bay (RT) | Summer | 7.8282 | 7.6238 | 7.6238 | 7.7399 | 8.0151 | 8.2078 | 8.2497 | 8.2935 | 8.3593 | 8.6253 | 9.1789 | 9.7329 | 0.96247 | 0.76111 | 9.0691 | 8.8576 | 8.8576 | 9.1335 | 9.3118 | 9.4811 | 9.5421 | 9.6166 | 9.7231 | 9.9174 | 10.4057 | 10.8484 | 0.97442 | 0.8838
EL | Electrona | Summer | 10.0694 | 12.3126 | 12.3126 | 12.5001 | 12.9446 | 13.2558 | 13.3235 | 13.3942 | 13.5005 | 13.9301 | 14.8241 | 15.7189 | 0.99951 | 0.78257 | 16.2935 | 16.2531 | 16.2531 | 16.7594 | 17.0866 | 17.3972 | 17.5091 | 17.6459 | 17.8412 | 18.1978 | 19.0938 | 19.9062 | 0.99914 | 0.88141
GT | George Town | Summer | 12.9473 | 15.7618 | 18.1979 | 14.6107 | 15.1302 | 15.494 | 15.5731 | 15.6557 | 15.78 | 16.282 | 17.327 | 18.3729 | 0.99855 | 0.91086 | 19.5416 | 19.8436 | 21.9865 | 19.2187 | 19.594 | 19.9502 | 20.0785 | 20.2354 | 20.4593 | 20.8683 | 21.8958 | 22.8274 | 0.99895 | 0.77669
HA | Hadspen | Summer | 40.4237 | 37.995 | 37.386 | 38.7283 | 39.3049 | 40.2501 | 40.4554 | 40.6701 | 40.993 | 42.2973 | 45.0118 | 47.7289 | 0.99865 | 0.93747 | 54.9768 | 55.2719 | 54.7361 | 57.1316 | 57.5431 | 58.5893 | 58.9661 | 59.4267 | 60.0845 | 61.2855 | 64.303 | 67.0389 | 0.99902 | 0.93765
HR | Huon River | Summer | 0.55446 | 0.62466 | 0.62466 | 0.63418 | 0.65672 | 0.67252 | 0.67595 | 0.67953 | 0.68493 | 0.70672 | 0.75208 | 0.79748 | 0.55938 | 0.83333 | 0.92276 | 0.57863 | 0.57863 | 0.59665 | 0.6083 | 0.61936 | 0.62334 | 0.62821 | 0.63517 | 0.64786 | 0.67976 | 0.70868 | 0.56163 | 0.81818
KE | Kermandie | Summer | 6.2488 | 7.0843 | 7.0843 | 7.1922 | 7.4479 | 7.627 | 7.6659 | 7.7066 | 7.7678 | 8.0149 | 8.5293 | 9.0441 | 0.98581 | 0.86854 | 8.6874 | 8.5363 | 8.5363 | 8.8022 | 8.974 | 9.1372 | 9.1959 | 9.2678 | 9.3703 | 9.5576 | 10.0282 | 10.4549 | 0.98708 | 0.91347
KI11 | Kingston 11kV | Summer | 16.2318 | 19.3602 | 19.3602 | 19.655 | 20.3539 | 20.8433 | 20.9497 | 21.0608 | 21.228 | 21.9035 | 23.3092 | 24.7162 | 0.9997 | 0.7452 | 27.5402 | 27.6208 | 27.6208 | 28.4811 | 29.0372 | 29.5651 | 29.7553 | 29.9877 | 30.3196 | 30.9257 | 32.4484 | 33.829 | 0.99979 | 0.9059
KI33 | Kingston 33kV | Summer | 5.6704 | 7.4365 | 7.4365 | 7.5498 | 7.8182 | 8.0062 | 8.047 | 8.0897 | 8.154 | 8.4134 | 8.9534 | 9.4938 | 0.99992 | 0.85913 | 11.1262 | 11.0615 | 11.0615 | 11.406 | 11.6287 | 11.8401 | 11.9163 | 12.0094 | 12.1423 | 12.385 | 12.9948 | 13.5477 | 0.99724 | 0.94338
KR | Knights Road | Summer | 15.0454 | 15.4095 | 16.3992 | 16.6489 | 17.2409 | 17.6555 | 17.7456 | 17.8397 | 17.9814 | 18.5535 | 19.7442 | 20.936 | 0.98727 | 0.90798 | 20.0543 | 18.7877 | 19.6583 | 20.2706 | 20.6664 | 21.0421 | 21.1775 | 21.3429 | 21.5791 | 22.0105 | 23.0942 | 24.0768 | 0.98922 | 0.96199
LF | Lindisfarne | Summer | 20.1035 | 25.692 | 25.692 | 26.0833 | 27.0106 | 27.6602 | 27.8013 | 27.9488 | 28.1707 | 29.067 | 30.9325 | 32.7997 | 1 | 0.81658 | 35.7593 | 36.1898 | 36.1898 | 37.3171 | 38.0457 | 38.7374 | 38.9866 | 39.2911 | 39.726 | 40.5201 | 42.5152 | 44.3241 | 0.99787 | 0.92622
MB | Meadowbank | Winter | 8.3046 | 8.4548 | 8.4548 | 8.5835 | 8.8887 | 9.1025 | 9.1489 | 9.1975 | 9.2705 | 9.5654 | 10.1793 | 10.7938 | 0.95908 | 0.71486 | 4.6221 | 5.236 | 5.236 | 5.399 | 5.5045 | 5.6045 | 5.6406 | 5.6846 | 5.7476 | 5.8625 | 6.1511 | 6.4128 | 1 | 0.69937
MT | Mornington | Summer | 22.6309 | 29.0785 | 29.0785 | 29.5214 | 30.571 | 31.3061 | 31.4659 | 31.6329 | 31.884 | 32.8984 | 35.0098 | 37.1231 | 0.99982 | 0.82309 | 38.7639 | 41.1453 | 41.1453 | 42.4269 | 43.2553 | 44.0417 | 44.3249 | 44.6711 | 45.1656 | 46.0684 | 48.3367 | 50.3933 | 0.99854 | 0.94757
MY | Mowbray | Summer | 22.4062 | 22.0811 | 22.6902 | 22.4174 | 23.2145 | 23.7727 | 23.894 | 24.0208 | 24.2115 | 24.9818 | 26.5851 | 28.1899 | 0.99846 | 0.73585 | 38.721 | 35.3881 | 35.9239 | 36.4904 | 37.2029 | 37.8793 | 38.1229 | 38.4207 | 38.8459 | 39.6225 | 41.5733 | 43.3422 | 0.9944 | 0.93917
NH | North Hobart | Summer | 19.9398 | 25.096 | 25.096 | 25.4782 | 26.3841 | 27.0186 | 27.1564 | 27.3006 | 27.5173 | 28.3928 | 30.215 | 32.0389 | 0.9987 | 0.82122 | 35.6257 | 34.7894 | 34.7894 | 35.873 | 36.5734 | 37.2384 | 37.4779 | 37.7706 | 38.1887 | 38.952 | 40.8699 | 42.6088 | 0.99767 | 0.94864
NN | New Norfolk | Winter | 14.95 | 13.7569 | 13.7569 | 13.9665 | 14.463 | 14.8108 | 14.8864 | 14.9654 | 15.0842 | 15.5641 | 16.563 | 17.5628 | 0.99134 | 0.89365 | 20.854 | 18.1369 | 18.1369 | 18.7019 | 19.067 | 19.4137 | 19.5385 | 19.6911 | 19.9091 | 20.3071 | 21.3069 | 22.2135 | 0.99676 | 0.85865
NT | Newton (Henty Goldmine) | Summer | 4.0472 | 4.3959 | 4.3959 | 4.4628 | 4.6215 | 4.7326 | 4.7568 | 4.782 | 4.82 | 4.9733 | 5.2925 | 5.612 | 0.99985 | 0.89037 | 3.8815 | 3.9408 | 3.9408 | 4.0636 | 4.1429 | 4.2182 | 4.2454 | 4.2785 | 4.3259 | 4.4124 | 4.6296 | 4.8266 | 0.99991 | 0.875
NW | Norwood | Summer | 16.7155 | 18.4659 | 18.4659 | 18.7472 | 19.4137 | 19.8806 | 19.982 | 20.088 | 20.2475 | 20.8917 | 22.2325 | 23.5745 | 0.9999 | 0.87602 | 29.396 | 28.5123 | 28.5123 | 29.4004 | 29.9745 | 30.5194 | 30.7157 | 30.9556 | 31.2983 | 31.9239 | 33.4957 | 34.9209 | 0.99986 | 0.90014
PL | Port Latta (RT) | Winter | 22.6255 | 11.7582 | 12.5195 | 11.9372 | 12.3617 | 12.6589 | 12.7235 | 12.791 | 12.8926 | 13.3028 | 14.1565 | 15.0111 | 0.93701 | 0.6205 | 21.4055 | 6.7645 | 7.4341 | 6.9752 | 7.1114 | 7.2407 | 7.2872 | 7.3442 | 7.4255 | 7.5739 | 7.9468 | 8.2849 | 0.99897 | 0.86096
PM | Palmerston | Winter | 15.0674 | 14.2197 | 14.4481 | 13.1224 | 13.589 | 13.9157 | 13.9867 | 14.061 | 14.1726 | 14.6235 | 15.562 | 16.5014 | 0.94916 | 0.69309 | 7.1856 | 10.2606 | 10.4615 | 9.4064 | 9.59 | 9.7644 | 9.8272 | 9.9039 | 10.0136 | 10.2137 | 10.7166 | 11.1726 | 0.98535 | 0.56731
QT | Queenstown | Summer | 3.7277 | 5.2756 | 5.2756 | 5.3559 | 5.5464 | 5.6797 | 5.7087 | 5.739 | 5.7846 | 5.9686 | 6.3517 | 6.7351 | 0.99981 | 0.84143 | 6.1594 | 6.0756 | 6.0756 | 6.2649 | 6.3872 | 6.5033 | 6.5451 | 6.5962 | 6.6693 | 6.8026 | 7.1375 | 7.4412 | 0.99994 | 0.88151
RA | Railton | Summer | 50.3439 | 47.0618 | 48.5844 | 47.7786 | 49.4773 | 50.6671 | 50.9256 | 51.1959 | 51.6023 | 53.2441 | 56.6612 | 60.0815 | 0.94147 | 0.76883 | 49.2087 | 46.2414 | 47.5807 | 47.6818 | 48.6128 | 49.4966 | 49.8149 | 50.204 | 50.7597 | 51.7744 | 54.3235 | 56.6349 | 0.98001 | 0.95984
RB22 | Rosebery 22kV | Summer | 2.2636 | 2.1547 | 2.1547 | 2.1875 | 2.2653 | 2.3197 | 2.3316 | 2.3439 | 2.3626 | 2.4377 | 2.5942 | 2.7508 | 1 | 0.64286 | 5.6267 | 2.3149 | 2.3149 | 2.387 | 2.4336 | 2.4778 | 2.4938 | 2.5132 | 2.5411 | 2.5918 | 2.7195 | 2.8352 | 0.99705 | 0
RB44 | Rosebery 44kV | Summer | 42.0001 | 24.2237 | 22.7773 | 24.5926 | 25.467 | 26.0794 | 26.2125 | 26.3516 | 26.5608 | 27.4059 | 29.1647 | 30.9252 | 0.94227 | 0.88287 | 42.8784 | 31.0724 | 29.8 | 32.0402 | 32.6658 | 33.2597 | 33.4736 | 33.7351 | 34.1085 | 34.7903 | 36.5032 | 38.0563 | 0.92948 | 0.86062
RI | Risdon 33kV | Summer | 45.7255 | 51.9616 | 51.9616 | 52.7529 | 56.3893 | 57.7453 | 58.04 | 58.348 | 58.8112 | 60.6824 | 64.5768 | 68.4749 | 0.98618 | 0.79104 | 67.9417 | 66.5925 | 66.5925 | 68.6668 | 71.5563 | 72.8573 | 73.3258 | 73.8986 | 74.7165 | 76.2101 | 79.9624 | 83.3646 | 0.98264 | 0.90684
RK | Rokeby | Summer | 13.4039 | 17.3402 | 17.3402 | 17.6043 | 18.2302 | 18.6686 | 18.7638 | 18.8634 | 19.0132 | 19.6181 | 20.8771 | 22.1373 | 0.99952 | 0.81879 | 22.8645 | 24.6628 | 24.6628 | 25.4311 | 25.9276 | 26.399 | 26.5688 | 26.7763 | 27.0727 | 27.6139 | 28.9735 | 30.2062 | 0.99995 | 0.8624
SD | Scottsdale | Summer | 12.5948 | 11.9955 | 11.9955 | 12.1782 | 12.6112 | 12.9144 | 12.9803 | 13.0492 | 13.1528 | 13.5713 | 14.4422 | 15.314 | 0.98743 | 0.76872 | 11.7572 | 11.8369 | 11.8369 | 12.2056 | 12.4439 | 12.6702 | 12.7516 | 12.8512 | 12.9935 | 13.2532 | 13.9058 | 14.4974 | 0.99964 | 1
SH | Sheffield | Summer | 0 | 1.7425 | 1.7425 | 1.769 | 1.8319 | 1.876 | 1.8855 | 1.8955 | 1.9106 | 1.9714 | 2.0979 | 2.2245 | 0.99185 | 0 | 0 | 1.9766 | 1.9766 | 2.0382 | 2.078 | 2.1158 | 2.1294 | 2.146 | 2.1698 | 2.2131 | 2.3221 | 2.4209 | 0.99598 | 0
SL | St Leonards | Summer | 36.3243 | 16.6205 | 16.6205 | 16.8736 | 17.4736 | 17.8938 | 17.9851 | 18.0805 | 18.224 | 18.8039 | 20.0106 | 21.2186 | 1 | 0.65982 | 31.1972 | 29.5835 | 29.5835 | 30.505 | 31.1006 | 31.666 | 31.8697 | 32.1186 | 32.4741 | 33.1233 | 34.7541 | 36.2328 | 0.9998 | 0.9316
SM | St Marys | Summer | 11.1371 | 12.8837 | 12.8837 | 13.08 | 13.545 | 13.8707 | 13.9415 | 14.0155 | 14.1268 | 14.5762 | 15.5117 | 16.448 | 0.99939 | 0.63105 | 17.1811 | 16.0318 | 16.0318 | 16.5311 | 16.8539 | 17.1603 | 17.2707 | 17.4056 | 17.5982 | 17.95 | 18.8338 | 19.6351 | 0.99922 | 0.75654
SO | Sorell | Summer | 23.7 | 26.7211 | 28.6243 | 27.128 | 28.0926 | 28.7681 | 28.9149 | 29.0683 | 29.2991 | 30.2313 | 32.1715 | 34.1135 | 0.99627 | 0.77083 | 37.4986 | 35.84 | 37.5142 | 36.9564 | 37.678 | 38.363 | 38.6097 | 38.9113 | 39.342 | 40.1284 | 42.1042 | 43.8957 | 0.99909 | 0.92281
SR | Savage River DL | Summer | 23.1001 | 0.99811 | 0.99811 | 1.0133 | 1.0493 | 1.0746 | 1.0801 | 1.0858 | 1.0944 | 1.1292 | 1.2017 | 1.2742 | 1 | 0.79167 | 23.3432 | 1.099 | 1.099 | 1.1333 | 1.1554 | 1.1764 | 1.184 | 1.1932 | 1.2064 | 1.2305 | 1.2911 | 1.3461 | 0.99964 | 0.17
ST | Smithton | Winter | 25.3099 | 24.1733 | 24.1733 | 24.5415 | 25.414 | 26.0252 | 26.1579 | 26.2968 | 26.5055 | 27.3488 | 29.104 | 30.8608 | 0.95114 | 0.87291 | 21.8625 | 21.3308 | 21.3308 | 21.9952 | 22.4247 | 22.8324 | 22.9792 | 23.1587 | 23.415 | 23.8831 | 25.059 | 26.1252 | 0.98096 | 0.79216
TB | Triabunna (RT) | Summer | 5.8378 | 6.2666 | 6.2666 | 6.3621 | 6.5883 | 6.7467 | 6.7811 | 6.8171 | 6.8712 | 7.0899 | 7.5449 | 8.0003 | 0.99495 | 0.662 | 9.0762 | 9.3239 | 9.3239 | 9.6144 | 9.8021 | 9.9803 | 10.0445 | 10.1229 | 10.235 | 10.4396 | 10.9536 | 11.4196 | 0.92612 | 0.82309
TR | Trevallyn | Summer | 38.6613 | 42.7373 | 43.3463 | 46.2478 | 44.9308 | 46.0113 | 46.2461 | 46.4915 | 46.8606 | 48.3515 | 51.4546 | 54.5606 | 0.99913 | 0.88594 | 71.3244 | 68.786 | 69.3218 | 73.4836 | 72.3135 | 73.6283 | 74.1018 | 74.6806 | 75.5072 | 77.0166 | 80.8086 | 84.2468 | 0.9998 | 0.92367
TU | Tungatinah | Summer | 0.74973 | 0.92972 | 0.92972 | 0.94388 | 0.97744 | 1.0009 | 1.006 | 1.0114 | 1.0194 | 1.0519 | 1.1194 | 1.1869 | 0.98394 | 0.61017 | 1.0265 | 1.0921 | 1.0921 | 1.1261 | 1.1481 | 1.169 | 1.1765 | 1.1857 | 1.1988 | 1.2228 | 1.283 | 1.3376 | 0.99846 | 0.83333
UL | Ulverstone | Summer | 19.0966 | 22.3624 | 22.3624 | 22.703 | 23.5102 | 24.0756 | 24.1984 | 24.3268 | 24.52 | 25.3001 | 26.9238 | 28.549 | 0.99829 | 0.67998 | 31.413 | 29.1115 | 29.1115 | 30.0183 | 30.6044 | 31.1608 | 31.3612 | 31.6062 | 31.956 | 32.5948 | 34.1996 | 35.6547 | 0.99998 | 0.84857
WA | Waddamana | Summer | 0.14344 | 0.49896 | 0.49896 | 0.50656 | 0.52457 | 0.53718 | 0.53992 | 0.54279 | 0.5471 | 0.5645 | 0.60073 | 0.63699 | 0.98608 | 0 | 0.90555 | 0.65002 | 0.65002 | 0.67026 | 0.68335 | 0.69578 | 0.70025 | 0.70572 | 0.71353 | 0.72779 | 0.76363 | 0.79612 | 1 | 0
WV | Wesley Vale | Summer | 8.8731 | 8.5858 | 9.3471 | 8.7166 | 9.0265 | 9.2435 | 9.2907 | 9.34 | 9.4142 | 9.7137 | 10.3371 | 10.9611 | 0.99678 | 0.77692 | 11.4381 | 11.109 | 11.7787 | 11.4551 | 11.6787 | 11.891 | 11.9675 | 12.061 | 12.1945 | 12.4383 | 13.0507 | 13.6059 | 0.9997 | 0.8574
|  |  | Summer | [13 empty] | Winter
Code | Name | Non-peaking season | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF
BEZ | Zs-Bellerive | Summer | 7.558 | 9.8484 | 9.8484 | 9.9984 | 10.3539 | 10.6029 | 10.657 | 10.7135 | 10.7986 | 11.1421 | 11.8572 | 12.573 | 0.99994 | 0 | 10.3203 | 10.5204 | 10.5204 | 10.8481 | 11.0599 | 11.2609 | 11.3334 | 11.4219 | 11.5483 | 11.7792 | 12.3591 | 12.885 | 0.99982 | 0
CAZ | Cambridge-Total | Summer | 12.5347 | 16.3127 | 16.3127 | 16.5611 | 17.15 | 17.5624 | 17.652 | 17.7457 | 17.8865 | 18.4556 | 19.6401 | 20.8256 | 0.98311 | 0 | 16.9885 | 18.8922 | 18.8922 | 19.4807 | 19.8611 | 20.2221 | 20.3522 | 20.5112 | 20.7382 | 21.1527 | 22.1942 | 23.1385 | 0.99488 | 0
CLZ | Zs-Claremont | Summer | 12.6915 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 | 0.99857 | 0 | 22.118 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 | 0.99941 | 0
DPZ | Zs-Derwent Park | Summer | 12.9504 | 18.1439 | 18.1439 | 18.4202 | 19.0752 | 19.5339 | 19.6335 | 19.7377 | 19.8944 | 20.5274 | 21.8448 | 23.1634 | 0.97772 | 0 | 19.1852 | 18.729 | 18.729 | 19.3124 | 19.6894 | 20.0474 | 20.1763 | 20.3339 | 20.559 | 20.97 | 22.0025 | 22.9386 | 0.98066 | 0
EHZ | Zs-East Hobart | Summer | 23.8662 | 26.0751 | 26.0751 | 26.4722 | 27.4134 | 28.0726 | 28.2159 | 28.3656 | 28.5908 | 29.5005 | 31.3937 | 33.2888 | 0.97267 | 0 | 29.2574 | 27.121 | 27.121 | 27.9658 | 28.5118 | 29.0302 | 29.2169 | 29.4451 | 29.771 | 30.3662 | 31.8613 | 33.2169 | 0.97304 | 0
GBZ | Zs-Geilston Bay | Summer | 10.354 | 18.3822 | 18.3822 | 18.6622 | 19.3257 | 19.7904 | 19.8914 | 19.997 | 20.1557 | 20.797 | 22.1317 | 23.4677 | 0.99983 | 0 | 19.0827 | 18.8139 | 18.8139 | 19.4 | 19.7787 | 20.1383 | 20.2678 | 20.4262 | 20.6522 | 21.0651 | 22.1022 | 23.0426 | 0.9995 | 0
GRZ | Zs-Gretna | Winter | 1.9864 | 1.0903 | 1.0903 | 1.1069 | 1.1463 | 1.1739 | 1.1799 | 1.1861 | 1.1955 | 1.2336 | 1.3127 | 1.392 | 0.90942 | 0 | 0.31302 | 0.27031 | 0.27031 | 0.27873 | 0.28417 | 0.28934 | 0.2912 | 0.29347 | 0.29672 | 0.30265 | 0.31756 | 0.33107 | 0.98037 | 0
HOZ | Zs-Howrah | Summer | 12.0396 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 | 0.99857 | 0 | 21.2816 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 | 0.99921 | 0
NTZ | Zs-New Town | Summer | 17.1169 | 22.5695 | 22.5695 | 22.9132 | 25.4887 | 26.1016 | 26.2348 | 26.374 | 26.5834 | 27.4292 | 29.1895 | 30.9515 | 0.98946 | 0 | 22.067 | 21.6125 | 21.6125 | 22.2857 | 24.2697 | 24.7109 | 24.8698 | 25.0641 | 25.3415 | 25.8481 | 27.1207 | 28.2747 | 0.99063 | 0
RIZ | Zs-Richmond | Winter | 2.3693 | 2.9973 | 4.9005 | 3.0429 | 3.1511 | 3.2269 | 3.2434 | 3.2606 | 3.2865 | 3.391 | 3.6087 | 3.8265 | 0.98547 | 0 | 3.8639 | 3.6172 | 5.2913 | 3.7298 | 3.8027 | 3.8718 | 3.8967 | 3.9271 | 3.9706 | 4.05 | 4.2494 | 4.4302 | 0.9952 | 0
RPZ | Zs-Rosny Park | Summer | 9.8715 | 11.3639 | 11.3639 | 11.537 | 11.9472 | 12.2345 | 12.2969 | 12.3622 | 12.4603 | 12.8568 | 13.6819 | 14.5078 | 0.99992 | 0 | 15.1503 | 15.0204 | 15.0204 | 15.4882 | 15.7906 | 16.0777 | 16.1811 | 16.3075 | 16.488 | 16.8176 | 17.6457 | 18.3964 | 0.99905 | 0
SBZ | Zs-Sandy Bay | Summer | 18.7989 | 36.1425 | 38.2741 | 36.6929 | 37.9975 | 38.9113 | 39.1098 | 39.3174 | 39.6295 | 40.8904 | 43.5146 | 46.1413 | 0.99611 | 0 | 39.248 | 37.7031 | 39.5781 | 38.8775 | 39.6366 | 40.3572 | 40.6168 | 40.934 | 41.3871 | 42.2144 | 44.2929 | 46.1774 | 0.99933 | 0
SUZ | Zs-Summerleas | Summer | 5.7946 | 7.5904 | 7.5904 | 7.706 | 7.98 | 8.1719 | 8.2136 | 8.2572 | 8.3228 | 8.5876 | 9.1387 | 9.6903 | 0.99911 | 0 | 12.055 | 11.2897 | 11.2897 | 11.6414 | 11.8687 | 12.0844 | 12.1622 | 12.2572 | 12.3928 | 12.6406 | 13.2629 | 13.8272 | 0.99956 | 0
THZ | Zs-Trial Harbour | Summer | 2.2437 | 7.5744 | 6.128 | 7.6898 | 7.9632 | 8.1547 | 8.1963 | 8.2398 | 8.3052 | 8.5695 | 9.1194 | 9.6699 | 0.90922 | 0 | 3.1466 | 2.5009 | 1.2286 | 2.5788 | 2.6292 | 2.677 | 2.6942 | 2.7152 | 2.7453 | 2.8002 | 2.938 | 3.0631 | 0.75751 | 0
WHZ | Zs-West Hobart | Summer | 26.2904 | 27.7002 | 27.7002 | 28.1221 | 29.1219 | 29.8222 | 29.9744 | 30.1335 | 30.3727 | 31.339 | 33.3503 | 35.3634 | 0.99855 | 0 | 37.7186 | 37.243 | 37.243 | 38.4031 | 39.1529 | 39.8647 | 40.1211 | 40.4345 | 40.8821 | 41.6993 | 43.7524 | 45.6139 | 0.99782 | 0
WYZ | Wayatinah | Winter | 1.2223 | 1.6743 | 1.6743 | 1.6998 | 1.7602 | 1.8025 | 1.8117 | 1.8213 | 1.8358 | 1.8942 | 2.0158 | 2.1374 | 0.96549 | 0.7972 | 1.1687 | 1.2821 | 1.2821 | 1.322 | 1.3479 | 1.3724 | 1.3812 | 1.392 | 1.4074 | 1.4355 | 1.5062 | 1.5703 | 0.95562 | 0.10569

## Forecast Data 2.0
|  |  | Summer | [13 empty] | Winter
Code | Name | Non-peaking season | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | PF | Regional DF
AL | Arthurs Lake (DL) | Winter | 0.37223 | 0.52501 | 0.51701 | 0.50991 | 0.50418 | 0.50611 | 0.51376 | 0.51934 | 0.5259 | 0.53195 | 0.53762 | 0.5434 | 0.99922 | 0.80435 | 0.020643 | 0.022543 | 0.022667 | 0.022247 | 0.022039 | 0.022008 | 0.022309 | 0.022516 | 0.022751 | 0.022888 | 0.023313 | 0.023519 | 0.99922 | 0.5974
AV | Avoca | Winter | 10.3262 | 13.2985 | 13.3437 | 13.1804 | 13.0778 | 13.1427 | 13.4131 | 13.6283 | 13.9001 | 14.1524 | 14.4064 | 14.7176 | 0.98539 | 0.43165 | 7.3639 | 8.2335 | 8.4584 | 8.359 | 8.3461 | 8.3759 | 8.5672 | 8.7244 | 8.9231 | 9.0819 | 9.3631 | 9.5878 | 0.98539 | 0.73008
BW | Bridgewater | Summer | 21.0321 | 19.096 | 18.489 | 18.9051 | 18.9796 | 19.0765 | 19.3234 | 19.506 | 19.7753 | 20.1706 | 20.6411 | 21.1634 | 0.9999 | 0.86038 | 36.4906 | 34.895 | 35.1625 | 35.497 | 35.7037 | 35.9336 | 36.6117 | 37.1373 | 37.7814 | 38.3962 | 39.5356 | 40.3752 | 0.99946 | 0.93665
BU | Burnie | Summer | 44.3842 | 41.8144 | 40.8413 | 40.1811 | 39.6538 | 39.9128 | 40.479 | 40.9682 | 41.6218 | 42.3717 | 43.2467 | 44.1577 | 0.99868 | 0.93437 | 57.5142 | 58.1268 | 57.902 | 56.7461 | 56.15 | 56.2288 | 56.965 | 57.5576 | 58.4054 | 59.1245 | 60.7562 | 61.8463 | 0.99863 | 0.92899
BEZ | Zs-Bellerive | 0 | 9.6417 | 7.558 | 7.3066 | 7.1006 | 6.9294 | 6.8764 | 6.9203 | 6.963 | 7.036 | 7.1379 | 7.2637 | 7.3924 |  |  | 10.4442 | 10.3203 | 10.4279 | 10.2694 | 10.1792 | 10.1931 | 10.3633 | 10.5157 | 10.7032 | 10.8832 | 11.2093 | 11.4546
CS | Chapel Street | Summer | 21.6881 | 20.2013 | 19.8779 | 19.4818 | 19.3476 | 19.5381 | 20.01 | 20.505 | 21.1028 | 21.9167 | 22.8124 | 23.7825 | 1 | 0.92902 | 39.343 | 38.759 | 39.268 | 38.7192 | 38.6818 | 38.9351 | 39.8349 | 40.6535 | 41.6554 | 42.6403 | 44.1976 | 45.4115 | 0.99976 | 0.90185
CR | Creek Road | Summer | 56.3751 | 51.9611 | 51.0448 | 50.7017 | 50.1533 | 50.279 | 51.0143 | 51.7271 | 52.6457 | 53.87 | 55.2141 | 56.6653 | 0.99836 | 0.8873 | 87.5113 | 89.0875 | 89.9332 | 89.0702 | 88.6317 | 88.8768 | 90.5321 | 92.0611 | 94.0411 | 96.0477 | 99.3545 | 101.9634 | 0.98957 | 0.9452
DE | Derby | Winter | 7.9449 | 7.8275 | 7.6469 | 7.4737 | 7.3389 | 7.4145 | 7.4909 | 7.542 | 7.6274 | 7.7051 | 7.7963 | 7.908 | 0.99802 | 0.71111 | 6.0029 | 7.0036 | 6.9744 | 6.8194 | 6.7424 | 6.7791 | 6.8636 | 6.9236 | 7.0138 | 7.0676 | 7.2318 | 7.3299 | 1 | 0.32805
DB | Derwent Bridge | Summer | 0.31856 | 0.28717 | 0.28375 | 0.28011 | 0.27733 | 0.27854 | 0.28337 | 0.28712 | 0.29168 | 0.29607 | 0.30049 | 0.30542 | 0.98995 | 0.76923 | 0.31143 | 0.33494 | 0.34036 | 0.33598 | 0.33456 | 0.33559 | 0.34211 | 0.3472 | 0.35297 | 0.35737 | 0.36635 | 0.37262 | 0.99451 | 0.71875
DP | Devonport | Summer | 39.4649 | 36.0101 | 35.9928 | 36.1406 | 35.8579 | 35.8464 | 36.1993 | 36.4508 | 36.8187 | 37.1803 | 37.6438 | 38.0799 | 0.99161 | 0.86328 | 56.3522 | 52.515 | 53.6751 | 53.666 | 53.5888 | 53.6442 | 54.4392 | 55.0365 | 55.7631 | 56.2256 | 57.5066 | 58.2075 | 0.9978 | 0.95374
EL | Electrona | Summer | 9.8412 | 10.0694 | 9.7878 | 9.679 | 9.5433 | 9.5355 | 9.645 | 9.7441 | 9.8831 | 10.0839 | 10.3227 | 10.5671 | 0.99855 | 0.78257 | 16.1153 | 16.2935 | 16.2331 | 15.9397 | 15.7373 | 15.6491 | 15.8016 | 15.9185 | 16.1023 | 16.2988 | 16.7348 | 17.0325 | 0.99827 | 0.88141
EB | Emu Bay (RT) | Summer | 7.7309 | 7.8282 | 7.678 | 7.709 | 7.6779 | 7.6603 | 7.7312 | 7.7719 | 7.8427 | 7.8681 | 7.9185 | 7.9017 | 0.95637 | 0.76111 | 9.4861 | 9.0691 | 9.0724 | 9.06 | 9.0473 | 8.9932 | 9.0792 | 9.1274 | 9.2052 | 9.1975 | 9.3391 | 9.3116 | 0.9601 | 0.8838
GT | George Town | Summer | 13.5516 | 12.9473 | 13.5827 | 16.3103 | 17.5396 | 18.3206 | 18.6793 | 18.859 | 19.1004 | 19.3219 | 19.5741 | 19.8116 | 0.99078 | 0.91086 | 20.701 | 19.5416 | 20.2239 | 22.5526 | 23.5964 | 24.2622 | 24.5581 | 24.6602 | 24.8518 | 24.9389 | 25.4046 | 25.6188 | 0.99989 | 0.77669
GO | Gordon | 0 | 0.33193 | 0.3265 | 0.31328 | 0.30856 | 0.30519 | 0.30428 | 0.30753 | 0.30966 | 0.31289 | 0.31425 | 0.31655 | 0.3162 |  | 0.63415 | 0.2693 | 0.2627 | 0.25731 | 0.2522 | 0.24992 | 0.24787 | 0.25013 | 0.25143 | 0.25348 | 0.25311 | 0.25683 | 0.25588 |  | 0.73585
HA | Hadspen | Summer | 38.3217 | 40.4237 | 39.6969 | 37.8152 | 37.6279 | 37.599 | 37.8427 | 37.9462 | 38.1938 | 38.5556 | 39.0114 | 39.5861 | 1 | 0.93747 | 55.8628 | 54.9768 | 55.75 | 53.8261 | 54.2863 | 54.6654 | 55.6507 | 56.3492 | 57.1776 | 57.7639 | 59.1172 | 59.979 | 0.99997 | 0.93765
HR | Huon River | Summer | 1.7871 | 0.55446 | 0.53171 | 0.5234 | 0.51743 | 0.51561 | 0.52083 | 0.52409 | 0.52919 | 0.53096 | 0.53416 | 0.53275 |  | 0.83333 | 0.81762 | 0.92276 | 0.9037 | 0.88566 | 0.87757 | 0.87019 | 0.87801 | 0.88234 | 0.88926 | 0.8876 | 0.90014 | 0.89621 |  | 0.81818
KE | Kermandie | Summer | 6.3951 | 6.2488 | 6.1025 | 5.9686 | 5.8676 | 5.8449 | 5.9088 | 5.9508 | 6.0149 | 6.077 | 6.1516 | 6.2323 | 0.99336 | 0.86854 | 8.4451 | 8.6874 | 8.7826 | 8.6219 | 8.5544 | 8.5429 | 8.6822 | 8.7829 | 8.911 | 9.0092 | 9.2319 | 9.3955 | 0.99325 | 0.91347
KI11 | Kingston 11kV | Summer | 15.4883 | 16.2318 | 15.7276 | 15.2113 | 14.7267 | 14.5198 | 14.5161 | 14.5192 | 14.588 | 14.7564 | 14.981 | 15.2218 | 0.99986 | 0.7452 | 27.7733 | 27.5402 | 27.7016 | 27.1939 | 26.8776 | 26.8273 | 27.2102 | 27.5601 | 28.0309 | 28.52 | 29.4314 | 30.1039 | 1 | 0.9059
KI33 | Kingston 33kV | Summer | 5.9545 | 5.6704 | 5.6147 | 5.7403 | 5.8116 | 5.9635 | 6.19 | 6.434 | 6.7158 | 7.0977 | 7.524 | 7.9881 | 0.99991 | 0.85913 | 11.1944 | 11.1262 | 11.242 | 11.2802 | 11.3657 | 11.5549 | 11.9422 | 12.3427 | 12.8532 | 13.4427 | 14.2447 | 14.9736 | 0.99555 | 0.94338
KR | Knights Road | Summer | 15.7919 | 15.0454 | 14.4547 | 14.4482 | 14.4122 | 14.4818 | 14.7009 | 14.841 | 15.0221 | 15.1817 | 15.3444 | 15.5351 | 0.9869 | 0.90798 | 19.2064 | 20.0543 | 19.7929 | 19.472 | 19.3043 | 19.2216 | 19.425 | 19.524 | 19.6715 | 19.7543 | 20.0832 | 20.3273 | 0.99261 | 0.96199
LF | Lindisfarne | Summer | 22.4525 | 20.1035 | 19.5646 | 18.984 | 18.5013 | 18.3947 | 18.5224 | 18.6338 | 18.8042 | 19.0804 | 19.3822 | 19.7586 | 0.9999 | 0.81658 | 36.5452 | 35.7593 | 36.0053 | 35.3337 | 34.9522 | 34.9271 | 35.4186 | 35.8099 | 36.2759 | 36.6808 | 37.5481 | 38.14 | 0.99913 | 0.92622
MB | Meadowbank | Winter | 7.7135 | 8.3046 | 8.1507 | 8.0559 | 7.9858 | 8.0197 | 8.1568 | 8.2646 | 8.3974 | 8.5172 | 8.6459 | 8.7678 | 0.99203 | 0.71486 | 4.6448 | 4.6221 | 4.6198 | 4.5333 | 4.494 | 4.4849 | 4.5541 | 4.6091 | 4.6811 | 4.7376 | 4.8655 | 4.9479 | 0.99999 | 0.69937
MT | Mornington | Summer | 22.9744 | 22.6309 | 21.8563 | 21.1222 | 20.5324 | 20.3735 | 20.4973 | 20.6313 | 20.8511 | 21.2223 | 21.6557 | 22.1616 | 0.99878 | 0.82309 | 38.1091 | 38.7639 | 38.9706 | 38.2617 | 37.8579 | 37.8616 | 38.4444 | 38.9525 | 39.5777 | 40.1773 | 41.3154 | 42.1482 | 0.99762 | 0.94757
MY | Mowbray | Summer | 23.1322 | 22.4062 | 21.9251 | 21.8649 | 21.5785 | 21.4923 | 21.6206 | 21.6962 | 21.838 | 21.9937 | 22.1786 | 22.3617 | 0.99792 | 0.73585 | 39.6803 | 38.721 | 38.7052 | 38.3203 | 38.0022 | 37.8392 | 38.2111 | 38.4689 | 38.8195 | 39.0224 | 39.7663 | 40.1188 | 0.99874 | 0.93917
NN | New Norfolk | Winter | 17.7032 | 14.95 | 12.3411 | 12.7529 | 12.8706 | 12.9608 | 13.18 | 13.366 | 13.603 | 13.7756 | 13.9929 | 14.1289 | 0.98984 | 0.89365 | 18.04 | 20.854 | 19.4809 | 19.5114 | 19.6647 | 19.6593 | 19.9361 | 20.155 | 20.457 | 20.599 | 21.0808 | 21.2289 | 0.99505 | 0.85865
NT | Newton (Henty Goldmine) | Summer | 4.2094 | 4.0472 | 4.0044 | 3.9579 | 3.9301 | 3.9368 | 3.9962 | 4.0354 | 4.0888 | 4.1305 | 4.1778 | 4.2247 | 0.99637 | 0.89037 | 3.7798 | 3.8815 | 3.9247 | 3.8608 | 3.8416 | 3.8285 | 3.8812 | 3.9133 | 3.9569 | 3.9762 | 4.0537 | 4.0929 | 0.9964 | 0.875
NH | North Hobart | Summer | 19.8857 | 19.9398 | 19.8138 | 19.8027 | 19.7113 | 19.9225 | 20.3542 | 20.7669 | 21.2348 | 21.7547 | 22.262 | 22.8658 | 0.99976 | 0.82122 | 37.0368 | 35.6257 | 36.1383 | 35.8848 | 35.8487 | 36.1706 | 37.0646 | 37.923 | 38.9446 | 39.9142 | 41.3574 | 42.5949 | 0.99887 | 0.94864
NW | Norwood | Summer | 16.3714 | 16.7155 | 16.1 | 15.7161 | 15.3734 | 15.2735 | 15.3807 | 15.4712 | 15.6219 | 15.8118 | 16.0447 | 16.2834 | 0.99989 | 0.87602 | 29.5689 | 29.396 | 29.2112 | 28.6691 | 28.3761 | 28.2697 | 28.6037 | 28.8504 | 29.1696 | 29.3664 | 29.9722 | 30.2636 | 0.99971 | 0.90014
PM | Palmerston | Winter | 11.5081 | 15.0674 | 15.9442 | 16.2273 | 16.2842 | 16.4179 | 16.7443 | 16.9963 | 17.3093 | 17.5643 | 17.8161 | 18.0998 | 0.95333 | 0.69309 | 6.0975 | 7.1856 | 8.1779 | 8.492 | 8.5979 | 8.6247 | 8.7679 | 8.8755 | 9.018 | 9.1023 | 9.3151 | 9.44 | 0.98298 | 0.56731
PL | Port Latta (RT) | Winter | 22.0321 | 22.6255 | 23.2909 | 23.1324 | 23.0263 | 23.011 | 23.1473 | 23.2525 | 23.406 | 23.5057 | 26.1236 | 26.1849 |  | 0.6205 | 20.7189 | 21.4055 | 22.3483 | 22.1556 | 22.0766 | 22.0139 | 22.1241 | 22.2087 | 22.3388 | 22.3994 | 25.1789 | 25.2418 |  | 0.86096
QT | Queenstown | Summer | 5.1861 | 3.7277 | 3.6754 | 3.605 | 3.5666 | 3.5616 | 3.6063 | 3.6349 | 3.6832 | 3.7358 | 3.8046 | 3.8923 | 0.94921 | 0.84143 | 5.7855 | 6.1594 | 6.2504 | 6.1516 | 6.1243 | 6.1075 | 6.1968 | 6.2572 | 6.3434 | 6.4025 | 6.5627 | 6.6739 | 0.99961 | 0.88151
RA | Railton | Summer | 47.0341 | 50.3439 | 49.5961 | 48.7 | 48.0307 | 49.6116 | 51.0189 | 52.2134 | 52.7354 | 52.2858 | 52.7854 | 51.9716 | 0.99614 | 0.76883 | 47.3585 | 49.2087 | 49.2097 | 48.0484 | 47.4464 | 48.4428 | 49.5747 | 50.4923 | 50.8584 | 50.2149 | 51.0435 | 50.212 | 0.99394 | 0.95984
RI | Risdon 33kV | Summer | 44.4865 | 45.7255 | 45.3484 | 47.5347 | 49.0766 | 50.1338 | 51.2035 | 51.95 | 52.7972 | 53.6439 | 54.4696 | 55.4058 | 0.99614 | 0.79104 | 70.5844 | 67.9417 | 69.0181 | 70.7898 | 72.3912 | 73.3803 | 74.8971 | 76.0066 | 77.2545 | 78.1984 | 80.0729 | 81.4051 | 0.97749 | 0.90684
RK | Rokeby | Summer | 14.3626 | 13.4039 | 12.6989 | 12.123 | 11.6872 | 11.5105 | 11.5141 | 11.5284 | 11.6013 | 11.7894 | 12.0346 | 12.3035 | 0.99998 | 0.81879 | 21.6782 | 22.8645 | 23.0691 | 22.744 | 22.6181 | 22.753 | 23.2288 | 23.6482 | 24.1313 | 24.6359 | 25.4703 | 26.1 | 0.99941 | 0.8624
RB22 | Rosebery 22kV | Summer | 1.9221 | 2.2636 | 2.4016 | 2.3532 | 2.3257 | 2.3194 | 2.344 | 2.3602 | 2.3895 | 2.4241 | 2.4705 | 2.5297 | 0.99891 | 0.64286 | 0.77159 | 5.6267 | 5.7453 | 5.6459 | 5.6116 | 5.587 | 5.6597 | 5.7084 | 5.7817 | 5.8284 | 5.9683 | 6.0552 | 0.99834
RB44 | Rosebery 44kV | Summer | 40.0117 | 42.0001 | 40.1039 | 39.5664 | 39.2252 | 39.1698 | 39.3604 | 39.494 | 39.6985 | 39.7745 | 40.6762 | 40.6294 |  | 0.88287 | 42.7625 | 42.8784 | 41.3864 | 40.7444 | 40.4416 | 40.2791 | 40.4455 | 40.549 | 40.7129 | 40.6756 | 41.7647 | 41.6739 |  | 0.86062
SR | Savage River DL | Summer | 22.9611 | 23.1001 | 25.2805 | 25.2588 | 25.2428 | 25.2341 | 25.2373 | 25.2391 | 25.2449 | 25.2482 | 30.1519 | 30.1534 |  | 0.79167 | 24.3329 | 23.3432 | 25.5383 | 25.5158 | 25.5064 | 25.4986 | 25.5108 | 25.5195 | 25.533 | 25.5376 | 30.444 | 30.448 |  | -0.17391
SD | Scottsdale | Summer | 12.717 | 12.5948 | 12.2591 | 11.9601 | 11.7217 | 11.8224 | 11.9304 | 12.0076 | 12.1465 | 12.2877 | 12.464 | 12.6745 | 0.98231 | 0.76872 | 11.889 | 11.7572 | 11.714 | 11.4179 | 11.255 | 11.339 | 11.4754 | 11.5805 | 11.7524 | 11.8908 | 12.2264 | 12.4833 | 1 | 1
ST | Smithton | Winter | 24.355 | 25.3099 | 26.2251 | 26.4874 | 26.4087 | 26.4217 | 26.7404 | 26.9425 | 27.2489 | 27.4768 | 27.7451 | 28.0015 | 0.95925 | 0.87291 | 20.062 | 21.8625 | 23.2722 | 23.4744 | 23.4989 | 23.4256 | 23.7103 | 23.8891 | 24.1527 | 24.2765 | 24.7651 | 25.0154 | 0.97926 | 0.79216
SO | Sorell | Summer | 23.1344 | 23.7 | 23.4583 | 24.4314 | 24.743 | 24.9164 | 25.24 | 25.4448 | 25.7455 | 26.0873 | 26.5161 | 26.9075 | 0.99992 | 0.77083 | 34.9534 | 37.4986 | 38.08 | 38.8545 | 39.1976 | 39.364 | 39.9664 | 40.3812 | 40.9167 | 41.3749 | 42.4236 | 43.0855 | 0.99998 | 0.92281
SL | St Leonards | Summer | 19.1789 | 36.3243 | 34.8125 | 34.0968 | 33.5185 | 33.3122 | 33.5555 | 33.7078 | 33.9819 | 34.1479 | 34.4003 | 34.4663 | 0.99983 | 0.65982 | 23.7605 | 31.1972 | 30.9234 | 30.2811 | 29.9252 | 29.7612 | 30.0508 | 30.2528 | 30.5219 | 30.6479 | 31.1965 | 31.3996 | 0.99893 | 0.9316
SM | St Marys | Summer | 10.7653 | 11.1371 | 10.7577 | 10.4579 | 10.1914 | 10.0538 | 10.0561 | 10.0398 | 10.0671 | 10.1119 | 10.1924 | 10.2725 | 0.99571 | 0.63105 | 15.1112 | 17.1811 | 17.2928 | 16.9775 | 16.7947 | 16.7159 | 16.9037 | 17.0323 | 17.2134 | 17.3474 | 17.7252 | 17.9586 | 0.99912 | 0.75654
TR | Trevallyn | Summer | 38.8026 | 38.6613 | 37.1623 | 36.7065 | 36.0912 | 35.8842 | 36.0529 | 36.1513 | 36.3832 | 36.7016 | 37.103 | 37.5277 |  | 0.88594 | 68.7532 | 71.3244 | 70.6397 | 69.5726 | 68.9059 | 68.601 | 69.2376 | 69.6539 | 70.2397 | 70.5701 | 71.8702 | 72.4654 | 0.99992 | 0.92367
TB | Triabunna (RT) | Summer | 6.1136 | 5.8378 | 5.8111 | 5.9046 | 5.917 | 5.9452 | 6.036 | 6.1116 | 6.2137 | 6.3307 | 6.475 | 6.611 | 0.99304 | 0.662 | 7.8426 | 9.0762 | 9.1933 | 9.2029 | 9.1935 | 9.1834 | 9.3127 | 9.4109 | 9.5514 | 9.6738 | 9.9467 | 10.1283 | 1 | 0.82309
TU | Tungatinah | Summer | 0.70458 | 0.74973 | 0.73167 | 0.71642 | 0.70512 | 0.70393 | 0.71297 | 0.72017 | 0.73047 | 0.7416 | 0.75488 | 0.76953 | 0.99832 | 0.61017 | 1.1565 | 1.0265 | 1.0362 | 1.0216 | 1.0169 | 1.0189 | 1.0385 | 1.0546 | 1.0742 | 1.0903 | 1.1222 | 1.1453 | 0.98466 | 0.83333
UL | Ulverstone | Summer | 23.2102 | 19.0966 | 18.3364 | 17.7131 | 17.1317 | 16.7992 | 16.7065 | 16.5977 | 16.5712 | 16.6017 | 16.7049 | 16.8159 | 0.99583 | 0.67998 | 32.1449 | 31.413 | 31.4189 | 30.875 | 30.5323 | 30.3636 | 30.6814 | 30.9119 | 31.2463 | 31.4904 | 32.2099 | 32.605 | 1 | 0.84857
WA | Waddamana | Summer | 0.1453 | 0.14344 | 0.13461 | 0.1317 | 0.13212 | 0.13654 | 0.14628 | 0.15938 | 0.17588 | 0.19996 | 0.23012 | 0.2621 | 0.95 |  | 0.55831 | 0.90555 | 0.9111 | 0.89823 | 0.89602 | 0.90382 | 0.92812 | 0.95182 | 0.98179 | 1.0141 | 1.0627 | 1.1053 | 0.99995
CAZ | Cambridge-Total | 0 | 11.5972 | 12.5347 | 12.2623 | 11.9919 | 11.7976 | 11.8209 | 11.9891 | 12.1207 | 12.2792 | 12.4435 | 12.5918 | 12.7962 |  |  | 17.4502 | 16.9885 | 17.0118 | 16.6128 | 16.4143 | 16.3909 | 16.6224 | 16.7917 | 16.9888 | 17.1201 | 17.4447 | 17.6761
WV | Wesley Vale | Summer | 7.9193 | 8.8731 | 8.4105 | 8.1959 | 8.0304 | 7.9395 | 7.9713 | 7.9837 | 8.0338 | 8.0532 | 8.1104 | 8.1003 |  | 0.77692 | 12.614 | 11.4381 | 11.1202 | 10.8327 | 10.6808 | 10.5453 | 10.6117 | 10.6468 | 10.733 | 10.7357 | 10.9305 | 10.9317 |  | 0.8574
CLZ | Zs-Claremont | 0 | 14.3675 | 12.6915 | 12.3336 | 11.9896 | 11.7432 | 11.7204 | 11.8959 | 12.0854 | 12.345 | 12.7175 | 13.1502 | 13.5975 |  |  | 22.3649 | 22.118 | 22.3641 | 21.9673 | 21.8083 | 21.8308 | 22.2188 | 22.5457 | 22.9666 | 23.3675 | 24.0959 | 24.6231
| Zs-CambridgeLF | 0
| Zs-CambridgeMT | 0
DPZ | Zs-Derwent Park | 0 | 14.472 | 12.9504 | 12.751 | 12.5131 | 12.3045 | 12.3101 | 12.4769 | 12.6229 | 12.8048 | 13.0048 | 13.2059 | 13.4335 |  |  | 19.6301 | 19.1852 | 19.4164 | 19.058 | 18.852 | 18.8312 | 19.1122 | 19.3447 | 19.6213 | 19.8379 | 20.2967 | 20.6115
EHZ | Zs-East Hobart | 0 | 23.8871 | 23.8662 | 23.4563 | 25.8637 | 27.0012 | 27.5933 | 28.1669 | 28.5239 | 28.9528 | 29.2924 | 29.6187 | 29.9456 |  |  | 28.5788 | 29.2574 | 29.6632 | 31.8147 | 32.94 | 33.4795 | 34.1831 | 34.6615 | 35.1923 | 35.5262 | 36.2663 | 36.7728
GBZ | Zs-Geilston Bay | 0 | 11.0712 | 10.354 | 9.9818 | 9.6686 | 9.4018 | 9.3182 | 9.362 | 9.411 | 9.5001 | 9.6705 | 9.885 | 10.1046 |  |  | 19.1596 | 19.0827 | 19.1263 | 18.7793 | 18.5522 | 18.4896 | 18.6986 | 18.863 | 19.0743 | 19.2745 | 19.751 | 20.0212
GRZ | Zs-Gretna | 0 | 1.0285 | 1.9864 | 1.9416 | 1.918 | 1.9007 | 1.9054 | 1.9353 | 1.9578 | 1.9863 | 2.0091 | 2.0342 | 2.0542 |  |  | 0.032832 | 0.31302 | 0.31721 | 0.31313 | 0.31199 | 0.31317 | 0.31973 | 0.32525 | 0.33194 | 0.33786 | 0.34866 | 0.35711
HOZ | Zs-Howrah | 0 | 11.3546 | 12.0396 | 11.5871 | 11.2266 | 10.9494 | 10.8814 | 10.9733 | 11.0704 | 11.2184 | 11.4326 | 11.6903 | 11.9613 |  |  | 21.6344 | 21.2816 | 21.5126 | 21.2046 | 21.057 | 21.1297 | 21.5141 | 21.8508 | 22.2417 | 22.604 | 23.2603 | 23.7391
NTZ | Zs-New Town | 0 | 13.7969 | 17.1169 | 17.0384 | 17.0891 | 17.691 | 18.1609 | 18.5833 | 18.8829 | 19.2011 | 19.5502 | 19.9064 | 20.2937 |  |  | 22.3948 | 22.067 | 22.5275 | 22.4988 | 23.1802 | 23.6793 | 24.2949 | 24.7818 | 25.3366 | 25.8535 | 26.6954 | 27.3562
RIZ | Zs-Richmond | 0 | 3.2633 | 2.3693 | 2.234 | 2.1185 | 2.0288 | 1.9743 | 1.9521 | 1.9283 | 1.9158 | 1.912 | 1.9179 | 1.9272 |  |  | 2.957 | 3.8639 | 3.8858 | 3.8119 | 3.7767 | 3.7757 | 3.8355 | 3.8823 | 3.9407 | 3.9928 | 4.0991 | 4.1762
RPZ | Zs-Rosny Park | 0 | 8.4629 | 9.8715 | 9.5571 | 9.29 | 9.067 | 9.0111 | 9.0741 | 9.1337 | 9.2278 | 9.3684 | 9.5351 | 9.7121 |  |  | 15.8764 | 15.1503 | 15.2175 | 14.9433 | 14.778 | 14.7572 | 14.9595 | 15.1315 | 15.3475 | 15.5485 | 15.963 | 16.2412
SBZ | Zs-Sandy Bay | 0 | 20.8534 | 18.7989 | 18.2036 | 17.9705 | 17.6707 | 17.6398 | 17.8429 | 18.0825 | 18.416 | 18.947 | 19.5684 | 20.2212 |  |  | 37.5846 | 39.248 | 39.2574 | 38.7716 | 38.4295 | 38.3492 | 38.8584 | 39.3168 | 39.9507 | 40.5843 | 41.8064 | 42.6291
SUZ | Zs-Summerleas | 0 | 6.0811 | 5.7946 | 5.5758 | 5.519 | 5.416 | 5.3729 | 5.3878 | 5.3999 | 5.4379 | 5.5173 | 5.6174 | 5.7323 |  |  | 11.8138 | 12.055 | 12.1258 | 12.0599 | 12.014 | 12.031 | 12.2151 | 12.3675 | 12.5587 | 12.7346 | 13.0894 | 13.3299
THZ | Zs-Trial Harbour | 0 | 1.9425 | 2.2437 | 2.2965 | 1.9216 | 1.7276 | 1.6645 | 1.6666 | 1.6788 | 1.6992 | 1.7213 | 1.7495 | 1.7864 |  |  | 2.6591 | 3.1466 | 3.1968 | 2.8121 | 2.6243 | 2.555 | 2.5728 | 2.5956 | 2.629 | 2.6513 | 2.7148 | 2.7584
WHZ | Zs-West Hobart | 0 | 23.1266 | 26.2904 | 27.1819 | 27.3333 | 27.2628 | 27.4879 | 27.9795 | 28.4224 | 28.9438 | 29.527 | 30.1052 | 30.7868 |  |  | 37.525 | 37.7186 | 38.7146 | 38.6083 | 38.5951 | 38.8252 | 39.6229 | 40.3429 | 41.2148 | 42.0053 | 43.3042 | 44.3479
WYZ | Wayatinah | 0 | 0.58305 | 1.2223 | 1.3054 | 1.3072 | 1.3076 | 1.3151 | 1.3209 | 1.3263 | 1.3302 | 1.3398 | 1.3457 | 1.3624 |  | 0.7972 | 1.2994 | 1.1687 | 1.3102 | 1.3173 | 1.321 | 1.3362 | 1.3486 | 1.3601 | 1.3692 | 1.3875 | 1.3996 | 1.4293 |  | 0.10569

## T-D data 2.0
Code |  |  |  | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | Load transfer point | Non-peaking season
AL | Substation capacity (winter and summer) (MVA) | Total | ALSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
AL | Substation capacity (winter and summer) (MVA) | Firm delivery | ALSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
AL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ALSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
AL | Maximum demand forecast(peak season) | Maximum demand (MW) | ALMaximum demand forecast(peak season)Maximum demand (MW) | 0.51914 | 0.53758 | 0.53758 | 0.54577 | 0.56518 | 0.57877 | 0.58172 | 0.58481 | 0.58945 | 0.6082 | 0.64724 | 0.68631 |  | Winter
AL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.078339 | 0.081123 | 0.081123 | 0.082358 | 0.085287 | 0.087338 | 0.087783 | 0.088249 | 0.08895 | 0.09178 | 0.09767 | 0.10357 |  | Winter
AL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ALMaximum demand forecast(peak season)Maximum demand (MVA) | 0.52501 | 0.54367 | 0.54367 | 0.55195 | 0.57158 | 0.58532 | 0.58831 | 0.59143 | 0.59612 | 0.61509 | 0.65457 | 0.69408 |  | Winter
AL | Maximum demand forecast(peak season) | Power factor (coincident) | ALMaximum demand forecast(peak season)Power factor (coincident) | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 | 0.98881 |  | Winter
AL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ALMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.015041 | 0.13404 | 0.13404 | 0.13821 | 0.14091 | 0.14348 | 0.1444 | 0.14553 | 0.14714 | 0.15008 | 0.15747 | 0.16417 |  | Winter
AL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.016792 | 0.14964 | 0.14964 | 0.1543 | 0.15732 | 0.16018 | 0.16121 | 0.16247 | 0.16426 | 0.16755 | 0.1758 | 0.18328 |  | Winter
AL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ALMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.022543 | 0.2009 | 0.2009 | 0.20715 | 0.2112 | 0.21504 | 0.21642 | 0.21811 | 0.22053 | 0.22493 | 0.23601 | 0.24605 |  | Winter
AL | Hours exceeding | 95% of maximum demand | ALHours exceeding95% of maximum demand | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 |  | Winter
AL | Hours exceeding | Firm capacity (continuous rating) | ALHours exceedingFirm capacity (continuous rating) | [13 empty] | Winter
AL | Hours exceeding | Firm capacity (short-term rating) | ALHours exceedingFirm capacity (short-term rating) | [13 empty] | Winter
AL | Regional diversity factor | Summer | ALRegional diversity factorSummer | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 | 0.80435 |  | Winter
AL | Regional diversity factor | Winter | ALRegional diversity factorWinter | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 | 0.5974 |  | Winter
AL | Load transfer capacity (MVA) | 1 | ALLoad transfer capacity (MVA)1 | 0.1 | [11 empty] | Wayatinah | Winter
AL | Load transfer capacity (MVA) | 2 | ALLoad transfer capacity (MVA)2 | [12 empty] | 0 | Winter
AL | Load transfer capacity (MVA) | 3 | ALLoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
AL | Load transfer capacity (MVA) | 4 | ALLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
AL | Load transfer capacity (MVA) | 5 | ALLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
AL | Embedded generation capacity (MVA) | Units less than 100 kVA | ALEmbedded generation capacity (MVA)Units less than 100 kVA | 0.36324 | [12 empty] | Winter
AL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ALEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.6 | [12 empty] | Winter
AV | Substation capacity (winter and summer) (MVA) | Total | AVSubstation capacity (winter and summer) (MVA)Total | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | Winter
AV | Substation capacity (winter and summer) (MVA) | Firm delivery | AVSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
AV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | AVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
AV | Maximum demand forecast(peak season) | Maximum demand (MW) | AVMaximum demand forecast(peak season)Maximum demand (MW) | 13.0981 | 10.4306 | 10.4306 | 10.5895 | 10.966 | 11.2297 | 11.287 | 11.3469 | 11.437 | 11.8009 | 12.5582 | 13.3163 |  | Winter
AV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.2998 | 1.8314 | 1.8314 | 1.8593 | 1.9254 | 1.9717 | 1.9818 | 1.9923 | 2.0081 | 2.072 | 2.205 | 2.3381 |  | Winter
AV | Maximum demand forecast(peak season) | Maximum demand (MVA) | AVMaximum demand forecast(peak season)Maximum demand (MVA) | 13.2985 | 10.5902 | 10.5902 | 10.7515 | 11.1337 | 11.4015 | 11.4597 | 11.5205 | 11.6119 | 11.9814 | 12.7503 | 13.52 |  | Winter
AV | Maximum demand forecast(peak season) | Power factor (coincident) | AVMaximum demand forecast(peak season)Power factor (coincident) | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 | 0.98493 |  | Winter
AV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | AVMaximum demand forecast(non-peak season)Maximum demand (MW) | 8.2335 | 6.4502 | 6.4502 | 6.6511 | 6.781 | 6.9043 | 6.9487 | 7.003 | 7.0805 | 7.222 | 7.5776 | 7.9 |  | Winter
AV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.00025751 | 0.00020173 | 0.00020173 | 0.00020802 | 0.00021208 | 0.00021593 | 0.00021732 | 0.00021902 | 0.00022145 | 0.00022587 | 0.00023699 | 0.00024708 |  | Winter
AV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | AVMaximum demand forecast(non-peak season)Maximum demand (MVA) | 8.2335 | 6.4502 | 6.4502 | 6.6511 | 6.781 | 6.9043 | 6.9487 | 7.003 | 7.0805 | 7.222 | 7.5776 | 7.9 |  | Winter
AV | Hours exceeding | 95% of maximum demand | AVHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Winter
AV | Hours exceeding | Firm capacity (continuous rating) | AVHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
AV | Hours exceeding | Firm capacity (short-term rating) | AVHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
AV | Regional diversity factor | Summer | AVRegional diversity factorSummer | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 | 0.43165 |  | Winter
AV | Regional diversity factor | Winter | AVRegional diversity factorWinter | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 | 0.73008 |  | Winter
AV | Load transfer capacity (MVA) | 1 | AVLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Palmerston | Winter
AV | Load transfer capacity (MVA) | 2 | AVLoad transfer capacity (MVA)2 | 4.6 | [11 empty] | St Marys | Winter
AV | Load transfer capacity (MVA) | 3 | AVLoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
AV | Load transfer capacity (MVA) | 4 | AVLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
AV | Load transfer capacity (MVA) | 5 | AVLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
AV | Embedded generation capacity (MVA) | Units less than 100 kVA | AVEmbedded generation capacity (MVA)Units less than 100 kVA | 1.2114 | [12 empty] | Winter
AV | Embedded generation capacity (MVA) | Units greater than 100 kVA | AVEmbedded generation capacity (MVA)Units greater than 100 kVA | 5 | [12 empty] | Winter
BU | Substation capacity (winter and summer) (MVA) | Total | BUSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
BU | Substation capacity (winter and summer) (MVA) | Firm delivery | BUSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
BU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | Summer
BU | Maximum demand forecast(peak season) | Maximum demand (MW) | BUMaximum demand forecast(peak season)Maximum demand (MW) | 58.0306 | 59.7417 | 60.2766 | 61.6026 | 62.8054 | 63.9473 | 64.3585 | 64.8612 | 65.5792 | 66.8901 | 70.1835 | 73.1696 |  | Summer
BU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.3423 | 3.4408 | 3.4716 | 3.548 | 3.6173 | 3.6831 | 3.7067 | 3.7357 | 3.777 | 3.8526 | 4.0422 | 4.2142 |  | Summer
BU | Maximum demand forecast(peak season) | Maximum demand (MVA) | BUMaximum demand forecast(peak season)Maximum demand (MVA) | 58.1268 | 59.8407 | 60.3765 | 61.7047 | 62.9095 | 64.0533 | 64.4652 | 64.9687 | 65.6878 | 67.0009 | 70.2998 | 73.2909 |  | Summer
BU | Maximum demand forecast(peak season) | Power factor (coincident) | BUMaximum demand forecast(peak season)Power factor (coincident) | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 |  | Summer
BU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BUMaximum demand forecast(non-peak season)Maximum demand (MW) | 41.7497 | 43.7259 | 44.334 | 44.3918 | 45.9702 | 47.0756 | 47.3158 | 47.5669 | 47.9446 | 49.47 | 52.6449 | 55.8227 |  | Summer
BU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.3245 | 2.4345 | 2.4683 | 2.4716 | 2.5594 | 2.621 | 2.6344 | 2.6483 | 2.6694 | 2.7543 | 2.9311 | 3.108 |  | Summer
BU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BUMaximum demand forecast(non-peak season)Maximum demand (MVA) | 41.8144 | 43.7936 | 44.4027 | 44.4606 | 46.0414 | 47.1486 | 47.3891 | 47.6406 | 48.0188 | 49.5466 | 52.7264 | 55.9091 |  | Summer
BU | Hours exceeding | 95% of maximum demand | BUHours exceeding95% of maximum demand | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 |  | Summer
BU | Hours exceeding | Firm capacity (continuous rating) | BUHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
BU | Hours exceeding | Firm capacity (short-term rating) | BUHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
BU | Regional diversity factor | Summer | BURegional diversity factorSummer | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 |  | Summer
BU | Regional diversity factor | Winter | BURegional diversity factorWinter | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 | 0.92899 |  | Summer
BU | Load transfer capacity (MVA) | 1 | BULoad transfer capacity (MVA)1 | 8.8 | [11 empty] | Port Latta | Summer
BU | Load transfer capacity (MVA) | 2 | BULoad transfer capacity (MVA)2 | 8.8 | [11 empty] | Ulverstone | Summer
BU | Load transfer capacity (MVA) | 3 | BULoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
BU | Load transfer capacity (MVA) | 4 | BULoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
BU | Load transfer capacity (MVA) | 5 | BULoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
BU | Embedded generation capacity (MVA) | Units less than 100 kVA | BUEmbedded generation capacity (MVA)Units less than 100 kVA | 13.9754 | [12 empty] | Summer
BU | Embedded generation capacity (MVA) | Units greater than 100 kVA | BUEmbedded generation capacity (MVA)Units greater than 100 kVA | 4.1353 | [12 empty] | Summer
BW | Substation capacity (winter and summer) (MVA) | Total | BWSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Summer
BW | Substation capacity (winter and summer) (MVA) | Firm delivery | BWSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Summer
BW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | Summer
BW | Maximum demand forecast(peak season) | Maximum demand (MW) | BWMaximum demand forecast(peak season)Maximum demand (MW) | 34.8864 | 35.4531 | 35.3192 | 36.5298 | 36.5673 | 37.2322 | 37.4716 | 37.7643 | 38.1823 | 38.9456 | 40.8631 | 42.6017 |  | Summer
BW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.77139 | 0.78392 | 0.78096 | 0.80773 | 0.80856 | 0.82326 | 0.82855 | 0.83503 | 0.84427 | 0.86115 | 0.90355 | 0.94199 |  | Summer
BW | Maximum demand forecast(peak season) | Maximum demand (MVA) | BWMaximum demand forecast(peak season)Maximum demand (MVA) | 34.895 | 35.4617 | 35.3278 | 36.5387 | 36.5763 | 37.2413 | 37.4808 | 37.7735 | 38.1916 | 38.9551 | 40.8731 | 42.6121 |  | Summer
BW | Maximum demand forecast(peak season) | Power factor (coincident) | BWMaximum demand forecast(peak season)Power factor (coincident) | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 | 0.99976 |  | Summer
BW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BWMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.0931 | 24.4824 | 24.3301 | 24.8243 | 24.9387 | 25.5384 | 25.6687 | 25.8049 | 26.0098 | 26.8373 | 28.5597 | 30.2837 |  | Summer
BW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.33109 | 0.42455 | 0.42191 | 0.43048 | 0.43246 | 0.44286 | 0.44512 | 0.44748 | 0.45104 | 0.46539 | 0.49525 | 0.52515 |  | Summer
BW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BWMaximum demand forecast(non-peak season)Maximum demand (MVA) | 19.096 | 24.486 | 24.3338 | 24.828 | 24.9425 | 25.5422 | 25.6726 | 25.8088 | 26.0137 | 26.8414 | 28.564 | 30.2882 |  | Summer
BW | Hours exceeding | 95% of maximum demand | BWHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 |  | Summer
BW | Hours exceeding | Firm capacity (continuous rating) | BWHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
BW | Hours exceeding | Firm capacity (short-term rating) | BWHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
BW | Regional diversity factor | Summer | BWRegional diversity factorSummer | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 | 0.86038 |  | Summer
BW | Regional diversity factor | Winter | BWRegional diversity factorWinter | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 | 0.93665 |  | Summer
BW | Load transfer capacity (MVA) | 1 | BWLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Claremont | Summer
BW | Load transfer capacity (MVA) | 2 | BWLoad transfer capacity (MVA)2 | 3.1 | [11 empty] | Derwent Park | Summer
BW | Load transfer capacity (MVA) | 3 | BWLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | New Norfolk | Summer
BW | Load transfer capacity (MVA) | 4 | BWLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
BW | Load transfer capacity (MVA) | 5 | BWLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
BW | Embedded generation capacity (MVA) | Units less than 100 kVA | BWEmbedded generation capacity (MVA)Units less than 100 kVA | 10.2075 | [12 empty] | Summer
BW | Embedded generation capacity (MVA) | Units greater than 100 kVA | BWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.32 | [12 empty] | Summer
CR | Substation capacity (winter and summer) (MVA) | Total | CRSubstation capacity (winter and summer) (MVA)Total | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | Summer
CR | Substation capacity (winter and summer) (MVA) | Firm delivery | CRSubstation capacity (winter and summer) (MVA)Firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
CR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | Summer
CR | Maximum demand forecast(peak season) | Maximum demand (MW) | CRMaximum demand forecast(peak season)Maximum demand (MW) | 88.276 | 91.705 | 93.5629 | 94.5615 | 96.4078 | 98.1606 | 98.7919 | 99.5635 | 100.6656 | 102.6778 | 107.7333 | 112.3171 |  | Summer
CR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 11.9971 | 12.4631 | 12.7156 | 12.8514 | 13.1023 | 13.3405 | 13.4263 | 13.5312 | 13.6809 | 13.9544 | 14.6415 | 15.2644 |  | Summer
CR | Maximum demand forecast(peak season) | Maximum demand (MVA) | CRMaximum demand forecast(peak season)Maximum demand (MVA) | 89.0875 | 92.548 | 94.423 | 95.4308 | 97.2941 | 99.063 | 99.7001 | 100.4788 | 101.591 | 103.6217 | 108.7237 | 113.3496 |  | Summer
CR | Maximum demand forecast(peak season) | Power factor (coincident) | CRMaximum demand forecast(peak season)Power factor (coincident) | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 |  | Summer
CR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CRMaximum demand forecast(non-peak season)Maximum demand (MW) | 51.7019 | 64.2035 | 66.3244 | 65.1813 | 67.4988 | 69.122 | 69.4746 | 69.8433 | 70.3978 | 72.6376 | 77.2993 | 81.9654 |  | Summer
CR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 5.1836 | 6.4369 | 6.6496 | 6.535 | 6.7673 | 6.9301 | 6.9654 | 7.0024 | 7.058 | 7.2825 | 7.7499 | 8.2177 |  | Summer
CR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 51.9611 | 64.5253 | 66.6569 | 65.5081 | 67.8372 | 69.4685 | 69.8229 | 70.1935 | 70.7507 | 73.0018 | 77.6869 | 82.3763 |  | Summer
CR | Hours exceeding | 95% of maximum demand | CRHours exceeding95% of maximum demand | 1 | 1 | [11 empty] | Summer | bar: 2024 to 2033
CR | Hours exceeding | Firm capacity (continuous rating) | CRHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
CR | Hours exceeding | Firm capacity (short-term rating) | CRHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
CR | Regional diversity factor | Summer | CRRegional diversity factorSummer | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 | 0.8873 |  | Summer
CR | Regional diversity factor | Winter | CRRegional diversity factorWinter | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 | 0.9452 |  | Summer
CR | Load transfer capacity (MVA) | 1 | CRLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont | Summer
CR | Load transfer capacity (MVA) | 2 | CRLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park | Summer
CR | Load transfer capacity (MVA) | 3 | CRLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town | Summer
CR | Load transfer capacity (MVA) | 4 | CRLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart | Summer
CR | Load transfer capacity (MVA) | 5 | CRLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
CR | Embedded generation capacity (MVA) | Units less than 100 kVA | CREmbedded generation capacity (MVA)Units less than 100 kVA | 15.6436 | [12 empty] | Summer
CR | Embedded generation capacity (MVA) | Units greater than 100 kVA | CREmbedded generation capacity (MVA)Units greater than 100 kVA | 1.065 | [12 empty] | Summer
CS | Substation capacity (winter and summer) (MVA) | Total | CSSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
CS | Substation capacity (winter and summer) (MVA) | Firm delivery | CSSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
CS | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CSSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
CS | Maximum demand forecast(peak season) | Maximum demand (MW) | CSMaximum demand forecast(peak season)Maximum demand (MW) | 38.7585 | 40.3606 | 40.3606 | 41.6178 | 42.4303 | 43.2018 | 43.4796 | 43.8192 | 44.3042 | 45.1899 | 47.4149 | 49.4322 |  | Summer
CS | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.20018 | 0.20845 | 0.20845 | 0.21495 | 0.21914 | 0.22313 | 0.22456 | 0.22632 | 0.22882 | 0.2334 | 0.24489 | 0.25531 |  | Summer
CS | Maximum demand forecast(peak season) | Maximum demand (MVA) | CSMaximum demand forecast(peak season)Maximum demand (MVA) | 38.759 | 40.3611 | 40.3611 | 41.6183 | 42.4309 | 43.2024 | 43.4802 | 43.8198 | 44.3048 | 45.1905 | 47.4155 | 49.4329 |  | Summer
CS | Maximum demand forecast(peak season) | Power factor (coincident) | CSMaximum demand forecast(peak season)Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 |  | Summer
CS | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CSMaximum demand forecast(non-peak season)Maximum demand (MW) | 20.2006 | 24.2404 | 24.2404 | 24.6096 | 25.4846 | 26.0974 | 26.2305 | 26.3697 | 26.5791 | 27.4247 | 29.1848 | 30.9465 |  | Summer
CS | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.16681 | 0.20017 | 0.20017 | 0.20322 | 0.21045 | 0.21551 | 0.21661 | 0.21775 | 0.21948 | 0.22647 | 0.241 | 0.25555 |  | Summer
CS | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CSMaximum demand forecast(non-peak season)Maximum demand (MVA) | 20.2013 | 24.2412 | 24.2412 | 24.6104 | 25.4854 | 26.0983 | 26.2314 | 26.3706 | 26.58 | 27.4257 | 29.1858 | 30.9475 |  | Summer
CS | Hours exceeding | 95% of maximum demand | CSHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
CS | Hours exceeding | Firm capacity (continuous rating) | CSHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
CS | Hours exceeding | Firm capacity (short-term rating) | CSHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
CS | Regional diversity factor | Summer | CSRegional diversity factorSummer | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 | 0.92902 |  | Summer
CS | Regional diversity factor | Winter | CSRegional diversity factorWinter | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 | 0.90185 |  | Summer
CS | Load transfer capacity (MVA) | 1 | CSLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont | Summer
CS | Load transfer capacity (MVA) | 2 | CSLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park | Summer
CS | Load transfer capacity (MVA) | 3 | CSLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town | Summer
CS | Load transfer capacity (MVA) | 4 | CSLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart | Summer
CS | Load transfer capacity (MVA) | 5 | CSLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
CS | Embedded generation capacity (MVA) | Units less than 100 kVA | CSEmbedded generation capacity (MVA)Units less than 100 kVA | 7.4504 | [12 empty] | Summer
CS | Embedded generation capacity (MVA) | Units greater than 100 kVA | CSEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.69 | [12 empty] | Summer
DB | Substation capacity (winter and summer) (MVA) | Total | DBSubstation capacity (winter and summer) (MVA)Total | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Summer
DB | Substation capacity (winter and summer) (MVA) | Firm delivery | DBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
DB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
DB | Maximum demand forecast(peak season) | Maximum demand (MW) | DBMaximum demand forecast(peak season)Maximum demand (MW) | 0.33494 | 0.33628 | 0.33628 | 0.34676 | 0.35353 | 0.35996 | 0.36227 | 0.3651 | 0.36914 | 0.37652 | 0.39506 | 0.41187 |  | Summer
DB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
DB | Maximum demand forecast(peak season) | Maximum demand (MVA) | DBMaximum demand forecast(peak season)Maximum demand (MVA) | 0.33494 | 0.33628 | 0.33628 | 0.34676 | 0.35353 | 0.35996 | 0.36227 | 0.3651 | 0.36914 | 0.37652 | 0.39506 | 0.41187 |  | Summer
DB | Maximum demand forecast(peak season) | Power factor (coincident) | DBMaximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | [11 empty] | Summer | bar: 2024 to 2033
DB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DBMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.28421 | 0.32925 | 0.32925 | 0.33426 | 0.34615 | 0.35447 | 0.35628 | 0.35817 | 0.36101 | 0.3725 | 0.39641 | 0.42033 |  | Summer
DB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.041129 | 0.047645 | 0.047645 | 0.048371 | 0.050091 | 0.051295 | 0.051557 | 0.051831 | 0.052242 | 0.053904 | 0.057364 | 0.060826 |  | Summer
DB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.28717 | 0.33268 | 0.33268 | 0.33774 | 0.34975 | 0.35816 | 0.35999 | 0.3619 | 0.36477 | 0.37638 | 0.40053 | 0.42471 |  | Summer
DB | Hours exceeding | 95% of maximum demand | DBHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | Summer
DB | Hours exceeding | Firm capacity (continuous rating) | DBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
DB | Hours exceeding | Firm capacity (short-term rating) | DBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
DB | Regional diversity factor | Summer | DBRegional diversity factorSummer | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 | 0.76923 |  | Summer
DB | Regional diversity factor | Winter | DBRegional diversity factorWinter | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 | 0.71875 |  | Summer
DB | Load transfer capacity (MVA) | 1 | DBLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
DB | Load transfer capacity (MVA) | 2 | DBLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
DB | Load transfer capacity (MVA) | 3 | DBLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
DB | Load transfer capacity (MVA) | 4 | DBLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
DB | Load transfer capacity (MVA) | 5 | DBLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
DB | Embedded generation capacity (MVA) | Units less than 100 kVA | DBEmbedded generation capacity (MVA)Units less than 100 kVA | 0 | [12 empty] | Summer
DB | Embedded generation capacity (MVA) | Units greater than 100 kVA | DBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
DE | Substation capacity (winter and summer) (MVA) | Total | DESubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
DE | Substation capacity (winter and summer) (MVA) | Firm delivery | DESubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
DE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
DE | Maximum demand forecast(peak season) | Maximum demand (MW) | DEMaximum demand forecast(peak season)Maximum demand (MW) | 7.7716 | 6.8418 | 6.8418 | 6.946 | 7.193 | 7.3659 | 7.4035 | 7.4428 | 7.5019 | 7.7406 | 8.2373 | 8.7346 |  | Winter
DE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.93315 | 0.82151 | 0.82151 | 0.83402 | 0.86367 | 0.88444 | 0.88895 | 0.89367 | 0.90077 | 0.92943 | 0.98907 | 1.0488 |  | Winter
DE | Maximum demand forecast(peak season) | Maximum demand (MVA) | DEMaximum demand forecast(peak season)Maximum demand (MVA) | 7.8275 | 6.8909 | 6.8909 | 6.9959 | 7.2446 | 7.4188 | 7.4567 | 7.4963 | 7.5558 | 7.7962 | 8.2965 | 8.7973 |  | Winter
DE | Maximum demand forecast(peak season) | Power factor (coincident) | DEMaximum demand forecast(peak season)Power factor (coincident) | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 |  | Winter
DE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DEMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.7245 | 5.5792 | 5.5792 | 5.753 | 5.8653 | 5.972 | 6.0104 | 6.0573 | 6.1244 | 6.2468 | 6.5544 | 6.8332 |  | Winter
DE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.9574 | 1.624 | 1.624 | 1.6746 | 1.7073 | 1.7384 | 1.7495 | 1.7632 | 1.7827 | 1.8184 | 1.9079 | 1.9891 |  | Winter
DE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.0036 | 5.8108 | 5.8108 | 5.9918 | 6.1088 | 6.2198 | 6.2598 | 6.3087 | 6.3786 | 6.5061 | 6.8264 | 7.1169 |  | Winter
DE | Hours exceeding | 95% of maximum demand | DEHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Winter
DE | Hours exceeding | Firm capacity (continuous rating) | DEHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
DE | Hours exceeding | Firm capacity (short-term rating) | DEHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
DE | Regional diversity factor | Summer | DERegional diversity factorSummer | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 | 0.71111 |  | Winter
DE | Regional diversity factor | Winter | DERegional diversity factorWinter | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 | 0.32805 |  | Winter
DE | Load transfer capacity (MVA) | 1 | DELoad transfer capacity (MVA)1 | 5.3 | [11 empty] | Scottsdale | Winter
DE | Load transfer capacity (MVA) | 2 | DELoad transfer capacity (MVA)2 | 1.6 | [11 empty] | St Marys | Winter
DE | Load transfer capacity (MVA) | 3 | DELoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
DE | Load transfer capacity (MVA) | 4 | DELoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
DE | Load transfer capacity (MVA) | 5 | DELoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
DE | Embedded generation capacity (MVA) | Units less than 100 kVA | DEEmbedded generation capacity (MVA)Units less than 100 kVA | 1.3562 | [12 empty] | Winter
DE | Embedded generation capacity (MVA) | Units greater than 100 kVA | DEEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.02 | [12 empty] | Winter
DP | Substation capacity (winter and summer) (MVA) | Total | DPSubstation capacity (winter and summer) (MVA)Total | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | Summer
DP | Substation capacity (winter and summer) (MVA) | Firm delivery | DPSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
DP | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | Summer
DP | Maximum demand forecast(peak season) | Maximum demand (MW) | DPMaximum demand forecast(peak season)Maximum demand (MW) | 52.3558 | 53.0652 | 53.399 | 58.1603 | 55.0846 | 56.0861 | 56.4469 | 56.8877 | 57.5174 | 58.6672 | 61.5557 | 64.1748 |  | Summer
DP | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 4.0853 | 4.1406 | 4.1667 | 4.5382 | 4.2982 | 4.3763 | 4.4045 | 4.4389 | 4.488 | 4.5777 | 4.8031 | 5.0075 |  | Summer
DP | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPMaximum demand forecast(peak season)Maximum demand (MVA) | 52.515 | 53.2265 | 53.5613 | 58.337 | 55.2521 | 56.2566 | 56.6184 | 57.0607 | 57.6922 | 58.8455 | 61.7428 | 64.3698 |  | Summer
DP | Maximum demand forecast(peak season) | Power factor (coincident) | DPMaximum demand forecast(peak season)Power factor (coincident) | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 |  | Summer
DP | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DPMaximum demand forecast(non-peak season)Maximum demand (MW) | 35.6735 | 36.2555 | 36.6326 | 40.636 | 37.3235 | 38.221 | 38.4161 | 38.6199 | 38.9265 | 40.165 | 42.7427 | 45.3228 |  | Summer
DP | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.9119 | 4.992 | 5.044 | 5.5952 | 5.1391 | 5.2627 | 5.2895 | 5.3176 | 5.3598 | 5.5303 | 5.8853 | 6.2405 |  | Summer
DP | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPMaximum demand forecast(non-peak season)Maximum demand (MVA) | 36.0101 | 36.5976 | 36.9782 | 41.0194 | 37.6757 | 38.5816 | 38.7785 | 38.9843 | 39.2938 | 40.544 | 43.146 | 45.7504 |  | Summer
DP | Hours exceeding | 95% of maximum demand | DPHours exceeding95% of maximum demand | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 |  | Summer
DP | Hours exceeding | Firm capacity (continuous rating) | DPHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
DP | Hours exceeding | Firm capacity (short-term rating) | DPHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
DP | Regional diversity factor | Summer | DPRegional diversity factorSummer | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 | 0.86328 |  | Summer
DP | Regional diversity factor | Winter | DPRegional diversity factorWinter | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 | 0.95374 |  | Summer
DP | Load transfer capacity (MVA) | 1 | DPLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Railton | Summer
DP | Load transfer capacity (MVA) | 2 | DPLoad transfer capacity (MVA)2 | 6.3 | [11 empty] | Ulverstone | Summer
DP | Load transfer capacity (MVA) | 3 | DPLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
DP | Load transfer capacity (MVA) | 4 | DPLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
DP | Load transfer capacity (MVA) | 5 | DPLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
DP | Embedded generation capacity (MVA) | Units less than 100 kVA | DPEmbedded generation capacity (MVA)Units less than 100 kVA | 11.2123 | [12 empty] | Summer
DP | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.95333 | [12 empty] | Summer
EB | Substation capacity (winter and summer) (MVA) | Total | EBSubstation capacity (winter and summer) (MVA)Total | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | Summer
EB | Substation capacity (winter and summer) (MVA) | Firm delivery | EBSubstation capacity (winter and summer) (MVA)Firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | Summer
EB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | Summer
EB | Maximum demand forecast(peak season) | Maximum demand (MW) | EBMaximum demand forecast(peak season)Maximum demand (MW) | 8.8371 | 8.631 | 8.631 | 8.8998 | 9.0736 | 9.2386 | 9.298 | 9.3706 | 9.4743 | 9.6637 | 10.1395 | 10.5709 |  | Summer
EB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.0382 | 1.9907 | 1.9907 | 2.0527 | 2.0927 | 2.1308 | 2.1445 | 2.1612 | 2.1852 | 2.2288 | 2.3386 | 2.4381 |  | Summer
EB | Maximum demand forecast(peak season) | Maximum demand (MVA) | EBMaximum demand forecast(peak season)Maximum demand (MVA) | 9.0691 | 8.8576 | 8.8576 | 9.1335 | 9.3118 | 9.4811 | 9.5421 | 9.6166 | 9.7231 | 9.9174 | 10.4057 | 10.8484 |  | Summer
EB | Maximum demand forecast(peak season) | Power factor (coincident) | EBMaximum demand forecast(peak season)Power factor (coincident) | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 |  | Summer
EB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | EBMaximum demand forecast(non-peak season)Maximum demand (MW) | 7.5343 | 7.3376 | 7.3376 | 7.4494 | 7.7143 | 7.8998 | 7.9401 | 7.9822 | 8.0456 | 8.3016 | 8.8343 | 9.3676 |  | Summer
EB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.1246 | 2.0691 | 2.0691 | 2.1007 | 2.1753 | 2.2277 | 2.239 | 2.2509 | 2.2688 | 2.341 | 2.4912 | 2.6416 |  | Summer
EB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.8282 | 7.6238 | 7.6238 | 7.7399 | 8.0151 | 8.2078 | 8.2497 | 8.2935 | 8.3593 | 8.6253 | 9.1789 | 9.7329 |  | Summer
EB | Hours exceeding | 95% of maximum demand | EBHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 |  | Summer
EB | Hours exceeding | Firm capacity (continuous rating) | EBHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
EB | Hours exceeding | Firm capacity (short-term rating) | EBHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
EB | Regional diversity factor | Summer | EBRegional diversity factorSummer | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 | 0.76111 |  | Summer
EB | Regional diversity factor | Winter | EBRegional diversity factorWinter | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 | 0.8838 |  | Summer
EB | Load transfer capacity (MVA) | 1 | EBLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
EB | Load transfer capacity (MVA) | 2 | EBLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
EB | Load transfer capacity (MVA) | 3 | EBLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
EB | Load transfer capacity (MVA) | 4 | EBLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
EB | Load transfer capacity (MVA) | 5 | EBLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
EB | Embedded generation capacity (MVA) | Units less than 100 kVA | EBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.70338 | [12 empty] | Summer
EB | Embedded generation capacity (MVA) | Units greater than 100 kVA | EBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
EL | Substation capacity (winter and summer) (MVA) | Total | ELSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
EL | Substation capacity (winter and summer) (MVA) | Firm delivery | ELSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
EL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ELSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Summer
EL | Maximum demand forecast(peak season) | Maximum demand (MW) | ELMaximum demand forecast(peak season)Maximum demand (MW) | 16.2795 | 16.2392 | 16.2392 | 16.745 | 17.072 | 17.3823 | 17.4941 | 17.6308 | 17.8259 | 18.1823 | 19.0775 | 19.8892 |  | Summer
EL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.67422 | 0.67255 | 0.67255 | 0.6935 | 0.70704 | 0.71989 | 0.72452 | 0.73018 | 0.73826 | 0.75302 | 0.7901 | 0.82371 |  | Summer
EL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ELMaximum demand forecast(peak season)Maximum demand (MVA) | 16.2935 | 16.2531 | 16.2531 | 16.7594 | 17.0866 | 17.3972 | 17.5091 | 17.6459 | 17.8412 | 18.1978 | 19.0938 | 19.9062 |  | Summer
EL | Maximum demand forecast(peak season) | Power factor (coincident) | ELMaximum demand forecast(peak season)Power factor (coincident) | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 |  | Summer
EL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ELMaximum demand forecast(non-peak season)Maximum demand (MW) | 10.0645 | 12.3065 | 12.3065 | 12.494 | 12.9382 | 13.2493 | 13.3169 | 13.3876 | 13.4939 | 13.9232 | 14.8168 | 15.7112 |  | Summer
EL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.31576 | 0.38611 | 0.38611 | 0.39199 | 0.40593 | 0.41569 | 0.41781 | 0.42003 | 0.42336 | 0.43683 | 0.46486 | 0.49292 |  | Summer
EL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ELMaximum demand forecast(non-peak season)Maximum demand (MVA) | 10.0694 | 12.3126 | 12.3126 | 12.5001 | 12.9446 | 13.2558 | 13.3235 | 13.3942 | 13.5005 | 13.9301 | 14.8241 | 15.7189 |  | Summer
EL | Hours exceeding | 95% of maximum demand | ELHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
EL | Hours exceeding | Firm capacity (continuous rating) | ELHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
EL | Hours exceeding | Firm capacity (short-term rating) | ELHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
EL | Regional diversity factor | Summer | ELRegional diversity factorSummer | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 | 0.78257 |  | Summer
EL | Regional diversity factor | Winter | ELRegional diversity factorWinter | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 | 0.88141 |  | Summer
EL | Load transfer capacity (MVA) | 1 | ELLoad transfer capacity (MVA)1 | 8 | [11 empty] | Kingston | Summer
EL | Load transfer capacity (MVA) | 2 | ELLoad transfer capacity (MVA)2 | 3 | [11 empty] | Knights Road | Summer
EL | Load transfer capacity (MVA) | 3 | ELLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
EL | Load transfer capacity (MVA) | 4 | ELLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
EL | Load transfer capacity (MVA) | 5 | ELLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
EL | Embedded generation capacity (MVA) | Units less than 100 kVA | ELEmbedded generation capacity (MVA)Units less than 100 kVA | 8.7161 | [12 empty] | Summer
EL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ELEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1298 | [12 empty] | Summer
GT | Substation capacity (winter and summer) (MVA) | Total | GTSubstation capacity (winter and summer) (MVA)Total | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | Summer
GT | Substation capacity (winter and summer) (MVA) | Firm delivery | GTSubstation capacity (winter and summer) (MVA)Firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | Summer
GT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | Summer
GT | Maximum demand forecast(peak season) | Maximum demand (MW) | GTMaximum demand forecast(peak season)Maximum demand (MW) | 19.521 | 19.8227 | 21.9634 | 19.1986 | 19.5734 | 19.9293 | 20.0574 | 20.2141 | 20.4378 | 20.8464 | 21.8728 | 22.8034 |  | Summer
GT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.89553 | 0.90937 | 1.0076 | 0.88074 | 0.89794 | 0.91426 | 0.92014 | 0.92733 | 0.93759 | 0.95633 | 1.0034 | 1.0461 |  | Summer
GT | Maximum demand forecast(peak season) | Maximum demand (MVA) | GTMaximum demand forecast(peak season)Maximum demand (MVA) | 19.5416 | 19.8436 | 21.9865 | 19.2187 | 19.594 | 19.9502 | 20.0785 | 20.2354 | 20.4593 | 20.8683 | 21.8958 | 22.8274 |  | Summer
GT | Maximum demand forecast(peak season) | Power factor (coincident) | GTMaximum demand forecast(peak season)Power factor (coincident) | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 |  | Summer
GT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | GTMaximum demand forecast(non-peak season)Maximum demand (MW) | 12.9285 | 15.7389 | 18.1715 | 14.5895 | 15.1082 | 15.4715 | 15.5504 | 15.633 | 15.7571 | 16.2584 | 17.3018 | 18.3462 |  | Summer
GT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.6974 | 0.84901 | 0.98023 | 0.787 | 0.81498 | 0.83458 | 0.83884 | 0.84329 | 0.84999 | 0.87703 | 0.93332 | 0.98965 |  | Summer
GT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GTMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.9473 | 15.7618 | 18.1979 | 14.6107 | 15.1302 | 15.494 | 15.5731 | 15.6557 | 15.78 | 16.282 | 17.327 | 18.3729 |  | Summer
GT | Hours exceeding | 95% of maximum demand | GTHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Summer
GT | Hours exceeding | Firm capacity (continuous rating) | GTHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
GT | Hours exceeding | Firm capacity (short-term rating) | GTHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
GT | Regional diversity factor | Summer | GTRegional diversity factorSummer | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 | 0.91086 |  | Summer
GT | Regional diversity factor | Winter | GTRegional diversity factorWinter | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 | 0.77669 |  | Summer
GT | Load transfer capacity (MVA) | 1 | GTLoad transfer capacity (MVA)1 | 2.1 | [11 empty] | Mowbray | Summer
GT | Load transfer capacity (MVA) | 2 | GTLoad transfer capacity (MVA)2 | 2.1 | [11 empty] | Scottsdale | Summer
GT | Load transfer capacity (MVA) | 3 | GTLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn | Summer
GT | Load transfer capacity (MVA) | 4 | GTLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
GT | Load transfer capacity (MVA) | 5 | GTLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
GT | Embedded generation capacity (MVA) | Units less than 100 kVA | GTEmbedded generation capacity (MVA)Units less than 100 kVA | 7.5015 | [12 empty] | Summer
GT | Embedded generation capacity (MVA) | Units greater than 100 kVA | GTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.30292 | [12 empty] | Summer
HA | Substation capacity (winter and summer) (MVA) | Total | HASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
HA | Substation capacity (winter and summer) (MVA) | Firm delivery | HASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
HA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
HA | Maximum demand forecast(peak season) | Maximum demand (MW) | HAMaximum demand forecast(peak season)Maximum demand (MW) | 54.9227 | 55.2175 | 54.6823 | 57.0755 | 57.4865 | 58.5317 | 58.9081 | 59.3682 | 60.0254 | 61.2253 | 64.2398 | 66.973 |  | Summer
HA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.4376 | 2.4507 | 2.427 | 2.5332 | 2.5514 | 2.5978 | 2.6145 | 2.6349 | 2.6641 | 2.7174 | 2.8512 | 2.9725 |  | Summer
HA | Maximum demand forecast(peak season) | Maximum demand (MVA) | HAMaximum demand forecast(peak season)Maximum demand (MVA) | 54.9768 | 55.2719 | 54.7361 | 57.1316 | 57.5431 | 58.5893 | 58.9661 | 59.4267 | 60.0845 | 61.2855 | 64.303 | 67.0389 |  | Summer
HA | Maximum demand forecast(peak season) | Power factor (coincident) | HAMaximum demand forecast(peak season)Power factor (coincident) | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 |  | Summer
HA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HAMaximum demand forecast(non-peak season)Maximum demand (MW) | 40.369 | 37.9436 | 37.3354 | 38.6758 | 39.2517 | 40.1956 | 40.4007 | 40.615 | 40.9375 | 42.24 | 44.9508 | 47.6642 |  | Summer
HA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.103 | 1.9767 | 1.945 | 2.0148 | 2.0448 | 2.094 | 2.1047 | 2.1159 | 2.1327 | 2.2005 | 2.3417 | 2.4831 |  | Summer
HA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HAMaximum demand forecast(non-peak season)Maximum demand (MVA) | 40.4237 | 37.995 | 37.386 | 38.7283 | 39.3049 | 40.2501 | 40.4554 | 40.6701 | 40.993 | 42.2973 | 45.0118 | 47.7289 |  | Summer
HA | Hours exceeding | 95% of maximum demand | HAHours exceeding95% of maximum demand | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | Summer
HA | Hours exceeding | Firm capacity (continuous rating) | HAHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
HA | Hours exceeding | Firm capacity (short-term rating) | HAHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
HA | Regional diversity factor | Summer | HARegional diversity factorSummer | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 | 0.93747 |  | Summer
HA | Regional diversity factor | Winter | HARegional diversity factorWinter | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 | 0.93765 |  | Summer
HA | Load transfer capacity (MVA) | 1 | HALoad transfer capacity (MVA)1 | 13.4 | [11 empty] | Norwood | Summer
HA | Load transfer capacity (MVA) | 2 | HALoad transfer capacity (MVA)2 | 5.3 | [11 empty] | Palmerston | Summer
HA | Load transfer capacity (MVA) | 3 | HALoad transfer capacity (MVA)3 | 5.3 | [11 empty] | Railton | Summer
HA | Load transfer capacity (MVA) | 4 | HALoad transfer capacity (MVA)4 | 26.7 | [11 empty] | Trevallyn | Summer
HA | Load transfer capacity (MVA) | 5 | HALoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
HA | Embedded generation capacity (MVA) | Units less than 100 kVA | HAEmbedded generation capacity (MVA)Units less than 100 kVA | 15.1834 | [12 empty] | Summer
HA | Embedded generation capacity (MVA) | Units greater than 100 kVA | HAEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.0487 | [12 empty] | Summer
HR | Substation capacity (winter and summer) (MVA) | Total | HRSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
HR | Substation capacity (winter and summer) (MVA) | Firm delivery | HRSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
HR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
HR | Maximum demand forecast(peak season) | Maximum demand (MW) | HRMaximum demand forecast(peak season)Maximum demand (MW) | 0.51825 | 0.32497 | 0.32497 | 0.3351 | 0.34164 | 0.34785 | 0.35009 | 0.35282 | 0.35673 | 0.36386 | 0.38177 | 0.39802 |  | Summer
HR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.76348 | 0.47875 | 0.47875 | 0.49366 | 0.5033 | 0.51245 | 0.51575 | 0.51978 | 0.52553 | 0.53603 | 0.56243 | 0.58636 |  | Summer
HR | Maximum demand forecast(peak season) | Maximum demand (MVA) | HRMaximum demand forecast(peak season)Maximum demand (MVA) | 0.92276 | 0.57863 | 0.57863 | 0.59665 | 0.6083 | 0.61936 | 0.62334 | 0.62821 | 0.63517 | 0.64786 | 0.67976 | 0.70868 |  | Summer
HR | Maximum demand forecast(peak season) | Power factor (coincident) | HRMaximum demand forecast(peak season)Power factor (coincident) | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 | 0.56163 |  | Summer
HR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HRMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.31016 | 0.34943 | 0.34943 | 0.35475 | 0.36736 | 0.37619 | 0.37811 | 0.38012 | 0.38314 | 0.39533 | 0.4207 | 0.44609 |  | Summer
HR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.4596 | 0.51779 | 0.51779 | 0.52567 | 0.54436 | 0.55745 | 0.5603 | 0.56327 | 0.56774 | 0.58581 | 0.6234 | 0.66103 |  | Summer
HR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.55446 | 0.62466 | 0.62466 | 0.63418 | 0.65672 | 0.67252 | 0.67595 | 0.67953 | 0.68493 | 0.70672 | 0.75208 | 0.79748 |  | Summer
HR | Hours exceeding | 95% of maximum demand | HRHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | Summer
HR | Hours exceeding | Firm capacity (continuous rating) | HRHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
HR | Hours exceeding | Firm capacity (short-term rating) | HRHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
HR | Regional diversity factor | Summer | HRRegional diversity factorSummer | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 |  | Summer
HR | Regional diversity factor | Winter | HRRegional diversity factorWinter | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 | 0.81818 |  | Summer
HR | Load transfer capacity (MVA) | 1 | HRLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
HR | Load transfer capacity (MVA) | 2 | HRLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
HR | Load transfer capacity (MVA) | 3 | HRLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
HR | Load transfer capacity (MVA) | 4 | HRLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
HR | Load transfer capacity (MVA) | 5 | HRLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
HR | Embedded generation capacity (MVA) | Units less than 100 kVA | HREmbedded generation capacity (MVA)Units less than 100 kVA | 0.01525 | [12 empty] | Summer
HR | Embedded generation capacity (MVA) | Units greater than 100 kVA | HREmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
KE | Substation capacity (winter and summer) (MVA) | Total | KESubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Summer
KE | Substation capacity (winter and summer) (MVA) | Firm delivery | KESubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Summer
KE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Summer
KE | Maximum demand forecast(peak season) | Maximum demand (MW) | KEMaximum demand forecast(peak season)Maximum demand (MW) | 8.5752 | 8.426 | 8.426 | 8.6884 | 8.8581 | 9.0191 | 9.0771 | 9.148 | 9.2493 | 9.4342 | 9.8987 | 10.3198 |  | Summer
KE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.3919 | 1.3677 | 1.3677 | 1.4103 | 1.4378 | 1.4639 | 1.4734 | 1.4849 | 1.5013 | 1.5313 | 1.6067 | 1.6751 |  | Summer
KE | Maximum demand forecast(peak season) | Maximum demand (MVA) | KEMaximum demand forecast(peak season)Maximum demand (MVA) | 8.6874 | 8.5363 | 8.5363 | 8.8022 | 8.974 | 9.1372 | 9.1959 | 9.2678 | 9.3703 | 9.5576 | 10.0282 | 10.4549 |  | Summer
KE | Maximum demand forecast(peak season) | Power factor (coincident) | KEMaximum demand forecast(peak season)Power factor (coincident) | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 |  | Summer
KE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KEMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.1601 | 6.9838 | 6.9838 | 7.0901 | 7.3422 | 7.5188 | 7.5572 | 7.5973 | 7.6576 | 7.9012 | 8.4083 | 8.9158 |  | Summer
KE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.0488 | 1.189 | 1.189 | 1.2071 | 1.25 | 1.2801 | 1.2866 | 1.2934 | 1.3037 | 1.3452 | 1.4315 | 1.5179 |  | Summer
KE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.2488 | 7.0843 | 7.0843 | 7.1922 | 7.4479 | 7.627 | 7.6659 | 7.7066 | 7.7678 | 8.0149 | 8.5293 | 9.0441 |  | Summer
KE | Hours exceeding | 95% of maximum demand | KEHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
KE | Hours exceeding | Firm capacity (continuous rating) | KEHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
KE | Hours exceeding | Firm capacity (short-term rating) | KEHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
KE | Regional diversity factor | Summer | KERegional diversity factorSummer | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 | 0.86854 |  | Summer
KE | Regional diversity factor | Winter | KERegional diversity factorWinter | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 | 0.91347 |  | Summer
KE | Load transfer capacity (MVA) | 1 | KELoad transfer capacity (MVA)1 | 4.4 | [11 empty] | Knights Road | Summer
KE | Load transfer capacity (MVA) | 2 | KELoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
KE | Load transfer capacity (MVA) | 3 | KELoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
KE | Load transfer capacity (MVA) | 4 | KELoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
KE | Load transfer capacity (MVA) | 5 | KELoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
KE | Embedded generation capacity (MVA) | Units less than 100 kVA | KEEmbedded generation capacity (MVA)Units less than 100 kVA | 3.2869 | [12 empty] | Summer
KE | Embedded generation capacity (MVA) | Units greater than 100 kVA | KEEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
KI11 | Substation capacity (winter and summer) (MVA) | Total | KI11Substation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Summer
KI11 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI11Substation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Summer
KI11 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI11Substation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | Summer
KI11 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI11Maximum demand forecast(peak season)Maximum demand (MW) | 27.5345 | 27.6151 | 27.6151 | 28.4753 | 29.0312 | 29.559 | 29.7492 | 29.9815 | 30.3134 | 30.9193 | 32.4417 | 33.822 |  | Summer
KI11 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.55916 | 0.5608 | 0.5608 | 0.57826 | 0.58955 | 0.60027 | 0.60413 | 0.60885 | 0.61559 | 0.6279 | 0.65881 | 0.68684 |  | Summer
KI11 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(peak season)Maximum demand (MVA) | 27.5402 | 27.6208 | 27.6208 | 28.4811 | 29.0372 | 29.5651 | 29.7553 | 29.9877 | 30.3196 | 30.9257 | 32.4484 | 33.829 |  | Summer
KI11 | Maximum demand forecast(peak season) | Power factor (coincident) | KI11Maximum demand forecast(peak season)Power factor (coincident) | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 |  | Summer
KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI11Maximum demand forecast(non-peak season)Maximum demand (MW) | 16.227 | 19.3544 | 19.3544 | 19.6491 | 20.3478 | 20.8371 | 20.9434 | 21.0545 | 21.2217 | 21.8969 | 23.3022 | 24.7088 |  | Summer
KI11 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.39788 | 0.47456 | 0.47456 | 0.48179 | 0.49892 | 0.51092 | 0.51353 | 0.51625 | 0.52035 | 0.5369 | 0.57136 | 0.60585 |  | Summer
KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(non-peak season)Maximum demand (MVA) | 16.2318 | 19.3602 | 19.3602 | 19.655 | 20.3539 | 20.8433 | 20.9497 | 21.0608 | 21.228 | 21.9035 | 23.3092 | 24.7162 |  | Summer
KI11 | Hours exceeding | 95% of maximum demand | KI11Hours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
KI11 | Hours exceeding | Firm capacity (continuous rating) | KI11Hours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
KI11 | Hours exceeding | Firm capacity (short-term rating) | KI11Hours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
KI11 | Regional diversity factor | Summer | KI11Regional diversity factorSummer | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 | 0.7452 |  | Summer
KI11 | Regional diversity factor | Winter | KI11Regional diversity factorWinter | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 | 0.9059 |  | Summer
KI11 | Load transfer capacity (MVA) | 1 | KI11Load transfer capacity (MVA)1 | 7.8 | [11 empty] | Electrona | Summer
KI11 | Load transfer capacity (MVA) | 2 | KI11Load transfer capacity (MVA)2 | 3.1 | [11 empty] | Knights Road | Summer
KI11 | Load transfer capacity (MVA) | 3 | KI11Load transfer capacity (MVA)3 | 1.6 | [11 empty] | Sandy Bay | Summer
KI11 | Load transfer capacity (MVA) | 4 | KI11Load transfer capacity (MVA)4 | [12 empty] | 0 | Summer
KI11 | Load transfer capacity (MVA) | 5 | KI11Load transfer capacity (MVA)5 | [12 empty] | 0 | Summer
KI11 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI11Embedded generation capacity (MVA)Units less than 100 kVA | 9.0801 | [12 empty] | Summer
KI11 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI11Embedded generation capacity (MVA)Units greater than 100 kVA | 0.30004 | [12 empty] | Summer
KI33 | Substation capacity (winter and summer) (MVA) | Total | KI33Substation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
KI33 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI33Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
KI33 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI33Substation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
KI33 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI33Maximum demand forecast(peak season)Maximum demand (MW) | 11.0956 | 11.031 | 11.031 | 11.3746 | 11.5967 | 11.8075 | 11.8835 | 11.9763 | 12.1088 | 12.3509 | 12.959 | 13.5104 |  | Summer
KI33 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.82547 | 0.82067 | 0.82067 | 0.84623 | 0.86276 | 0.87844 | 0.88409 | 0.891 | 0.90086 | 0.91887 | 0.96411 | 1.0051 |  | Summer
KI33 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI33Maximum demand forecast(peak season)Maximum demand (MVA) | 11.1262 | 11.0615 | 11.0615 | 11.406 | 11.6287 | 11.8401 | 11.9163 | 12.0094 | 12.1423 | 12.385 | 12.9948 | 13.5477 |  | Summer
KI33 | Maximum demand forecast(peak season) | Power factor (coincident) | KI33Maximum demand forecast(peak season)Power factor (coincident) | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 | 0.99724 |  | Summer
KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI33Maximum demand forecast(non-peak season)Maximum demand (MW) | 5.6699 | 7.4359 | 7.4359 | 7.5492 | 7.8176 | 8.0056 | 8.0464 | 8.0891 | 8.1533 | 8.4128 | 8.9527 | 9.4931 |  | Summer
KI33 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.070526 | 0.092493 | 0.092493 | 0.093901 | 0.09724 | 0.099578 | 0.10009 | 0.10062 | 0.10142 | 0.10464 | 0.11136 | 0.11808 |  | Summer
KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 5.6704 | 7.4365 | 7.4365 | 7.5498 | 7.8182 | 8.0062 | 8.047 | 8.0897 | 8.154 | 8.4134 | 8.9534 | 9.4938 | 0 | Summer
KI33 | Hours exceeding | 95% of maximum demand | KI33Hours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
KI33 | Hours exceeding | Firm capacity (continuous rating) | KI33Hours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
KI33 | Hours exceeding | Firm capacity (short-term rating) | KI33Hours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
KI33 | Regional diversity factor | Summer | KI33Regional diversity factorSummer | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 | 0.85913 |  | Summer
KI33 | Regional diversity factor | Winter | KI33Regional diversity factorWinter | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 | 0.94338 |  | Summer
KI33 | Load transfer capacity (MVA) | 1 | KI33Load transfer capacity (MVA)1 | [12 empty] | 0 | Summer
KI33 | Load transfer capacity (MVA) | 2 | KI33Load transfer capacity (MVA)2 | [12 empty] | 0 | Summer
KI33 | Load transfer capacity (MVA) | 3 | KI33Load transfer capacity (MVA)3 | [12 empty] | 0 | Summer
KI33 | Load transfer capacity (MVA) | 4 | KI33Load transfer capacity (MVA)4 | [12 empty] | 0 | Summer
KI33 | Load transfer capacity (MVA) | 5 | KI33Load transfer capacity (MVA)5 | [12 empty] | 0 | Summer
KI33 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI33Embedded generation capacity (MVA)Units less than 100 kVA | 2.8651 | [12 empty] | Summer
KI33 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI33Embedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
KR | Substation capacity (winter and summer) (MVA) | Total | KRSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 |  | Summer
KR | Substation capacity (winter and summer) (MVA) | Firm delivery | KRSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 |  | Summer
KR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 30 | 30 | 30 | 30 | 30 |  | Summer
KR | Maximum demand forecast(peak season) | Maximum demand (MW) | KRMaximum demand forecast(peak season)Maximum demand (MW) | 19.8381 | 18.5852 | 19.4463 | 20.0521 | 20.4436 | 20.8153 | 20.9491 | 21.1128 | 21.3464 | 21.7732 | 22.8452 | 23.8172 |  | Summer
KR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.937 | 2.7515 | 2.879 | 2.9687 | 3.0267 | 3.0817 | 3.1015 | 3.1257 | 3.1603 | 3.2235 | 3.3822 | 3.5261 |  | Summer
KR | Maximum demand forecast(peak season) | Maximum demand (MVA) | KRMaximum demand forecast(peak season)Maximum demand (MVA) | 20.0543 | 18.7877 | 19.6583 | 20.2706 | 20.6664 | 21.0421 | 21.1775 | 21.3429 | 21.5791 | 22.0105 | 23.0942 | 24.0768 |  | Summer
KR | Maximum demand forecast(peak season) | Power factor (coincident) | KRMaximum demand forecast(peak season)Power factor (coincident) | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 |  | Summer
KR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KRMaximum demand forecast(non-peak season)Maximum demand (MW) | 14.8539 | 15.2134 | 16.1904 | 16.437 | 17.0214 | 17.4307 | 17.5197 | 17.6127 | 17.7525 | 18.3173 | 19.4929 | 20.6695 |  | Summer
KR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.3929 | 2.4508 | 2.6083 | 2.648 | 2.7421 | 2.8081 | 2.8224 | 2.8374 | 2.8599 | 2.9509 | 3.1403 | 3.3298 |  | Summer
KR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 15.0454 | 15.4095 | 16.3992 | 16.6489 | 17.2409 | 17.6555 | 17.7456 | 17.8397 | 17.9814 | 18.5535 | 19.7442 | 20.936 | 0 | Summer
KR | Hours exceeding | 95% of maximum demand | KRHours exceeding95% of maximum demand | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Summer
KR | Hours exceeding | Firm capacity (continuous rating) | KRHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
KR | Hours exceeding | Firm capacity (short-term rating) | KRHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
KR | Regional diversity factor | Summer | KRRegional diversity factorSummer | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 | 0.90798 |  | Summer
KR | Regional diversity factor | Winter | KRRegional diversity factorWinter | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 | 0.96199 |  | Summer
KR | Load transfer capacity (MVA) | 1 | KRLoad transfer capacity (MVA)1 | 1.7 | [11 empty] | Electrona | Summer
KR | Load transfer capacity (MVA) | 2 | KRLoad transfer capacity (MVA)2 | 3.4 | [11 empty] | Kermandie | Summer
KR | Load transfer capacity (MVA) | 3 | KRLoad transfer capacity (MVA)3 | 1.7 | [11 empty] | Kingston | Summer
KR | Load transfer capacity (MVA) | 4 | KRLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
KR | Load transfer capacity (MVA) | 5 | KRLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
KR | Embedded generation capacity (MVA) | Units less than 100 kVA | KREmbedded generation capacity (MVA)Units less than 100 kVA | 6.9122 | [12 empty] | Summer
KR | Embedded generation capacity (MVA) | Units greater than 100 kVA | KREmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1992 | [12 empty] | Summer
LF | Substation capacity (winter and summer) (MVA) | Total | LFSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
LF | Substation capacity (winter and summer) (MVA) | Firm delivery | LFSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
LF | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | LFSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | Summer
LF | Maximum demand forecast(peak season) | Maximum demand (MW) | LFMaximum demand forecast(peak season)Maximum demand (MW) | 35.6832 | 36.1128 | 36.1128 | 37.2377 | 37.9647 | 38.6549 | 38.9035 | 39.2074 | 39.6414 | 40.4338 | 42.4246 | 44.2297 |  | Summer
LF | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.3326 | 2.3606 | 2.3606 | 2.4342 | 2.4817 | 2.5268 | 2.5431 | 2.5629 | 2.5913 | 2.6431 | 2.7732 | 2.8912 |  | Summer
LF | Maximum demand forecast(peak season) | Maximum demand (MVA) | LFMaximum demand forecast(peak season)Maximum demand (MVA) | 35.7593 | 36.1898 | 36.1898 | 37.3171 | 38.0457 | 38.7374 | 38.9866 | 39.2911 | 39.726 | 40.5201 | 42.5152 | 44.3241 |  | Summer
LF | Maximum demand forecast(peak season) | Power factor (coincident) | LFMaximum demand forecast(peak season)Power factor (coincident) | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 |  | Summer
LF | Maximum demand forecast(non-peak season) | Maximum demand (MW) | LFMaximum demand forecast(non-peak season)Maximum demand (MW) | 20.1035 | 25.6919 | 25.6919 | 26.0832 | 27.0106 | 27.6601 | 27.8013 | 27.9488 | 28.1707 | 29.067 | 30.9324 | 32.7996 |  | Summer
LF | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.032764 | 0.041872 | 0.041872 | 0.042509 | 0.044021 | 0.045079 | 0.045309 | 0.04555 | 0.045912 | 0.047372 | 0.050413 | 0.053456 |  | Summer
LF | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 20.1035 | 25.692 | 25.692 | 26.0833 | 27.0106 | 27.6602 | 27.8013 | 27.9488 | 28.1707 | 29.067 | 30.9325 | 32.7997 | 0 | Summer
LF | Hours exceeding | 95% of maximum demand | LFHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
LF | Hours exceeding | Firm capacity (continuous rating) | LFHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
LF | Hours exceeding | Firm capacity (short-term rating) | LFHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
LF | Regional diversity factor | Summer | LFRegional diversity factorSummer | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 | 0.81658 |  | Summer
LF | Regional diversity factor | Winter | LFRegional diversity factorWinter | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 | 0.92622 |  | Summer
LF | Load transfer capacity (MVA) | 1 | LFLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
LF | Load transfer capacity (MVA) | 2 | LFLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
LF | Load transfer capacity (MVA) | 3 | LFLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
LF | Load transfer capacity (MVA) | 4 | LFLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
LF | Load transfer capacity (MVA) | 5 | LFLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
LF | Embedded generation capacity (MVA) | Units less than 100 kVA | LFEmbedded generation capacity (MVA)Units less than 100 kVA | 5.6014 | [12 empty] | Summer
LF | Embedded generation capacity (MVA) | Units greater than 100 kVA | LFEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
MB | Substation capacity (winter and summer) (MVA) | Total | MBSubstation capacity (winter and summer) (MVA)Total | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Winter
MB | Substation capacity (winter and summer) (MVA) | Firm delivery | MBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
MB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Winter
MB | Maximum demand forecast(peak season) | Maximum demand (MW) | MBMaximum demand forecast(peak season)Maximum demand (MW) | 7.9647 | 8.1088 | 8.1088 | 8.2323 | 8.525 | 8.73 | 8.7746 | 8.8211 | 8.8911 | 9.174 | 9.7628 | 10.3521 |  | Winter
MB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.3513 | 2.3938 | 2.3938 | 2.4303 | 2.5167 | 2.5772 | 2.5904 | 2.6041 | 2.6248 | 2.7083 | 2.8821 | 3.0561 |  | Winter
MB | Maximum demand forecast(peak season) | Maximum demand (MVA) | MBMaximum demand forecast(peak season)Maximum demand (MVA) | 8.3046 | 8.4548 | 8.4548 | 8.5835 | 8.8887 | 9.1025 | 9.1489 | 9.1975 | 9.2705 | 9.5654 | 10.1793 | 10.7938 |  | Winter
MB | Maximum demand forecast(peak season) | Power factor (coincident) | MBMaximum demand forecast(peak season)Power factor (coincident) | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 | 0.95908 |  | Winter
MB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MBMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.6221 | 5.236 | 5.236 | 5.399 | 5.5045 | 5.6045 | 5.6406 | 5.6846 | 5.7476 | 5.8625 | 6.1511 | 6.4128 |  | Winter
MB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.0002 | 0.00022656 | 0.00022656 | 0.00023361 | 0.00023818 | 0.00024251 | 0.00024407 | 0.00024597 | 0.00024869 | 0.00025367 | 0.00026615 | 0.00027748 |  | Winter
MB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.6221 | 5.236 | 5.236 | 5.399 | 5.5045 | 5.6045 | 5.6406 | 5.6846 | 5.7476 | 5.8625 | 6.1511 | 6.4128 | 0 | Winter
MB | Hours exceeding | 95% of maximum demand | MBHours exceeding95% of maximum demand | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 |  | Winter
MB | Hours exceeding | Firm capacity (continuous rating) | MBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
MB | Hours exceeding | Firm capacity (short-term rating) | MBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Winter
MB | Regional diversity factor | Summer | MBRegional diversity factorSummer | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 | 0.71486 |  | Winter
MB | Regional diversity factor | Winter | MBRegional diversity factorWinter | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 | 0.69937 |  | Winter
MB | Load transfer capacity (MVA) | 1 | MBLoad transfer capacity (MVA)1 | 2.3 | [11 empty] | New Norfolk | Winter
MB | Load transfer capacity (MVA) | 2 | MBLoad transfer capacity (MVA)2 | 1.3 | [11 empty] | Wayatinah | Winter
MB | Load transfer capacity (MVA) | 3 | MBLoad transfer capacity (MVA)3 | 1.8 | [11 empty] | Sorell | Winter
MB | Load transfer capacity (MVA) | 4 | MBLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
MB | Load transfer capacity (MVA) | 5 | MBLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
MB | Embedded generation capacity (MVA) | Units less than 100 kVA | MBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.91829 | [12 empty] | Winter
MB | Embedded generation capacity (MVA) | Units greater than 100 kVA | MBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.2 | [12 empty] | Winter
MT | Substation capacity (winter and summer) (MVA) | Total | MTSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
MT | Substation capacity (winter and summer) (MVA) | Firm delivery | MTSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
MT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | Summer
MT | Maximum demand forecast(peak season) | Maximum demand (MW) | MTMaximum demand forecast(peak season)Maximum demand (MW) | 38.7073 | 41.0852 | 41.0852 | 42.3649 | 43.1921 | 43.9774 | 44.2602 | 44.6059 | 45.0996 | 46.0012 | 48.2661 | 50.3197 |  | Summer
MT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.094 | 2.2226 | 2.2226 | 2.2919 | 2.3366 | 2.3791 | 2.3944 | 2.4131 | 2.4398 | 2.4886 | 2.6111 | 2.7222 |  | Summer
MT | Maximum demand forecast(peak season) | Maximum demand (MVA) | MTMaximum demand forecast(peak season)Maximum demand (MVA) | 38.7639 | 41.1453 | 41.1453 | 42.4269 | 43.2553 | 44.0417 | 44.3249 | 44.6711 | 45.1656 | 46.0684 | 48.3367 | 50.3933 |  | Summer
MT | Maximum demand forecast(peak season) | Power factor (coincident) | MTMaximum demand forecast(peak season)Power factor (coincident) | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 |  | Summer
MT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MTMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.6269 | 29.0733 | 29.0733 | 29.5161 | 30.5656 | 31.3006 | 31.4603 | 31.6272 | 31.8783 | 32.8926 | 35.0036 | 37.1165 |  | Summer
MT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.42649 | 0.548 | 0.548 | 0.55634 | 0.57612 | 0.58998 | 0.59299 | 0.59613 | 0.60087 | 0.61998 | 0.65977 | 0.6996 |  | Summer
MT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.6309 | 29.0785 | 29.0785 | 29.5214 | 30.571 | 31.3061 | 31.4659 | 31.6329 | 31.884 | 32.8984 | 35.0098 | 37.1231 | 0 | Summer
MT | Hours exceeding | 95% of maximum demand | MTHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Summer
MT | Hours exceeding | Firm capacity (continuous rating) | MTHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
MT | Hours exceeding | Firm capacity (short-term rating) | MTHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
MT | Regional diversity factor | Summer | MTRegional diversity factorSummer | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 |  | Summer
MT | Regional diversity factor | Winter | MTRegional diversity factorWinter | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 | 0.94757 |  | Summer
MT | Load transfer capacity (MVA) | 1 | MTLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
MT | Load transfer capacity (MVA) | 2 | MTLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
MT | Load transfer capacity (MVA) | 3 | MTLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
MT | Load transfer capacity (MVA) | 4 | MTLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
MT | Load transfer capacity (MVA) | 5 | MTLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
MT | Embedded generation capacity (MVA) | Units less than 100 kVA | MTEmbedded generation capacity (MVA)Units less than 100 kVA | 11.4925 | [12 empty] | Summer
MT | Embedded generation capacity (MVA) | Units greater than 100 kVA | MTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
MY | Substation capacity (winter and summer) (MVA) | Total | MYSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
MY | Substation capacity (winter and summer) (MVA) | Firm delivery | MYSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
MY | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MYSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
MY | Maximum demand forecast(peak season) | Maximum demand (MW) | MYMaximum demand forecast(peak season)Maximum demand (MW) | 38.5042 | 35.1901 | 35.7228 | 36.2862 | 36.9947 | 37.6673 | 37.9095 | 38.2056 | 38.6285 | 39.4007 | 41.3406 | 43.0996 |  | Summer
MY | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 4.0911 | 3.739 | 3.7956 | 3.8555 | 3.9307 | 4.0022 | 4.0279 | 4.0594 | 4.1043 | 4.1864 | 4.3925 | 4.5794 |  | Summer
MY | Maximum demand forecast(peak season) | Maximum demand (MVA) | MYMaximum demand forecast(peak season)Maximum demand (MVA) | 38.721 | 35.3881 | 35.9239 | 36.4904 | 37.2029 | 37.8793 | 38.1229 | 38.4207 | 38.8459 | 39.6225 | 41.5733 | 43.3422 |  | Summer
MY | Maximum demand forecast(peak season) | Power factor (coincident) | MYMaximum demand forecast(peak season)Power factor (coincident) | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 |  | Summer
MY | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MYMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.3718 | 22.0472 | 22.6553 | 22.383 | 23.1788 | 23.7362 | 23.8573 | 23.9839 | 24.1743 | 24.9434 | 26.5442 | 28.1465 |  | Summer
MY | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.2418 | 1.2238 | 1.2575 | 1.2424 | 1.2866 | 1.3175 | 1.3243 | 1.3313 | 1.3419 | 1.3846 | 1.4734 | 1.5624 |  | Summer
MY | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.4062 | 22.0811 | 22.6902 | 22.4174 | 23.2145 | 23.7727 | 23.894 | 24.0208 | 24.2115 | 24.9818 | 26.5851 | 28.1899 | 0 | Summer
MY | Hours exceeding | 95% of maximum demand | MYHours exceeding95% of maximum demand | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | Summer
MY | Hours exceeding | Firm capacity (continuous rating) | MYHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
MY | Hours exceeding | Firm capacity (short-term rating) | MYHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
MY | Regional diversity factor | Summer | MYRegional diversity factorSummer | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 | 0.73585 |  | Summer
MY | Regional diversity factor | Winter | MYRegional diversity factorWinter | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 | 0.93917 |  | Summer
MY | Load transfer capacity (MVA) | 1 | MYLoad transfer capacity (MVA)1 | 6.3 | [11 empty] | Norwood | Summer
MY | Load transfer capacity (MVA) | 2 | MYLoad transfer capacity (MVA)2 | 31.4 | [11 empty] | Trevallyn | Summer
MY | Load transfer capacity (MVA) | 3 | MYLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
MY | Load transfer capacity (MVA) | 4 | MYLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
MY | Load transfer capacity (MVA) | 5 | MYLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
MY | Embedded generation capacity (MVA) | Units less than 100 kVA | MYEmbedded generation capacity (MVA)Units less than 100 kVA | 6.4748 | [12 empty] | Summer
MY | Embedded generation capacity (MVA) | Units greater than 100 kVA | MYEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.2 | [12 empty] | Summer
NH | Substation capacity (winter and summer) (MVA) | Total | NHSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Summer
NH | Substation capacity (winter and summer) (MVA) | Firm delivery | NHSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Summer
NH | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NHSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
NH | Maximum demand forecast(peak season) | Maximum demand (MW) | NHMaximum demand forecast(peak season)Maximum demand (MW) | 35.5429 | 34.7085 | 34.7085 | 35.7896 | 36.4884 | 37.1518 | 37.3907 | 37.6828 | 38.0999 | 38.8615 | 40.7749 | 42.5097 |  | Summer
NH | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.4281 | 2.3711 | 2.3711 | 2.445 | 2.4927 | 2.538 | 2.5544 | 2.5743 | 2.6028 | 2.6548 | 2.7855 | 2.9041 |  | Summer
NH | Maximum demand forecast(peak season) | Maximum demand (MVA) | NHMaximum demand forecast(peak season)Maximum demand (MVA) | 35.6257 | 34.7894 | 34.7894 | 35.873 | 36.5734 | 37.2384 | 37.4779 | 37.7706 | 38.1887 | 38.952 | 40.8699 | 42.6088 |  | Summer
NH | Maximum demand forecast(peak season) | Power factor (coincident) | NHMaximum demand forecast(peak season)Power factor (coincident) | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 | 0.99767 |  | Summer
NH | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NHMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.9138 | 25.0633 | 25.0633 | 25.445 | 26.3497 | 26.9834 | 27.121 | 27.265 | 27.4814 | 28.3558 | 30.1756 | 31.9971 |  | Summer
NH | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.018 | 1.2812 | 1.2812 | 1.3007 | 1.347 | 1.3794 | 1.3864 | 1.3938 | 1.4048 | 1.4495 | 1.5426 | 1.6357 |  | Summer
NH | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 19.9398 | 25.096 | 25.096 | 25.4782 | 26.3841 | 27.0186 | 27.1564 | 27.3006 | 27.5173 | 28.3928 | 30.215 | 32.0389 | 0 | Summer
NH | Hours exceeding | 95% of maximum demand | NHHours exceeding95% of maximum demand | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 |  | Summer
NH | Hours exceeding | Firm capacity (continuous rating) | NHHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
NH | Hours exceeding | Firm capacity (short-term rating) | NHHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
NH | Regional diversity factor | Summer | NHRegional diversity factorSummer | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 | 0.82122 |  | Summer
NH | Regional diversity factor | Winter | NHRegional diversity factorWinter | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 | 0.94864 |  | Summer
NH | Load transfer capacity (MVA) | 1 | NHLoad transfer capacity (MVA)1 | 9.8 | [11 empty] | Chapel Street | Summer
NH | Load transfer capacity (MVA) | 2 | NHLoad transfer capacity (MVA)2 | 14.6 | [11 empty] | East Hobart | Summer
NH | Load transfer capacity (MVA) | 3 | NHLoad transfer capacity (MVA)3 | 9.8 | [11 empty] | New Town | Summer
NH | Load transfer capacity (MVA) | 4 | NHLoad transfer capacity (MVA)4 | 14.6 | [11 empty] | West Hobart | Summer
NH | Load transfer capacity (MVA) | 5 | NHLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
NH | Embedded generation capacity (MVA) | Units less than 100 kVA | NHEmbedded generation capacity (MVA)Units less than 100 kVA | 5.5279 | [12 empty] | Summer
NH | Embedded generation capacity (MVA) | Units greater than 100 kVA | NHEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
NN | Substation capacity (winter and summer) (MVA) | Total | NNSubstation capacity (winter and summer) (MVA)Total | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Winter
NN | Substation capacity (winter and summer) (MVA) | Firm delivery | NNSubstation capacity (winter and summer) (MVA)Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Winter
NN | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NNSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Winter
NN | Maximum demand forecast(peak season) | Maximum demand (MW) | NNMaximum demand forecast(peak season)Maximum demand (MW) | 14.8206 | 13.6379 | 13.6379 | 13.8456 | 14.3378 | 14.6826 | 14.7575 | 14.8359 | 14.9536 | 15.4294 | 16.4196 | 17.4108 |  | Winter
NN | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.9627 | 1.8061 | 1.8061 | 1.8336 | 1.8988 | 1.9444 | 1.9543 | 1.9647 | 1.9803 | 2.0433 | 2.1745 | 2.3057 |  | Winter
NN | Maximum demand forecast(peak season) | Maximum demand (MVA) | NNMaximum demand forecast(peak season)Maximum demand (MVA) | 14.95 | 13.7569 | 13.7569 | 13.9665 | 14.463 | 14.8108 | 14.8864 | 14.9654 | 15.0842 | 15.5641 | 16.563 | 17.5628 |  | Winter
NN | Maximum demand forecast(peak season) | Power factor (coincident) | NNMaximum demand forecast(peak season)Power factor (coincident) | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 | 0.99134 |  | Winter
NN | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NNMaximum demand forecast(non-peak season)Maximum demand (MW) | 20.7865 | 18.0781 | 18.0781 | 18.6413 | 19.0052 | 19.3508 | 19.4752 | 19.6273 | 19.8446 | 20.2413 | 21.2379 | 22.1415 |  | Winter
NN | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.6773 | 1.4588 | 1.4588 | 1.5042 | 1.5336 | 1.5615 | 1.5715 | 1.5838 | 1.6013 | 1.6333 | 1.7137 | 1.7867 |  | Winter
NN | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 20.854 | 18.1369 | 18.1369 | 18.7019 | 19.067 | 19.4137 | 19.5385 | 19.6911 | 19.9091 | 20.3071 | 21.3069 | 22.2135 | 0 | Winter
NN | Hours exceeding | 95% of maximum demand | NNHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Winter
NN | Hours exceeding | Firm capacity (continuous rating) | NNHours exceedingFirm capacity (continuous rating) | [13 empty] | Winter
NN | Hours exceeding | Firm capacity (short-term rating) | NNHours exceedingFirm capacity (short-term rating) | [13 empty] | Winter
NN | Regional diversity factor | Summer | NNRegional diversity factorSummer | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 | 0.89365 |  | Winter
NN | Regional diversity factor | Winter | NNRegional diversity factorWinter | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 | 0.85865 |  | Winter
NN | Load transfer capacity (MVA) | 1 | NNLoad transfer capacity (MVA)1 | 6.6 | [11 empty] | Meadowbank | Winter
NN | Load transfer capacity (MVA) | 2 | NNLoad transfer capacity (MVA)2 | [12 empty] | 0 | Winter
NN | Load transfer capacity (MVA) | 3 | NNLoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
NN | Load transfer capacity (MVA) | 4 | NNLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
NN | Load transfer capacity (MVA) | 5 | NNLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
NN | Embedded generation capacity (MVA) | Units less than 100 kVA | NNEmbedded generation capacity (MVA)Units less than 100 kVA | 4.4486 | [12 empty] | Winter
NN | Embedded generation capacity (MVA) | Units greater than 100 kVA | NNEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.56 | [12 empty] | Winter
NT | Substation capacity (winter and summer) (MVA) | Total | NTSubstation capacity (winter and summer) (MVA)Total | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 |  | Summer
NT | Substation capacity (winter and summer) (MVA) | Firm delivery | NTSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
NT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
NT | Maximum demand forecast(peak season) | Maximum demand (MW) | NTMaximum demand forecast(peak season)Maximum demand (MW) | 3.8811 | 3.9404 | 3.9404 | 4.0632 | 4.1425 | 4.2178 | 4.245 | 4.2781 | 4.3255 | 4.4119 | 4.6292 | 4.8261 |  | Summer
NT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.053453 | 0.054271 | 0.054271 | 0.055961 | 0.057054 | 0.058091 | 0.058465 | 0.058921 | 0.059573 | 0.060764 | 0.063756 | 0.066469 |  | Summer
NT | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTMaximum demand forecast(peak season)Maximum demand (MVA) | 3.8815 | 3.9408 | 3.9408 | 4.0636 | 4.1429 | 4.2182 | 4.2454 | 4.2785 | 4.3259 | 4.4124 | 4.6296 | 4.8266 |  | Summer
NT | Maximum demand forecast(peak season) | Power factor (coincident) | NTMaximum demand forecast(peak season)Power factor (coincident) | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 |  | Summer
NT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NTMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.0466 | 4.3952 | 4.3952 | 4.4621 | 4.6208 | 4.7319 | 4.756 | 4.7813 | 4.8192 | 4.9726 | 5.2917 | 5.6111 |  | Summer
NT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.071224 | 0.077359 | 0.077359 | 0.078537 | 0.08133 | 0.083286 | 0.083711 | 0.084155 | 0.084823 | 0.087522 | 0.093139 | 0.098761 |  | Summer
NT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.0472 | 4.3959 | 4.3959 | 4.4628 | 4.6215 | 4.7326 | 4.7568 | 4.782 | 4.82 | 4.9733 | 5.2925 | 5.612 | 0 | Summer
NT | Hours exceeding | 95% of maximum demand | NTHours exceeding95% of maximum demand | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Summer
NT | Hours exceeding | Firm capacity (continuous rating) | NTHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
NT | Hours exceeding | Firm capacity (short-term rating) | NTHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
NT | Regional diversity factor | Summer | NTRegional diversity factorSummer | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 | 0.89037 |  | Summer
NT | Regional diversity factor | Winter | NTRegional diversity factorWinter | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 | 0.875 |  | Summer
NT | Load transfer capacity (MVA) | 1 | NTLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
NT | Load transfer capacity (MVA) | 2 | NTLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
NT | Load transfer capacity (MVA) | 3 | NTLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
NT | Load transfer capacity (MVA) | 4 | NTLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
NT | Load transfer capacity (MVA) | 5 | NTLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
NT | Embedded generation capacity (MVA) | Units less than 100 kVA | NTEmbedded generation capacity (MVA)Units less than 100 kVA | 0 | [12 empty] | Summer
NT | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
NW | Substation capacity (winter and summer) (MVA) | Total | NWSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
NW | Substation capacity (winter and summer) (MVA) | Firm delivery | NWSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
NW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
NW | Maximum demand forecast(peak season) | Maximum demand (MW) | NWMaximum demand forecast(peak season)Maximum demand (MW) | 29.3918 | 28.5082 | 28.5082 | 29.3962 | 29.9702 | 30.5151 | 30.7113 | 30.9512 | 31.2938 | 31.9193 | 33.4909 | 34.9159 |  | Summer
NW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.49709 | 0.48215 | 0.48215 | 0.49716 | 0.50687 | 0.51609 | 0.51941 | 0.52346 | 0.52926 | 0.53984 | 0.56642 | 0.59052 |  | Summer
NW | Maximum demand forecast(peak season) | Maximum demand (MVA) | NWMaximum demand forecast(peak season)Maximum demand (MVA) | 29.396 | 28.5123 | 28.5123 | 29.4004 | 29.9745 | 30.5194 | 30.7157 | 30.9556 | 31.2983 | 31.9239 | 33.4957 | 34.9209 |  | Summer
NW | Maximum demand forecast(peak season) | Power factor (coincident) | NWMaximum demand forecast(peak season)Power factor (coincident) | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 |  | Summer
NW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NWMaximum demand forecast(non-peak season)Maximum demand (MW) | 16.7139 | 18.4642 | 18.4642 | 18.7454 | 19.4118 | 19.8786 | 19.9801 | 20.0861 | 20.2456 | 20.8897 | 22.2304 | 23.5723 |  | Summer
NW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.23142 | 0.25565 | 0.25565 | 0.25954 | 0.26877 | 0.27523 | 0.27664 | 0.27811 | 0.28031 | 0.28923 | 0.3078 | 0.32638 |  | Summer
NW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 16.7155 | 18.4659 | 18.4659 | 18.7472 | 19.4137 | 19.8806 | 19.982 | 20.088 | 20.2475 | 20.8917 | 22.2325 | 23.5745 | 0 | Summer
NW | Hours exceeding | 95% of maximum demand | NWHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Summer
NW | Hours exceeding | Firm capacity (continuous rating) | NWHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
NW | Hours exceeding | Firm capacity (short-term rating) | NWHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
NW | Regional diversity factor | Summer | NWRegional diversity factorSummer | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 | 0.87602 |  | Summer
NW | Regional diversity factor | Winter | NWRegional diversity factorWinter | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 | 0.90014 |  | Summer
NW | Load transfer capacity (MVA) | 1 | NWLoad transfer capacity (MVA)1 | 16.2 | [11 empty] | Hadspen | Summer
NW | Load transfer capacity (MVA) | 2 | NWLoad transfer capacity (MVA)2 | 10.8 | [11 empty] | Mowbray | Summer
NW | Load transfer capacity (MVA) | 3 | NWLoad transfer capacity (MVA)3 | 27 | [11 empty] | St Leonards | Summer
NW | Load transfer capacity (MVA) | 4 | NWLoad transfer capacity (MVA)4 | 16.2 | [11 empty] | Trevallyn | Summer
NW | Load transfer capacity (MVA) | 5 | NWLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
NW | Embedded generation capacity (MVA) | Units less than 100 kVA | NWEmbedded generation capacity (MVA)Units less than 100 kVA | 7.5109 | [12 empty] | Summer
NW | Embedded generation capacity (MVA) | Units greater than 100 kVA | NWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.58708 | [12 empty] | Summer
PL | Substation capacity (winter and summer) (MVA) | Total | PLSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 |  | Winter
PL | Substation capacity (winter and summer) (MVA) | Firm delivery | PLSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25 | 25 | 25 | 25 |  | Winter
PL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Winter
PL | Maximum demand forecast(peak season) | Maximum demand (MW) | PLMaximum demand forecast(peak season)Maximum demand (MW) | 21.2003 | 11.0175 | 11.7308 | 11.1853 | 11.583 | 11.8615 | 11.9221 | 11.9853 | 12.0805 | 12.4648 | 13.2648 | 14.0655 |  | Winter
PL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 7.9032 | 4.1072 | 4.3731 | 4.1697 | 4.318 | 4.4218 | 4.4444 | 4.4679 | 4.5034 | 4.6467 | 4.9449 | 5.2434 |  | Winter
PL | Maximum demand forecast(peak season) | Maximum demand (MVA) | PLMaximum demand forecast(peak season)Maximum demand (MVA) | 22.6255 | 11.7582 | 12.5195 | 11.9372 | 12.3617 | 12.6589 | 12.7235 | 12.791 | 12.8926 | 13.3028 | 14.1565 | 15.0111 |  | Winter
PL | Maximum demand forecast(peak season) | Power factor (coincident) | PLMaximum demand forecast(peak season)Power factor (coincident) | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 | 0.93701 |  | Winter
PL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PLMaximum demand forecast(non-peak season)Maximum demand (MW) | 21.3835 | 6.7575 | 7.4265 | 6.968 | 7.1041 | 7.2332 | 7.2797 | 7.3366 | 7.4178 | 7.5661 | 7.9386 | 8.2764 |  | Winter
PL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.97112 | 0.30689 | 0.33727 | 0.31645 | 0.32263 | 0.32849 | 0.3306 | 0.33319 | 0.33687 | 0.34361 | 0.36053 | 0.37587 |  | Winter
PL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 21.4055 | 6.7645 | 7.4341 | 6.9752 | 7.1114 | 7.2407 | 7.2872 | 7.3442 | 7.4255 | 7.5739 | 7.9468 | 8.2849 | 0 | Winter
PL | Hours exceeding | 95% of maximum demand | PLHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 |  | Winter
PL | Hours exceeding | Firm capacity (continuous rating) | PLHours exceedingFirm capacity (continuous rating) | [13 empty] | Winter
PL | Hours exceeding | Firm capacity (short-term rating) | PLHours exceedingFirm capacity (short-term rating) | [13 empty] | Winter
PL | Regional diversity factor | Summer | PLRegional diversity factorSummer | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 | 0.6205 |  | Winter
PL | Regional diversity factor | Winter | PLRegional diversity factorWinter | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 | 0.86096 |  | Winter
PL | Load transfer capacity (MVA) | 1 | PLLoad transfer capacity (MVA)1 | 3.9 | [11 empty] | Burnie | Winter
PL | Load transfer capacity (MVA) | 2 | PLLoad transfer capacity (MVA)2 | 3.9 | [11 empty] | Smithton | Winter
PL | Load transfer capacity (MVA) | 3 | PLLoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
PL | Load transfer capacity (MVA) | 4 | PLLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
PL | Load transfer capacity (MVA) | 5 | PLLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
PL | Embedded generation capacity (MVA) | Units less than 100 kVA | PLEmbedded generation capacity (MVA)Units less than 100 kVA | 2.3477 | [12 empty] | Winter
PL | Embedded generation capacity (MVA) | Units greater than 100 kVA | PLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.45 | [12 empty] | Winter
PM | Substation capacity (winter and summer) (MVA) | Total | PMSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
PM | Substation capacity (winter and summer) (MVA) | Firm delivery | PMSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
PM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Winter
PM | Maximum demand forecast(peak season) | Maximum demand (MW) | PMMaximum demand forecast(peak season)Maximum demand (MW) | 14.3014 | 13.4968 | 13.7136 | 12.4553 | 12.8981 | 13.2083 | 13.2757 | 13.3461 | 13.4521 | 13.8801 | 14.7709 | 15.6625 |  | Winter
PM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 4.743 | 4.4762 | 4.5481 | 4.1307 | 4.2776 | 4.3805 | 4.4028 | 4.4262 | 4.4613 | 4.6033 | 4.8987 | 5.1944 |  | Winter
PM | Maximum demand forecast(peak season) | Maximum demand (MVA) | PMMaximum demand forecast(peak season)Maximum demand (MVA) | 15.0674 | 14.2197 | 14.4481 | 13.1224 | 13.589 | 13.9157 | 13.9867 | 14.061 | 14.1726 | 14.6235 | 15.562 | 16.5014 |  | Winter
PM | Maximum demand forecast(peak season) | Power factor (coincident) | PMMaximum demand forecast(peak season)Power factor (coincident) | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 | 0.94916 |  | Winter
PM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PMMaximum demand forecast(non-peak season)Maximum demand (MW) | 7.0803 | 10.1103 | 10.3083 | 9.2686 | 9.4495 | 9.6214 | 9.6832 | 9.7589 | 9.8669 | 10.0641 | 10.5596 | 11.0089 |  | Winter
PM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.2254 | 1.7498 | 1.7841 | 1.6041 | 1.6355 | 1.6652 | 1.6759 | 1.689 | 1.7077 | 1.7418 | 1.8276 | 1.9053 |  | Winter
PM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 7.1856 | 10.2606 | 10.4615 | 9.4064 | 9.59 | 9.7644 | 9.8272 | 9.9039 | 10.0136 | 10.2137 | 10.7166 | 11.1726 | 0 | Winter
PM | Hours exceeding | 95% of maximum demand | PMHours exceeding95% of maximum demand | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | Winter
PM | Hours exceeding | Firm capacity (continuous rating) | PMHours exceedingFirm capacity (continuous rating) | [13 empty] | Winter
PM | Hours exceeding | Firm capacity (short-term rating) | PMHours exceedingFirm capacity (short-term rating) | [13 empty] | Winter
PM | Regional diversity factor | Summer | PMRegional diversity factorSummer | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 | 0.69309 |  | Winter
PM | Regional diversity factor | Winter | PMRegional diversity factorWinter | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 | 0.56731 |  | Winter
PM | Load transfer capacity (MVA) | 1 | PMLoad transfer capacity (MVA)1 | 1 | [11 empty] | Avoca | Winter
PM | Load transfer capacity (MVA) | 2 | PMLoad transfer capacity (MVA)2 | 5 | [11 empty] | Hadspen | Winter
PM | Load transfer capacity (MVA) | 3 | PMLoad transfer capacity (MVA)3 | 2 | [11 empty] | Norwood | Winter
PM | Load transfer capacity (MVA) | 4 | PMLoad transfer capacity (MVA)4 | 1.5 | [11 empty] | Railton | Winter
PM | Load transfer capacity (MVA) | 5 | PMLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
PM | Embedded generation capacity (MVA) | Units less than 100 kVA | PMEmbedded generation capacity (MVA)Units less than 100 kVA | 1.026 | [12 empty] | Winter
PM | Embedded generation capacity (MVA) | Units greater than 100 kVA | PMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Winter
QT | Substation capacity (winter and summer) (MVA) | Total | QTSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
QT | Substation capacity (winter and summer) (MVA) | Firm delivery | QTSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
QT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | QTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Summer
QT | Maximum demand forecast(peak season) | Maximum demand (MW) | QTMaximum demand forecast(peak season)Maximum demand (MW) | 6.159 | 6.0752 | 6.0752 | 6.2644 | 6.3868 | 6.5029 | 6.5447 | 6.5958 | 6.6688 | 6.8021 | 7.137 | 7.4407 |  | Summer
QT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.069988 | 0.069036 | 0.069036 | 0.071187 | 0.072577 | 0.073896 | 0.074372 | 0.074952 | 0.075782 | 0.077297 | 0.081103 | 0.084554 |  | Summer
QT | Maximum demand forecast(peak season) | Maximum demand (MVA) | QTMaximum demand forecast(peak season)Maximum demand (MVA) | 6.1594 | 6.0756 | 6.0756 | 6.2649 | 6.3872 | 6.5033 | 6.5451 | 6.5962 | 6.6693 | 6.8026 | 7.1375 | 7.4412 |  | Summer
QT | Maximum demand forecast(peak season) | Power factor (coincident) | QTMaximum demand forecast(peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 |  | Summer
QT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | QTMaximum demand forecast(non-peak season)Maximum demand (MW) | 3.727 | 5.2746 | 5.2746 | 5.3549 | 5.5453 | 5.6787 | 5.7077 | 5.7379 | 5.7835 | 5.9675 | 6.3505 | 6.7338 |  | Summer
QT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.072311 | 0.10234 | 0.10234 | 0.1039 | 0.10759 | 0.11018 | 0.11074 | 0.11133 | 0.11221 | 0.11578 | 0.12321 | 0.13065 |  | Summer
QT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 3.7277 | 5.2756 | 5.2756 | 5.3559 | 5.5464 | 5.6797 | 5.7087 | 5.739 | 5.7846 | 5.9686 | 6.3517 | 6.7351 | 0 | Summer
QT | Hours exceeding | 95% of maximum demand | QTHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | Summer
QT | Hours exceeding | Firm capacity (continuous rating) | QTHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
QT | Hours exceeding | Firm capacity (short-term rating) | QTHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
QT | Regional diversity factor | Summer | QTRegional diversity factorSummer | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 | 0.84143 |  | Summer
QT | Regional diversity factor | Winter | QTRegional diversity factorWinter | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 | 0.88151 |  | Summer
QT | Load transfer capacity (MVA) | 1 | QTLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
QT | Load transfer capacity (MVA) | 2 | QTLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
QT | Load transfer capacity (MVA) | 3 | QTLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
QT | Load transfer capacity (MVA) | 4 | QTLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
QT | Load transfer capacity (MVA) | 5 | QTLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
QT | Embedded generation capacity (MVA) | Units less than 100 kVA | QTEmbedded generation capacity (MVA)Units less than 100 kVA | 0.88118 | [12 empty] | Summer
QT | Embedded generation capacity (MVA) | Units greater than 100 kVA | QTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
RA | Substation capacity (winter and summer) (MVA) | Total | RASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
RA | Substation capacity (winter and summer) (MVA) | Firm delivery | RASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
RA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | Summer
RA | Maximum demand forecast(peak season) | Maximum demand (MW) | RAMaximum demand forecast(peak season)Maximum demand (MW) | 48.2251 | 45.3172 | 46.6297 | 46.7288 | 47.6411 | 48.5073 | 48.8192 | 49.2006 | 49.7451 | 50.7395 | 53.2378 | 55.5029 |  | Summer
RA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 9.7894 | 9.1991 | 9.4655 | 9.4856 | 9.6708 | 9.8466 | 9.91 | 9.9874 | 10.0979 | 10.2998 | 10.8069 | 11.2667 |  | Summer
RA | Maximum demand forecast(peak season) | Maximum demand (MVA) | RAMaximum demand forecast(peak season)Maximum demand (MVA) | 49.2087 | 46.2414 | 47.5807 | 47.6818 | 48.6128 | 49.4966 | 49.8149 | 50.204 | 50.7597 | 51.7744 | 54.3235 | 56.6349 |  | Summer
RA | Maximum demand forecast(peak season) | Power factor (coincident) | RAMaximum demand forecast(peak season)Power factor (coincident) | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 |  | Summer
RA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RAMaximum demand forecast(non-peak season)Maximum demand (MW) | 47.3972 | 44.3072 | 45.7406 | 44.982 | 46.5813 | 47.7015 | 47.9449 | 48.1993 | 48.5819 | 50.1277 | 53.3447 | 56.5648 |  | Summer
RA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 16.971 | 15.8646 | 16.3779 | 16.1062 | 16.6789 | 17.08 | 17.1671 | 17.2582 | 17.3952 | 17.9487 | 19.1006 | 20.2536 |  | Summer
RA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 50.3439 | 47.0618 | 48.5844 | 47.7786 | 49.4773 | 50.6671 | 50.9256 | 51.1959 | 51.6023 | 53.2441 | 56.6612 | 60.0815 | 0 | Summer
RA | Hours exceeding | 95% of maximum demand | RAHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 |  | Summer
RA | Hours exceeding | Firm capacity (continuous rating) | RAHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
RA | Hours exceeding | Firm capacity (short-term rating) | RAHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
RA | Regional diversity factor | Summer | RARegional diversity factorSummer | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 | 0.76883 |  | Summer
RA | Regional diversity factor | Winter | RARegional diversity factorWinter | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 | 0.95984 |  | Summer
RA | Load transfer capacity (MVA) | 1 | RALoad transfer capacity (MVA)1 | 8.7 | [11 empty] | Devonport | Summer
RA | Load transfer capacity (MVA) | 2 | RALoad transfer capacity (MVA)2 | 4.4 | [11 empty] | Ulverstone | Summer
RA | Load transfer capacity (MVA) | 3 | RALoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
RA | Load transfer capacity (MVA) | 4 | RALoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
RA | Load transfer capacity (MVA) | 5 | RALoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
RA | Embedded generation capacity (MVA) | Units less than 100 kVA | RAEmbedded generation capacity (MVA)Units less than 100 kVA | 11.638 | [12 empty] | Summer
RA | Embedded generation capacity (MVA) | Units greater than 100 kVA | RAEmbedded generation capacity (MVA)Units greater than 100 kVA | 3.2592 | [12 empty] | Summer
RB22 | Substation capacity (winter and summer) (MVA) | Total | RB22Substation capacity (winter and summer) (MVA)Total | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | Summer
RB22 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB22Substation capacity (winter and summer) (MVA)Firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | Summer
RB22 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB22Substation capacity (winter and summer) (MVA)Short-term firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | Summer
RB22 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB22Maximum demand forecast(peak season)Maximum demand (MW) | 5.6102 | 2.308 | 2.308 | 2.3799 | 2.4264 | 2.4705 | 2.4864 | 2.5058 | 2.5336 | 2.5842 | 2.7114 | 2.8268 |  | Summer
RB22 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.43155 | 0.17754 | 0.17754 | 0.18307 | 0.18665 | 0.19004 | 0.19126 | 0.19276 | 0.19489 | 0.19879 | 0.20857 | 0.21745 |  | Summer
RB22 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB22Maximum demand forecast(peak season)Maximum demand (MVA) | 5.6267 | 2.3149 | 2.3149 | 2.387 | 2.4336 | 2.4778 | 2.4938 | 2.5132 | 2.5411 | 2.5918 | 2.7195 | 2.8352 |  | Summer
RB22 | Maximum demand forecast(peak season) | Power factor (coincident) | RB22Maximum demand forecast(peak season)Power factor (coincident) | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 | 0.99705 |  | Summer
RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB22Maximum demand forecast(non-peak season)Maximum demand (MW) | 2.2636 | 2.1547 | 2.1547 | 2.1875 | 2.2653 | 2.3197 | 2.3316 | 2.3439 | 2.3626 | 2.4377 | 2.5942 | 2.7508 |  | Summer
RB22 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 2.2636 | 2.1547 | 2.1547 | 2.1875 | 2.2653 | 2.3197 | 2.3316 | 2.3439 | 2.3626 | 2.4377 | 2.5942 | 2.7508 | 0 | Summer
RB22 | Hours exceeding | 95% of maximum demand | RB22Hours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Summer
RB22 | Hours exceeding | Firm capacity (continuous rating) | RB22Hours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
RB22 | Hours exceeding | Firm capacity (short-term rating) | RB22Hours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
RB22 | Regional diversity factor | Summer | RB22Regional diversity factorSummer | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 | 0.64286 |  | Summer
RB22 | Regional diversity factor | Winter | RB22Regional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RB22 | Load transfer capacity (MVA) | 1 | RB22Load transfer capacity (MVA)1 | [12 empty] | 0 | Summer
RB22 | Load transfer capacity (MVA) | 2 | RB22Load transfer capacity (MVA)2 | [12 empty] | 0 | Summer
RB22 | Load transfer capacity (MVA) | 3 | RB22Load transfer capacity (MVA)3 | [12 empty] | 0 | Summer
RB22 | Load transfer capacity (MVA) | 4 | RB22Load transfer capacity (MVA)4 | [12 empty] | 0 | Summer
RB22 | Load transfer capacity (MVA) | 5 | RB22Load transfer capacity (MVA)5 | [12 empty] | 0 | Summer
RB22 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB22Embedded generation capacity (MVA)Units less than 100 kVA | 0 | [12 empty] | Summer
RB22 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB22Embedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
RB44 | Substation capacity (winter and summer) (MVA) | Total | RB44Substation capacity (winter and summer) (MVA)Total | 72 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | Summer
RB44 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB44Substation capacity (winter and summer) (MVA)Firm delivery | 36 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | Summer
RB44 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB44Substation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | Summer
RB44 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB44Maximum demand forecast(peak season)Maximum demand (MW) | 39.8547 | 28.8812 | 27.6986 | 29.7808 | 30.3623 | 30.9143 | 31.1131 | 31.3562 | 31.7032 | 32.337 | 33.9291 | 35.3727 |  | Summer
RB44 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 15.8164 | 11.4615 | 10.9922 | 11.8185 | 12.0493 | 12.2684 | 12.3473 | 12.4437 | 12.5814 | 12.8329 | 13.4648 | 14.0377 |  | Summer
RB44 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB44Maximum demand forecast(peak season)Maximum demand (MVA) | 42.8784 | 31.0724 | 29.8 | 32.0402 | 32.6658 | 33.2597 | 33.4736 | 33.7351 | 34.1085 | 34.7903 | 36.5032 | 38.0563 |  | Summer
RB44 | Maximum demand forecast(peak season) | Power factor (coincident) | RB44Maximum demand forecast(peak season)Power factor (coincident) | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 | 0.92948 |  | Summer
RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB44Maximum demand forecast(non-peak season)Maximum demand (MW) | 39.5753 | 22.8253 | 21.4623 | 23.1729 | 23.9968 | 24.5738 | 24.6992 | 24.8303 | 25.0274 | 25.8237 | 27.481 | 29.1399 |  | Summer
RB44 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 14.0641 | 8.1115 | 7.6272 | 8.235 | 8.5278 | 8.7329 | 8.7775 | 8.824 | 8.8941 | 9.1771 | 9.766 | 10.3556 |  | Summer
RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 42.0001 | 24.2237 | 22.7773 | 24.5926 | 25.467 | 26.0794 | 26.2125 | 26.3516 | 26.5608 | 27.4059 | 29.1647 | 30.9252 | 0 | Summer
RB44 | Hours exceeding | 95% of maximum demand | RB44Hours exceeding95% of maximum demand | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 |  | Summer
RB44 | Hours exceeding | Firm capacity (continuous rating) | RB44Hours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
RB44 | Hours exceeding | Firm capacity (short-term rating) | RB44Hours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
RB44 | Regional diversity factor | Summer | RB44Regional diversity factorSummer | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 | 0.88287 |  | Summer
RB44 | Regional diversity factor | Winter | RB44Regional diversity factorWinter | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 | 0.86062 |  | Summer
RB44 | Load transfer capacity (MVA) | 1 | RB44Load transfer capacity (MVA)1 | [12 empty] | 0 | Summer
RB44 | Load transfer capacity (MVA) | 2 | RB44Load transfer capacity (MVA)2 | [12 empty] | 0 | Summer
RB44 | Load transfer capacity (MVA) | 3 | RB44Load transfer capacity (MVA)3 | [12 empty] | 0 | Summer
RB44 | Load transfer capacity (MVA) | 4 | RB44Load transfer capacity (MVA)4 | [12 empty] | 0 | Summer
RB44 | Load transfer capacity (MVA) | 5 | RB44Load transfer capacity (MVA)5 | [12 empty] | 0 | Summer
RB44 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB44Embedded generation capacity (MVA)Units less than 100 kVA | 0.57149 | [12 empty] | Summer
RB44 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB44Embedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
RI | Substation capacity (winter and summer) (MVA) | Total | RISubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Summer
RI | Substation capacity (winter and summer) (MVA) | Firm delivery | RISubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
RI | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RISubstation capacity (winter and summer) (MVA)Short-term firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
RI | Maximum demand forecast(peak season) | Maximum demand (MW) | RIMaximum demand forecast(peak season)Maximum demand (MW) | 66.7623 | 65.4366 | 65.4366 | 67.4749 | 70.3142 | 71.5926 | 72.053 | 72.6158 | 73.4196 | 74.8872 | 78.5744 | 81.9175 |  | Summer
RI | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 12.6041 | 12.3538 | 12.3538 | 12.7386 | 13.2747 | 13.516 | 13.6029 | 13.7092 | 13.8609 | 14.138 | 14.8341 | 15.4652 |  | Summer
RI | Maximum demand forecast(peak season) | Maximum demand (MVA) | RIMaximum demand forecast(peak season)Maximum demand (MVA) | 67.9417 | 66.5925 | 66.5925 | 68.6668 | 71.5563 | 72.8573 | 73.3258 | 73.8986 | 74.7165 | 76.2101 | 79.9624 | 83.3646 |  | Summer
RI | Maximum demand forecast(peak season) | Power factor (coincident) | RIMaximum demand forecast(peak season)Power factor (coincident) | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 |  | Summer
RI | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RIMaximum demand forecast(non-peak season)Maximum demand (MW) | 45.0936 | 51.2434 | 51.2434 | 52.0239 | 55.61 | 56.9473 | 57.2378 | 57.5416 | 57.9984 | 59.8437 | 63.6843 | 67.5285 |  | Summer
RI | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 7.5758 | 8.609 | 8.609 | 8.7401 | 9.3426 | 9.5672 | 9.616 | 9.6671 | 9.7438 | 10.0538 | 10.6991 | 11.3449 |  | Summer
RI | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 45.7255 | 51.9616 | 51.9616 | 52.7529 | 56.3893 | 57.7453 | 58.04 | 58.348 | 58.8112 | 60.6824 | 64.5768 | 68.4749 | 0 | Summer
RI | Hours exceeding | 95% of maximum demand | RIHours exceeding95% of maximum demand | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 |  | Summer
RI | Hours exceeding | Firm capacity (continuous rating) | RIHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
RI | Hours exceeding | Firm capacity (short-term rating) | RIHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
RI | Regional diversity factor | Summer | RIRegional diversity factorSummer | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 | 0.79104 |  | Summer
RI | Regional diversity factor | Winter | RIRegional diversity factorWinter | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 | 0.90684 |  | Summer
RI | Load transfer capacity (MVA) | 1 | RILoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
RI | Load transfer capacity (MVA) | 2 | RILoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
RI | Load transfer capacity (MVA) | 3 | RILoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
RI | Load transfer capacity (MVA) | 4 | RILoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
RI | Load transfer capacity (MVA) | 5 | RILoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
RI | Embedded generation capacity (MVA) | Units less than 100 kVA | RIEmbedded generation capacity (MVA)Units less than 100 kVA | 5.8486 | [12 empty] | Summer
RI | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.59998 | [12 empty] | Summer
RK | Substation capacity (winter and summer) (MVA) | Total | RKSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Summer
RK | Substation capacity (winter and summer) (MVA) | Firm delivery | RKSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Summer
RK | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RKSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | Summer
RK | Maximum demand forecast(peak season) | Maximum demand (MW) | RKMaximum demand forecast(peak season)Maximum demand (MW) | 22.8633 | 24.6616 | 24.6616 | 25.4297 | 25.9263 | 26.3976 | 26.5674 | 26.7749 | 27.0713 | 27.6124 | 28.9719 | 30.2046 |  | Summer
RK | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.23395 | 0.25235 | 0.25235 | 0.26021 | 0.26529 | 0.27011 | 0.27185 | 0.27398 | 0.27701 | 0.28255 | 0.29646 | 0.30907 |  | Summer
RK | Maximum demand forecast(peak season) | Maximum demand (MVA) | RKMaximum demand forecast(peak season)Maximum demand (MVA) | 22.8645 | 24.6628 | 24.6628 | 25.4311 | 25.9276 | 26.399 | 26.5688 | 26.7763 | 27.0727 | 27.6139 | 28.9735 | 30.2062 |  | Summer
RK | Maximum demand forecast(peak season) | Power factor (coincident) | RKMaximum demand forecast(peak season)Power factor (coincident) | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 |  | Summer
RK | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RKMaximum demand forecast(non-peak season)Maximum demand (MW) | 13.3975 | 17.3319 | 17.3319 | 17.5959 | 18.2215 | 18.6597 | 18.7549 | 18.8544 | 19.0041 | 19.6087 | 20.8672 | 22.1268 |  | Summer
RK | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.41426 | 0.53591 | 0.53591 | 0.54407 | 0.56341 | 0.57696 | 0.57991 | 0.58298 | 0.58761 | 0.60631 | 0.64522 | 0.68417 |  | Summer
RK | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 13.4039 | 17.3402 | 17.3402 | 17.6043 | 18.2302 | 18.6686 | 18.7638 | 18.8634 | 19.0132 | 19.6181 | 20.8771 | 22.1373 | 0 | Summer
RK | Hours exceeding | 95% of maximum demand | RKHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Summer
RK | Hours exceeding | Firm capacity (continuous rating) | RKHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
RK | Hours exceeding | Firm capacity (short-term rating) | RKHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
RK | Regional diversity factor | Summer | RKRegional diversity factorSummer | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 | 0.81879 |  | Summer
RK | Regional diversity factor | Winter | RKRegional diversity factorWinter | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 | 0.8624 |  | Summer
RK | Load transfer capacity (MVA) | 1 | RKLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Cambridge | Summer
RK | Load transfer capacity (MVA) | 2 | RKLoad transfer capacity (MVA)2 | 5.8 | [11 empty] | Howrah | Summer
RK | Load transfer capacity (MVA) | 3 | RKLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
RK | Load transfer capacity (MVA) | 4 | RKLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
RK | Load transfer capacity (MVA) | 5 | RKLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
RK | Embedded generation capacity (MVA) | Units less than 100 kVA | RKEmbedded generation capacity (MVA)Units less than 100 kVA | 7.1907 | [12 empty] | Summer
RK | Embedded generation capacity (MVA) | Units greater than 100 kVA | RKEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
SD | Substation capacity (winter and summer) (MVA) | Total | SDSubstation capacity (winter and summer) (MVA)Total | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | Summer
SD | Substation capacity (winter and summer) (MVA) | Firm delivery | SDSubstation capacity (winter and summer) (MVA)Firm delivery | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 |  | Summer
SD | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SDSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | Summer
SD | Maximum demand forecast(peak season) | Maximum demand (MW) | SDMaximum demand forecast(peak season)Maximum demand (MW) | 11.753 | 11.8326 | 11.8326 | 12.2012 | 12.4394 | 12.6656 | 12.747 | 12.8466 | 12.9888 | 13.2484 | 13.9007 | 14.4922 |  | Summer
SD | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.31679 | 0.31893 | 0.31893 | 0.32887 | 0.33529 | 0.34139 | 0.34358 | 0.34626 | 0.3501 | 0.3571 | 0.37468 | 0.39062 |  | Summer
SD | Maximum demand forecast(peak season) | Maximum demand (MVA) | SDMaximum demand forecast(peak season)Maximum demand (MVA) | 11.7572 | 11.8369 | 11.8369 | 12.2056 | 12.4439 | 12.6702 | 12.7516 | 12.8512 | 12.9935 | 13.2532 | 13.9058 | 14.4974 |  | Summer
SD | Maximum demand forecast(peak season) | Power factor (coincident) | SDMaximum demand forecast(peak season)Power factor (coincident) | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 |  | Summer
SD | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SDMaximum demand forecast(non-peak season)Maximum demand (MW) | 12.4365 | 11.8447 | 11.8447 | 12.0251 | 12.4526 | 12.7521 | 12.8171 | 12.8851 | 12.9874 | 13.4007 | 14.2607 | 15.1215 |  | Summer
SD | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.9908 | 1.896 | 1.896 | 1.9249 | 1.9934 | 2.0413 | 2.0517 | 2.0626 | 2.079 | 2.1451 | 2.2828 | 2.4206 |  | Summer
SD | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 12.5948 | 11.9955 | 11.9955 | 12.1782 | 12.6112 | 12.9144 | 12.9803 | 13.0492 | 13.1528 | 13.5713 | 14.4422 | 15.314 | 0 | Summer
SD | Hours exceeding | 95% of maximum demand | SDHours exceeding95% of maximum demand | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Summer
SD | Hours exceeding | Firm capacity (continuous rating) | SDHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
SD | Hours exceeding | Firm capacity (short-term rating) | SDHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
SD | Regional diversity factor | Summer | SDRegional diversity factorSummer | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 |  | Summer
SD | Regional diversity factor | Winter | SDRegional diversity factorWinter | 1 | 1 | [11 empty] | Summer | bar: 2024 to 2033
SD | Load transfer capacity (MVA) | 1 | SDLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Derby | Summer
SD | Load transfer capacity (MVA) | 2 | SDLoad transfer capacity (MVA)2 | 3.2 | [11 empty] | George Town | Summer
SD | Load transfer capacity (MVA) | 3 | SDLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn | Summer
SD | Load transfer capacity (MVA) | 4 | SDLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SD | Load transfer capacity (MVA) | 5 | SDLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SD | Embedded generation capacity (MVA) | Units less than 100 kVA | SDEmbedded generation capacity (MVA)Units less than 100 kVA | 4.8918 | [12 empty] | Summer
SD | Embedded generation capacity (MVA) | Units greater than 100 kVA | SDEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.89 | [12 empty] | Summer
SH | Substation capacity (winter and summer) (MVA) | Total | SHSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
SH | Substation capacity (winter and summer) (MVA) | Firm delivery | SHSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SH | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SHSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SH | Maximum demand forecast(peak season) | Maximum demand (MW) | SHMaximum demand forecast(peak season)Maximum demand (MW) | 0 | 1.9687 | 1.9687 | 2.03 | 2.0696 | 2.1073 | 2.1208 | 2.1374 | 2.161 | 2.2042 | 2.3128 | 2.4112 |  | Summer
SH | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SHMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0 | 0.17708 | 0.17708 | 0.18259 | 0.18616 | 0.18954 | 0.19076 | 0.19225 | 0.19438 | 0.19827 | 0.20803 | 0.21688 |  | Summer
SH | Maximum demand forecast(peak season) | Maximum demand (MVA) | SHMaximum demand forecast(peak season)Maximum demand (MVA) | 0 | 1.9766 | 1.9766 | 2.0382 | 2.078 | 2.1158 | 2.1294 | 2.146 | 2.1698 | 2.2131 | 2.3221 | 2.4209 |  | Summer
SH | Maximum demand forecast(peak season) | Power factor (coincident) | SHMaximum demand forecast(peak season)Power factor (coincident) | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 |  | Summer
SH | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SHMaximum demand forecast(non-peak season)Maximum demand (MW) | 0 | 1.7283 | 1.7283 | 1.7546 | 1.817 | 1.8607 | 1.8702 | 1.8801 | 1.895 | 1.9553 | 2.0808 | 2.2064 |  | Summer
SH | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SHMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0.22199 | 0.22199 | 0.22538 | 0.23339 | 0.239 | 0.24022 | 0.24149 | 0.24341 | 0.25116 | 0.26728 | 0.28341 |  | Summer
SH | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SHMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0 | 1.7425 | 1.7425 | 1.769 | 1.8319 | 1.876 | 1.8855 | 1.8955 | 1.9106 | 1.9714 | 2.0979 | 2.2245 |  | Summer
SH | Hours exceeding | 95% of maximum demand | SHHours exceeding95% of maximum demand | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 |  | Summer
SH | Hours exceeding | Firm capacity (continuous rating) | SHHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
SH | Hours exceeding | Firm capacity (short-term rating) | SHHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
SH | Regional diversity factor | Summer | SHRegional diversity factorSummer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SH | Regional diversity factor | Winter | SHRegional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SH | Load transfer capacity (MVA) | 1 | SHLoad transfer capacity (MVA)1 | 7.5 | [11 empty] | Railton | Summer
SH | Load transfer capacity (MVA) | 2 | SHLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
SH | Load transfer capacity (MVA) | 3 | SHLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
SH | Load transfer capacity (MVA) | 4 | SHLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SH | Load transfer capacity (MVA) | 5 | SHLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SH | Embedded generation capacity (MVA) | Units less than 100 kVA | SHEmbedded generation capacity (MVA)Units less than 100 kVA | 1.1198 | [12 empty] | Summer
SH | Embedded generation capacity (MVA) | Units greater than 100 kVA | SHEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
SL | Substation capacity (winter and summer) (MVA) | Total | SLSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
SL | Substation capacity (winter and summer) (MVA) | Firm delivery | SLSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
SL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 |  | Summer
SL | Maximum demand forecast(peak season) | Maximum demand (MW) | SLMaximum demand forecast(peak season)Maximum demand (MW) | 31.1908 | 29.5774 | 29.5774 | 30.4988 | 31.0942 | 31.6596 | 31.8632 | 32.1121 | 32.4675 | 33.1165 | 34.747 | 36.2254 |  | Summer
SL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.63027 | 0.59767 | 0.59767 | 0.61629 | 0.62832 | 0.63974 | 0.64386 | 0.64889 | 0.65607 | 0.66919 | 0.70213 | 0.73201 |  | Summer
SL | Maximum demand forecast(peak season) | Maximum demand (MVA) | SLMaximum demand forecast(peak season)Maximum demand (MVA) | 31.1972 | 29.5835 | 29.5835 | 30.505 | 31.1006 | 31.666 | 31.8697 | 32.1186 | 32.4741 | 33.1233 | 34.7541 | 36.2328 |  | Summer
SL | Maximum demand forecast(peak season) | Power factor (coincident) | SLMaximum demand forecast(peak season)Power factor (coincident) | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 |  | Summer
SL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SLMaximum demand forecast(non-peak season)Maximum demand (MW) | 36.3243 | 16.6205 | 16.6205 | 16.8736 | 17.4736 | 17.8938 | 17.9851 | 18.0805 | 18.224 | 18.8039 | 20.0106 | 21.2186 |  | Summer
SL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 36.3243 | 16.6205 | 16.6205 | 16.8736 | 17.4736 | 17.8938 | 17.9851 | 18.0805 | 18.224 | 18.8039 | 20.0106 | 21.2186 | 0 | Summer
SL | Hours exceeding | 95% of maximum demand | SLHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 |  | Summer
SL | Hours exceeding | Firm capacity (continuous rating) | SLHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
SL | Hours exceeding | Firm capacity (short-term rating) | SLHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
SL | Regional diversity factor | Summer | SLRegional diversity factorSummer | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 | 0.65982 |  | Summer
SL | Regional diversity factor | Winter | SLRegional diversity factorWinter | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 | 0.9316 |  | Summer
SL | Load transfer capacity (MVA) | 1 | SLLoad transfer capacity (MVA)1 | 3 | [11 empty] | Mowbray | Summer
SL | Load transfer capacity (MVA) | 2 | SLLoad transfer capacity (MVA)2 | 10 | [11 empty] | Norwood | Summer
SL | Load transfer capacity (MVA) | 3 | SLLoad transfer capacity (MVA)3 | 3 | [11 empty] | Trevallyn | Summer
SL | Load transfer capacity (MVA) | 4 | SLLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SL | Load transfer capacity (MVA) | 5 | SLLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SL | Embedded generation capacity (MVA) | Units less than 100 kVA | SLEmbedded generation capacity (MVA)Units less than 100 kVA | 5.9534 | [12 empty] | Summer
SL | Embedded generation capacity (MVA) | Units greater than 100 kVA | SLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
SM | Substation capacity (winter and summer) (MVA) | Total | SMSubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
SM | Substation capacity (winter and summer) (MVA) | Firm delivery | SMSubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 25[1] | 25 | 25 | 25 | 25 | 25 |  | Summer
SM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 30 | 30 | 30 | 30 | 30 |  | Summer
SM | Maximum demand forecast(peak season) | Maximum demand (MW) | SMMaximum demand forecast(peak season)Maximum demand (MW) | 17.1677 | 16.0193 | 16.0193 | 16.5183 | 16.8408 | 17.147 | 17.2572 | 17.392 | 17.5845 | 17.936 | 18.8191 | 19.6199 |  | Summer
SM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.67787 | 0.63252 | 0.63252 | 0.65223 | 0.66496 | 0.67705 | 0.6814 | 0.68673 | 0.69433 | 0.70821 | 0.74308 | 0.77469 |  | Summer
SM | Maximum demand forecast(peak season) | Maximum demand (MVA) | SMMaximum demand forecast(peak season)Maximum demand (MVA) | 17.1811 | 16.0318 | 16.0318 | 16.5311 | 16.8539 | 17.1603 | 17.2707 | 17.4056 | 17.5982 | 17.95 | 18.8338 | 19.6351 |  | Summer
SM | Maximum demand forecast(peak season) | Power factor (coincident) | SMMaximum demand forecast(peak season)Power factor (coincident) | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 | 0.99922 |  | Summer
SM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SMMaximum demand forecast(non-peak season)Maximum demand (MW) | 11.1303 | 12.8759 | 12.8759 | 13.072 | 13.5367 | 13.8622 | 13.933 | 14.0069 | 14.1181 | 14.5673 | 15.5022 | 16.438 |  | Summer
SM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.38952 | 0.4506 | 0.4506 | 0.45747 | 0.47373 | 0.48512 | 0.4876 | 0.49019 | 0.49408 | 0.5098 | 0.54252 | 0.57526 |  | Summer
SM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 11.1371 | 12.8837 | 12.8837 | 13.08 | 13.545 | 13.8707 | 13.9415 | 14.0155 | 14.1268 | 14.5762 | 15.5117 | 16.448 | 0 | Summer
SM | Hours exceeding | 95% of maximum demand | SMHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Summer
SM | Hours exceeding | Firm capacity (continuous rating) | SMHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
SM | Hours exceeding | Firm capacity (short-term rating) | SMHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
SM | Regional diversity factor | Summer | SMRegional diversity factorSummer | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 | 0.63105 |  | Summer
SM | Regional diversity factor | Winter | SMRegional diversity factorWinter | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 | 0.75654 |  | Summer
SM | Load transfer capacity (MVA) | 1 | SMLoad transfer capacity (MVA)1 | 2.8 | [11 empty] | Avoca | Summer
SM | Load transfer capacity (MVA) | 2 | SMLoad transfer capacity (MVA)2 | 4 | [11 empty] | Derby | Summer
SM | Load transfer capacity (MVA) | 3 | SMLoad transfer capacity (MVA)3 | 4.5 | [11 empty] | Triabunna | Summer
SM | Load transfer capacity (MVA) | 4 | SMLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SM | Load transfer capacity (MVA) | 5 | SMLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SM | Embedded generation capacity (MVA) | Units less than 100 kVA | SMEmbedded generation capacity (MVA)Units less than 100 kVA | 6.2124 | [12 empty] | Summer
SM | Embedded generation capacity (MVA) | Units greater than 100 kVA | SMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
SO | Substation capacity (winter and summer) (MVA) | Total | SOSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
SO | Substation capacity (winter and summer) (MVA) | Firm delivery | SOSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
SO | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SOSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 |  | Summer
SO | Maximum demand forecast(peak season) | Maximum demand (MW) | SOMaximum demand forecast(peak season)Maximum demand (MW) | 37.4644 | 35.8073 | 37.48 | 36.9227 | 37.6436 | 38.328 | 38.5745 | 38.8758 | 39.3061 | 40.0918 | 42.0658 | 43.8556 |  | Summer
SO | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.6015 | 1.5307 | 1.6022 | 1.5784 | 1.6092 | 1.6384 | 1.649 | 1.6619 | 1.6802 | 1.7138 | 1.7982 | 1.8747 |  | Summer
SO | Maximum demand forecast(peak season) | Maximum demand (MVA) | SOMaximum demand forecast(peak season)Maximum demand (MVA) | 37.4986 | 35.84 | 37.5142 | 36.9564 | 37.678 | 38.363 | 38.6097 | 38.9113 | 39.342 | 40.1284 | 42.1042 | 43.8957 |  | Summer
SO | Maximum demand forecast(peak season) | Power factor (coincident) | SOMaximum demand forecast(peak season)Power factor (coincident) | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 |  | Summer
SO | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SOMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.6115 | 26.6213 | 28.5174 | 27.0267 | 27.9877 | 28.6607 | 28.8069 | 28.9598 | 29.1897 | 30.1184 | 32.0514 | 33.9861 |  | Summer
SO | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.0462 | 2.3071 | 2.4714 | 2.3422 | 2.4255 | 2.4838 | 2.4965 | 2.5097 | 2.5297 | 2.6102 | 2.7777 | 2.9453 |  | Summer
SO | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.7 | 26.7211 | 28.6243 | 27.128 | 28.0926 | 28.7681 | 28.9149 | 29.0683 | 29.2991 | 30.2313 | 32.1715 | 34.1135 | 0 | Summer
SO | Hours exceeding | 95% of maximum demand | SOHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Summer
SO | Hours exceeding | Firm capacity (continuous rating) | SOHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
SO | Hours exceeding | Firm capacity (short-term rating) | SOHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
SO | Regional diversity factor | Summer | SORegional diversity factorSummer | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 | 0.77083 |  | Summer
SO | Regional diversity factor | Winter | SORegional diversity factorWinter | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 | 0.92281 |  | Summer
SO | Load transfer capacity (MVA) | 1 | SOLoad transfer capacity (MVA)1 | 1.5 | [11 empty] | Avoca | Summer
SO | Load transfer capacity (MVA) | 2 | SOLoad transfer capacity (MVA)2 | 1.5 | [11 empty] | Meadowbank | Summer
SO | Load transfer capacity (MVA) | 3 | SOLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | Triabunna | Summer
SO | Load transfer capacity (MVA) | 4 | SOLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SO | Load transfer capacity (MVA) | 5 | SOLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SO | Embedded generation capacity (MVA) | Units less than 100 kVA | SOEmbedded generation capacity (MVA)Units less than 100 kVA | 12.6619 | [12 empty] | Summer
SO | Embedded generation capacity (MVA) | Units greater than 100 kVA | SOEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.067 | [12 empty] | Summer
SR | Substation capacity (winter and summer) (MVA) | Total | SRSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 |  | Summer
SR | Substation capacity (winter and summer) (MVA) | Firm delivery | SRSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25[2] | 25 | 25 |  | Summer
SR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 |  | Summer
SR | Maximum demand forecast(peak season) | Maximum demand (MW) | SRMaximum demand forecast(peak season)Maximum demand (MW) | 23.3348 | 1.0986 | 1.0986 | 1.1329 | 1.155 | 1.176 | 1.1836 | 1.1928 | 1.206 | 1.2301 | 1.2907 | 1.3456 |  | Summer
SR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.62659 | 0.029501 | 0.029501 | 0.03042 | 0.031014 | 0.031578 | 0.031781 | 0.032029 | 0.032384 | 0.033031 | 0.034657 | 0.036132 |  | Summer
SR | Maximum demand forecast(peak season) | Maximum demand (MVA) | SRMaximum demand forecast(peak season)Maximum demand (MVA) | 23.3432 | 1.099 | 1.099 | 1.1333 | 1.1554 | 1.1764 | 1.184 | 1.1932 | 1.2064 | 1.2305 | 1.2911 | 1.3461 |  | Summer
SR | Maximum demand forecast(peak season) | Power factor (coincident) | SRMaximum demand forecast(peak season)Power factor (coincident) | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 |  | Summer
SR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SRMaximum demand forecast(non-peak season)Maximum demand (MW) | 23.1001 | 0.99811 | 0.99811 | 1.0133 | 1.0493 | 1.0746 | 1.0801 | 1.0858 | 1.0944 | 1.1292 | 1.2017 | 1.2742 |  | Summer
SR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.1001 | 0.99811 | 0.99811 | 1.0133 | 1.0493 | 1.0746 | 1.0801 | 1.0858 | 1.0944 | 1.1292 | 1.2017 | 1.2742 | 0 | Summer
SR | Hours exceeding | 95% of maximum demand | SRHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Summer
SR | Hours exceeding | Firm capacity (continuous rating) | SRHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
SR | Hours exceeding | Firm capacity (short-term rating) | SRHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
SR | Regional diversity factor | Summer | SRRegional diversity factorSummer | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 | 0.79167 |  | Summer
SR | Regional diversity factor | Winter | SRRegional diversity factorWinter | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 |  | Summer
SR | Load transfer capacity (MVA) | 1 | SRLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
SR | Load transfer capacity (MVA) | 2 | SRLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
SR | Load transfer capacity (MVA) | 3 | SRLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
SR | Load transfer capacity (MVA) | 4 | SRLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
SR | Load transfer capacity (MVA) | 5 | SRLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
SR | Embedded generation capacity (MVA) | Units less than 100 kVA | SREmbedded generation capacity (MVA)Units less than 100 kVA | 0.19812 | [12 empty] | Summer
SR | Embedded generation capacity (MVA) | Units greater than 100 kVA | SREmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
ST | Substation capacity (winter and summer) (MVA) | Total | STSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
ST | Substation capacity (winter and summer) (MVA) | Firm delivery | STSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | Winter
ST | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | STSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | Winter
ST | Maximum demand forecast(peak season) | Maximum demand (MW) | STMaximum demand forecast(peak season)Maximum demand (MW) | 24.0732 | 22.9921 | 22.9921 | 23.3423 | 24.1722 | 24.7535 | 24.8798 | 25.0118 | 25.2104 | 26.0125 | 27.6819 | 29.3529 |  | Winter
ST | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 7.815 | 7.464 | 7.464 | 7.5777 | 7.8471 | 8.0358 | 8.0768 | 8.1197 | 8.1842 | 8.4446 | 8.9865 | 9.529 |  | Winter
ST | Maximum demand forecast(peak season) | Maximum demand (MVA) | STMaximum demand forecast(peak season)Maximum demand (MVA) | 25.3099 | 24.1733 | 24.1733 | 24.5415 | 25.414 | 26.0252 | 26.1579 | 26.2968 | 26.5055 | 27.3488 | 29.104 | 30.8608 |  | Winter
ST | Maximum demand forecast(peak season) | Power factor (coincident) | STMaximum demand forecast(peak season)Power factor (coincident) | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 | 0.95114 |  | Winter
ST | Maximum demand forecast(non-peak season) | Maximum demand (MW) | STMaximum demand forecast(non-peak season)Maximum demand (MW) | 21.4463 | 20.9247 | 20.9247 | 21.5765 | 21.9977 | 22.3977 | 22.5417 | 22.7178 | 22.9693 | 23.4284 | 24.5819 | 25.6278 |  | Winter
ST | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.2457 | 4.1424 | 4.1424 | 4.2715 | 4.3549 | 4.4341 | 4.4626 | 4.4974 | 4.5472 | 4.6381 | 4.8665 | 5.0735 |  | Winter
ST | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 21.8625 | 21.3308 | 21.3308 | 21.9952 | 22.4247 | 22.8324 | 22.9792 | 23.1587 | 23.415 | 23.8831 | 25.059 | 26.1252 | 0 | Winter
ST | Hours exceeding | 95% of maximum demand | STHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 |  | Winter
ST | Hours exceeding | Firm capacity (continuous rating) | STHours exceedingFirm capacity (continuous rating) | [13 empty] | Winter
ST | Hours exceeding | Firm capacity (short-term rating) | STHours exceedingFirm capacity (short-term rating) | [13 empty] | Winter
ST | Regional diversity factor | Summer | STRegional diversity factorSummer | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 | 0.87291 |  | Winter
ST | Regional diversity factor | Winter | STRegional diversity factorWinter | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 | 0.79216 |  | Winter
ST | Load transfer capacity (MVA) | 1 | STLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Port Latta | Winter
ST | Load transfer capacity (MVA) | 2 | STLoad transfer capacity (MVA)2 | [12 empty] | 0 | Winter
ST | Load transfer capacity (MVA) | 3 | STLoad transfer capacity (MVA)3 | [12 empty] | 0 | Winter
ST | Load transfer capacity (MVA) | 4 | STLoad transfer capacity (MVA)4 | [12 empty] | 0 | Winter
ST | Load transfer capacity (MVA) | 5 | STLoad transfer capacity (MVA)5 | [12 empty] | 0 | Winter
ST | Embedded generation capacity (MVA) | Units less than 100 kVA | STEmbedded generation capacity (MVA)Units less than 100 kVA | 3.3141 | [12 empty] | Winter
ST | Embedded generation capacity (MVA) | Units greater than 100 kVA | STEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.1333 | [12 empty] | Winter
TB | Substation capacity (winter and summer) (MVA) | Total | TBSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
TB | Substation capacity (winter and summer) (MVA) | Firm delivery | TBSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
TB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | Summer
TB | Maximum demand forecast(peak season) | Maximum demand (MW) | TBMaximum demand forecast(peak season)Maximum demand (MW) | 8.4056 | 8.6351 | 8.6351 | 8.9041 | 9.0779 | 9.243 | 9.3024 | 9.3751 | 9.4788 | 9.6683 | 10.1443 | 10.576 |  | Summer
TB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.4238 | 3.5172 | 3.5172 | 3.6268 | 3.6976 | 3.7648 | 3.7891 | 3.8187 | 3.8609 | 3.9381 | 4.132 | 4.3078 |  | Summer
TB | Maximum demand forecast(peak season) | Maximum demand (MVA) | TBMaximum demand forecast(peak season)Maximum demand (MVA) | 9.0762 | 9.3239 | 9.3239 | 9.6144 | 9.8021 | 9.9803 | 10.0445 | 10.1229 | 10.235 | 10.4396 | 10.9536 | 11.4196 |  | Summer
TB | Maximum demand forecast(peak season) | Power factor (coincident) | TBMaximum demand forecast(peak season)Power factor (coincident) | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 | 0.92612 |  | Summer
TB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TBMaximum demand forecast(non-peak season)Maximum demand (MW) | 5.8083 | 6.235 | 6.235 | 6.3299 | 6.555 | 6.7126 | 6.7469 | 6.7827 | 6.8365 | 7.0541 | 7.5068 | 7.9599 |  | Summer
TB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.58603 | 0.62908 | 0.62908 | 0.63866 | 0.66137 | 0.67727 | 0.68073 | 0.68434 | 0.68977 | 0.71172 | 0.7574 | 0.80312 |  | Summer
TB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 5.8378 | 6.2666 | 6.2666 | 6.3621 | 6.5883 | 6.7467 | 6.7811 | 6.8171 | 6.8712 | 7.0899 | 7.5449 | 8.0003 | 0 | Summer
TB | Hours exceeding | 95% of maximum demand | TBHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Summer
TB | Hours exceeding | Firm capacity (continuous rating) | TBHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
TB | Hours exceeding | Firm capacity (short-term rating) | TBHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
TB | Regional diversity factor | Summer | TBRegional diversity factorSummer | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 | 0.662 |  | Summer
TB | Regional diversity factor | Winter | TBRegional diversity factorWinter | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 | 0.82309 |  | Summer
TB | Load transfer capacity (MVA) | 1 | TBLoad transfer capacity (MVA)1 | 3 | [11 empty] | St Marys | Summer
TB | Load transfer capacity (MVA) | 2 | TBLoad transfer capacity (MVA)2 | 1.8 | [11 empty] | Sorell | Summer
TB | Load transfer capacity (MVA) | 3 | TBLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
TB | Load transfer capacity (MVA) | 4 | TBLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
TB | Load transfer capacity (MVA) | 5 | TBLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
TB | Embedded generation capacity (MVA) | Units less than 100 kVA | TBEmbedded generation capacity (MVA)Units less than 100 kVA | 2.9445 | [12 empty] | Summer
TB | Embedded generation capacity (MVA) | Units greater than 100 kVA | TBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
TR | Substation capacity (winter and summer) (MVA) | Total | TRSubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Summer
TR | Substation capacity (winter and summer) (MVA) | Firm delivery | TRSubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Summer
TR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | Summer
TR | Maximum demand forecast(peak season) | Maximum demand (MW) | TRMaximum demand forecast(peak season)Maximum demand (MW) | 71.3102 | 68.7723 | 69.3079 | 73.4689 | 72.2991 | 73.6135 | 74.087 | 74.6656 | 75.4921 | 77.0012 | 80.7924 | 84.2299 |  | Summer
TR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.4265 | 1.3757 | 1.3864 | 1.4696 | 1.4462 | 1.4725 | 1.482 | 1.4936 | 1.5101 | 1.5403 | 1.6161 | 1.6849 |  | Summer
TR | Maximum demand forecast(peak season) | Maximum demand (MVA) | TRMaximum demand forecast(peak season)Maximum demand (MVA) | 71.3244 | 68.786 | 69.3218 | 73.4836 | 72.3135 | 73.6283 | 74.1018 | 74.6806 | 75.5072 | 77.0166 | 80.8086 | 84.2468 |  | Summer
TR | Maximum demand forecast(peak season) | Power factor (coincident) | TRMaximum demand forecast(peak season)Power factor (coincident) | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 |  | Summer
TR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TRMaximum demand forecast(non-peak season)Maximum demand (MW) | 38.6277 | 42.7002 | 43.3087 | 46.2077 | 44.8918 | 45.9713 | 46.2059 | 46.4511 | 46.8199 | 48.3095 | 51.4099 | 54.5132 |  | Summer
TR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.6109 | 1.7808 | 1.8061 | 1.927 | 1.8722 | 1.9172 | 1.927 | 1.9372 | 1.9526 | 2.0147 | 2.144 | 2.2734 |  | Summer
TR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 38.6613 | 42.7373 | 43.3463 | 46.2478 | 44.9308 | 46.0113 | 46.2461 | 46.4915 | 46.8606 | 48.3515 | 51.4546 | 54.5606 | 0 | Summer
TR | Hours exceeding | 95% of maximum demand | TRHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 |  | Summer
TR | Hours exceeding | Firm capacity (continuous rating) | TRHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
TR | Hours exceeding | Firm capacity (short-term rating) | TRHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
TR | Regional diversity factor | Summer | TRRegional diversity factorSummer | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 | 0.88594 |  | Summer
TR | Regional diversity factor | Winter | TRRegional diversity factorWinter | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 | 0.92367 |  | Summer
TR | Load transfer capacity (MVA) | 1 | TRLoad transfer capacity (MVA)1 | 3.6 | [11 empty] | George Town | Summer
TR | Load transfer capacity (MVA) | 2 | TRLoad transfer capacity (MVA)2 | 14.4 | [11 empty] | Hadspen | Summer
TR | Load transfer capacity (MVA) | 3 | TRLoad transfer capacity (MVA)3 | 36.1 | [11 empty] | Mowbray | Summer
TR | Load transfer capacity (MVA) | 4 | TRLoad transfer capacity (MVA)4 | 21.7 | [11 empty] | Norwood | Summer
TR | Load transfer capacity (MVA) | 5 | TRLoad transfer capacity (MVA)5 | 21.7 | [11 empty] | St Leonards | Summer
TR | Embedded generation capacity (MVA) | Units less than 100 kVA | TREmbedded generation capacity (MVA)Units less than 100 kVA | 20.6073 | [12 empty] | Summer
TR | Embedded generation capacity (MVA) | Units greater than 100 kVA | TREmbedded generation capacity (MVA)Units greater than 100 kVA | 2 | [12 empty] | Summer
TU | Substation capacity (winter and summer) (MVA) | Total | TUSubstation capacity (winter and summer) (MVA)Total | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | Summer
TU | Substation capacity (winter and summer) (MVA) | Firm delivery | TUSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
TU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
TU | Maximum demand forecast(peak season) | Maximum demand (MW) | TUMaximum demand forecast(peak season)Maximum demand (MW) | 1.025 | 1.0904 | 1.0904 | 1.1244 | 1.1463 | 1.1672 | 1.1747 | 1.1839 | 1.197 | 1.2209 | 1.281 | 1.3355 |  | Summer
TU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.057031 | 0.060674 | 0.060674 | 0.062564 | 0.063785 | 0.064945 | 0.065363 | 0.065873 | 0.066602 | 0.067934 | 0.071278 | 0.074311 |  | Summer
TU | Maximum demand forecast(peak season) | Maximum demand (MVA) | TUMaximum demand forecast(peak season)Maximum demand (MVA) | 1.0265 | 1.0921 | 1.0921 | 1.1261 | 1.1481 | 1.169 | 1.1765 | 1.1857 | 1.1988 | 1.2228 | 1.283 | 1.3376 |  | Summer
TU | Maximum demand forecast(peak season) | Power factor (coincident) | TUMaximum demand forecast(peak season)Power factor (coincident) | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 |  | Summer
TU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TUMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.73769 | 0.91479 | 0.91479 | 0.92872 | 0.96174 | 0.98487 | 0.98989 | 0.99515 | 1.003 | 1.035 | 1.1014 | 1.1679 |  | Summer
TU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.13382 | 0.16595 | 0.16595 | 0.16848 | 0.17447 | 0.17866 | 0.17958 | 0.18053 | 0.18196 | 0.18775 | 0.1998 | 0.21186 |  | Summer
TU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.74973 | 0.92972 | 0.92972 | 0.94388 | 0.97744 | 1.0009 | 1.006 | 1.0114 | 1.0194 | 1.0519 | 1.1194 | 1.1869 | 0 | Summer
TU | Hours exceeding | 95% of maximum demand | TUHours exceeding95% of maximum demand | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 |  | Summer
TU | Hours exceeding | Firm capacity (continuous rating) | TUHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
TU | Hours exceeding | Firm capacity (short-term rating) | TUHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
TU | Regional diversity factor | Summer | TURegional diversity factorSummer | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 | 0.61017 |  | Summer
TU | Regional diversity factor | Winter | TURegional diversity factorWinter | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 | 0.83333 |  | Summer
TU | Load transfer capacity (MVA) | 1 | TULoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
TU | Load transfer capacity (MVA) | 2 | TULoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
TU | Load transfer capacity (MVA) | 3 | TULoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
TU | Load transfer capacity (MVA) | 4 | TULoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
TU | Load transfer capacity (MVA) | 5 | TULoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
TU | Embedded generation capacity (MVA) | Units less than 100 kVA | TUEmbedded generation capacity (MVA)Units less than 100 kVA | 0.0657 | [12 empty] | Summer
TU | Embedded generation capacity (MVA) | Units greater than 100 kVA | TUEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
UL | Substation capacity (winter and summer) (MVA) | Total | ULSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Summer
UL | Substation capacity (winter and summer) (MVA) | Firm delivery | ULSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Summer
UL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ULSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | Summer
UL | Maximum demand forecast(peak season) | Maximum demand (MW) | ULMaximum demand forecast(peak season)Maximum demand (MW) | 31.4125 | 29.111 | 29.111 | 30.0178 | 30.6039 | 31.1603 | 31.3607 | 31.6056 | 31.9555 | 32.5943 | 34.1991 | 35.6542 |  | Summer
UL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.18071 | 0.16747 | 0.16747 | 0.17268 | 0.17605 | 0.17925 | 0.18041 | 0.18182 | 0.18383 | 0.1875 | 0.19674 | 0.20511 |  | Summer
UL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ULMaximum demand forecast(peak season)Maximum demand (MVA) | 31.413 | 29.1115 | 29.1115 | 30.0183 | 30.6044 | 31.1608 | 31.3612 | 31.6062 | 31.956 | 32.5948 | 34.1996 | 35.6547 |  | Summer
UL | Maximum demand forecast(peak season) | Power factor (coincident) | ULMaximum demand forecast(peak season)Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 |  | Summer
UL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ULMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.0639 | 22.3242 | 22.3242 | 22.6642 | 23.47 | 24.0344 | 24.157 | 24.2852 | 24.478 | 25.2568 | 26.8777 | 28.5002 |  | Summer
UL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.1166 | 1.3076 | 1.3076 | 1.3275 | 1.3747 | 1.4078 | 1.415 | 1.4225 | 1.4338 | 1.4794 | 1.5743 | 1.6694 |  | Summer
UL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 19.0966 | 22.3624 | 22.3624 | 22.703 | 23.5102 | 24.0756 | 24.1984 | 24.3268 | 24.52 | 25.3001 | 26.9238 | 28.549 | 0 | Summer
UL | Hours exceeding | 95% of maximum demand | ULHours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |  | Summer
UL | Hours exceeding | Firm capacity (continuous rating) | ULHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
UL | Hours exceeding | Firm capacity (short-term rating) | ULHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
UL | Regional diversity factor | Summer | ULRegional diversity factorSummer | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 | 0.67998 |  | Summer
UL | Regional diversity factor | Winter | ULRegional diversity factorWinter | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 | 0.84857 |  | Summer
UL | Load transfer capacity (MVA) | 1 | ULLoad transfer capacity (MVA)1 | 6.8 | [11 empty] | Burnie | Summer
UL | Load transfer capacity (MVA) | 2 | ULLoad transfer capacity (MVA)2 | 10.3 | [11 empty] | Devonport | Summer
UL | Load transfer capacity (MVA) | 3 | ULLoad transfer capacity (MVA)3 | 3.4 | [11 empty] | Railton | Summer
UL | Load transfer capacity (MVA) | 4 | ULLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
UL | Load transfer capacity (MVA) | 5 | ULLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
UL | Embedded generation capacity (MVA) | Units less than 100 kVA | ULEmbedded generation capacity (MVA)Units less than 100 kVA | 10.809 | [12 empty] | Summer
UL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ULEmbedded generation capacity (MVA)Units greater than 100 kVA | 8.805 | [12 empty] | Summer
WA | Substation capacity (winter and summer) (MVA) | Total | WASubstation capacity (winter and summer) (MVA)Total | 3.8[1] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Summer
WA | Substation capacity (winter and summer) (MVA) | Firm delivery | WASubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
WA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
WA | Maximum demand forecast(peak season) | Maximum demand (MW) | WAMaximum demand forecast(peak season)Maximum demand (MW) | 0.90555 | 0.65002 | 0.65002 | 0.67026 | 0.68335 | 0.69578 | 0.70025 | 0.70572 | 0.71353 | 0.72779 | 0.76363 | 0.79612 |  | Summer
WA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
WA | Maximum demand forecast(peak season) | Maximum demand (MVA) | WAMaximum demand forecast(peak season)Maximum demand (MVA) | 0.90555 | 0.65002 | 0.65002 | 0.67026 | 0.68335 | 0.69578 | 0.70025 | 0.70572 | 0.71353 | 0.72779 | 0.76363 | 0.79612 |  | Summer
WA | Maximum demand forecast(peak season) | Power factor (coincident) | WAMaximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | [11 empty] | Summer | bar: 2024 to 2033
WA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WAMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.14144 | 0.49201 | 0.49201 | 0.49951 | 0.51727 | 0.52971 | 0.53241 | 0.53523 | 0.53948 | 0.55665 | 0.59237 | 0.62813 |  | Summer
WA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.023849 | 0.082958 | 0.082958 | 0.084222 | 0.087216 | 0.089314 | 0.089769 | 0.090246 | 0.090962 | 0.093856 | 0.09988 | 0.10591 |  | Summer
WA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.14344 | 0.49896 | 0.49896 | 0.50656 | 0.52457 | 0.53718 | 0.53992 | 0.54279 | 0.5471 | 0.5645 | 0.60073 | 0.63699 | 0 | Summer
WA | Hours exceeding | 95% of maximum demand | WAHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Summer
WA | Hours exceeding | Firm capacity (continuous rating) | WAHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
WA | Hours exceeding | Firm capacity (short-term rating) | WAHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  | Summer
WA | Regional diversity factor | Summer | WARegional diversity factorSummer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
WA | Regional diversity factor | Winter | WARegional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
WA | Load transfer capacity (MVA) | 1 | WALoad transfer capacity (MVA)1 | 0.9 | [11 empty] | Arthurs Lake | Summer
WA | Load transfer capacity (MVA) | 2 | WALoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
WA | Load transfer capacity (MVA) | 3 | WALoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
WA | Load transfer capacity (MVA) | 4 | WALoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
WA | Load transfer capacity (MVA) | 5 | WALoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
WA | Embedded generation capacity (MVA) | Units less than 100 kVA | WAEmbedded generation capacity (MVA)Units less than 100 kVA | 0 | [12 empty] | Summer
WA | Embedded generation capacity (MVA) | Units greater than 100 kVA | WAEmbedded generation capacity (MVA)Units greater than 100 kVA | 0 | [12 empty] | Summer
WV | Substation capacity (winter and summer) (MVA) | Total | WVSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
WV | Substation capacity (winter and summer) (MVA) | Firm delivery | WVSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
WV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | Summer
WV | Maximum demand forecast(peak season) | Maximum demand (MW) | WVMaximum demand forecast(peak season)Maximum demand (MW) | 11.4346 | 11.1056 | 11.7751 | 11.4516 | 11.6752 | 11.8874 | 11.9639 | 12.0573 | 12.1908 | 12.4345 | 13.0467 | 13.6018 |  | Summer
WV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.28204 | 0.27393 | 0.29044 | 0.28246 | 0.28797 | 0.29321 | 0.29509 | 0.2974 | 0.30069 | 0.3067 | 0.3218 | 0.33549 |  | Summer
WV | Maximum demand forecast(peak season) | Maximum demand (MVA) | WVMaximum demand forecast(peak season)Maximum demand (MVA) | 11.4381 | 11.109 | 11.7787 | 11.4551 | 11.6787 | 11.891 | 11.9675 | 12.061 | 12.1945 | 12.4383 | 13.0507 | 13.6059 |  | Summer
WV | Maximum demand forecast(peak season) | Power factor (coincident) | WVMaximum demand forecast(peak season)Power factor (coincident) | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 |  | Summer
WV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WVMaximum demand forecast(non-peak season)Maximum demand (MW) | 8.8445 | 8.5582 | 9.317 | 8.6885 | 8.9974 | 9.2138 | 9.2608 | 9.3099 | 9.3839 | 9.6824 | 10.3038 | 10.9258 |  | Summer
WV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.7113 | 0.68827 | 0.7493 | 0.69875 | 0.7236 | 0.741 | 0.74478 | 0.74873 | 0.75467 | 0.77868 | 0.82866 | 0.87868 |  | Summer
WV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 8.8731 | 8.5858 | 9.3471 | 8.7166 | 9.0265 | 9.2435 | 9.2907 | 9.34 | 9.4142 | 9.7137 | 10.3371 | 10.9611 | 0 | Summer
WV | Hours exceeding | 95% of maximum demand | WVHours exceeding95% of maximum demand | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | Summer
WV | Hours exceeding | Firm capacity (continuous rating) | WVHours exceedingFirm capacity (continuous rating) | [13 empty] | Summer
WV | Hours exceeding | Firm capacity (short-term rating) | WVHours exceedingFirm capacity (short-term rating) | [13 empty] | Summer
WV | Regional diversity factor | Summer | WVRegional diversity factorSummer | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 | 0.77692 |  | Summer
WV | Regional diversity factor | Winter | WVRegional diversity factorWinter | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 | 0.8574 |  | Summer
WV | Load transfer capacity (MVA) | 1 | WVLoad transfer capacity (MVA)1 | [12 empty] | 0 | Summer
WV | Load transfer capacity (MVA) | 2 | WVLoad transfer capacity (MVA)2 | [12 empty] | 0 | Summer
WV | Load transfer capacity (MVA) | 3 | WVLoad transfer capacity (MVA)3 | [12 empty] | 0 | Summer
WV | Load transfer capacity (MVA) | 4 | WVLoad transfer capacity (MVA)4 | [12 empty] | 0 | Summer
WV | Load transfer capacity (MVA) | 5 | WVLoad transfer capacity (MVA)5 | [12 empty] | 0 | Summer
WV | Embedded generation capacity (MVA) | Units less than 100 kVA | WVEmbedded generation capacity (MVA)Units less than 100 kVA | 4.0988 | [12 empty] | Summer
WV | Embedded generation capacity (MVA) | Units greater than 100 kVA | WVEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.265 | [12 empty] | Summer

## Zone data 2.0
CODE |  |  |  | 2022 (Actuals) | 2023 (Actuals) | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | Load transfer point | Non-peaking season
BEZ | Substation capacity (winter and summer) (MVA) | Total | BEZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 |  | Summer
BEZ | Substation capacity (winter and summer) (MVA) | Firm delivery | BEZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer | Macros
BEZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BEZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
BEZ | Sub-transmission lines capacity | Total (winter) | BEZSub-transmission lines capacityTotal (winter) | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 |  | Summer
BEZ | Sub-transmission lines capacity | Firm delivery (winter) | BEZSub-transmission lines capacityFirm delivery (winter) | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 |  | Summer
BEZ | Sub-transmission lines capacity | Total (summer) | BEZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | Summer
BEZ | Sub-transmission lines capacity | Firm delivery (summer) | BEZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  | Summer
BEZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(peak season)Maximum demand (MVA) | 10.3203 | 10.5204 | 10.5204 | 10.8481 | 11.0599 | 11.2609 | 11.3334 | 11.4219 | 11.5483 | 11.7792 | 12.3591 | 12.885 |  | Summer
BEZ | Maximum demand forecast(peak season) | Power factor (coincident) | BEZMaximum demand forecast(peak season)Power factor (coincident) | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 |  | Summer
BEZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.558 | 9.8484 | 9.8484 | 9.9984 | 10.3539 | 10.6029 | 10.657 | 10.7135 | 10.7986 | 11.1421 | 11.8572 | 12.573 |  | Summer
BEZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | BEZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 |  | Summer
BEZ | Hours exceeding | 95% of maximum demand | BEZHours exceeding95% of maximum demand | 3 | [12 empty] | Summer
BEZ | Load transfer capacity (MVA) | 1 | BEZLoad transfer capacity (MVA)1 | 6.2 | [11 empty] | Cambridge | Summer
BEZ | Load transfer capacity (MVA) | 2 | BEZLoad transfer capacity (MVA)2 | 4.1 | [11 empty] | Geilston Bay | Summer
BEZ | Load transfer capacity (MVA) | 3 | BEZLoad transfer capacity (MVA)3 | 3.1 | [11 empty] | Howrah | Summer
BEZ | Load transfer capacity (MVA) | 4 | BEZLoad transfer capacity (MVA)4 | 3.1 | [11 empty] | Rokeby | Summer
BEZ | Embedded generation capacity (MVA) | Units less than 100 kVA | BEZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.876 | [12 empty] | Summer
BEZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | BEZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
CAZ | Substation capacity (winter and summer) (MVA) | Total | CAZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Summer
CAZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CAZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Summer
CAZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CAZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | Summer
CAZ | Sub-transmission lines capacity | Total (winter) | CAZSub-transmission lines capacityTotal (winter) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 |  | Summer
CAZ | Sub-transmission lines capacity | Firm delivery (winter) | CAZSub-transmission lines capacityFirm delivery (winter) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 |  | Summer
CAZ | Sub-transmission lines capacity | Total (summer) | CAZSub-transmission lines capacityTotal (summer) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 |  | Summer
CAZ | Sub-transmission lines capacity | Firm delivery (summer) | CAZSub-transmission lines capacityFirm delivery (summer) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 |  | Summer
CAZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(peak season)Maximum demand (MVA) | 16.9885 | 18.8922 | 18.8922 | 19.4807 | 19.8611 | 20.2221 | 20.3522 | 20.5112 | 20.7382 | 21.1527 | 22.1942 | 23.1385 |  | Summer
CAZ | Maximum demand forecast(peak season) | Power factor (coincident) | CAZMaximum demand forecast(peak season)Power factor (coincident) | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 | 0.99488 |  | Summer
CAZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.5347 | 16.3127 | 16.3127 | 16.5611 | 17.15 | 17.5624 | 17.652 | 17.7457 | 17.8865 | 18.4556 | 19.6401 | 20.8256 |  | Summer
CAZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CAZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 | 0.98311 |  | Summer
CAZ | Hours exceeding | 95% of maximum demand | CAZHours exceeding95% of maximum demand | 11 | [12 empty] | Summer
CAZ | Load transfer capacity (MVA) | 1 | CAZLoad transfer capacity (MVA)1 | 7.4 | [11 empty] | Bellerive | Summer
CAZ | Load transfer capacity (MVA) | 2 | CAZLoad transfer capacity (MVA)2 | 7.4 | [11 empty] | Rokeby | Summer
CAZ | Load transfer capacity (MVA) | 3 | CAZLoad transfer capacity (MVA)3 | [13 empty] | Summer
CAZ | Load transfer capacity (MVA) | 4 | CAZLoad transfer capacity (MVA)4 | [13 empty] | Summer
CAZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CAZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.794 | [12 empty] | Summer
CAZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CAZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
CLZ | Substation capacity (winter and summer) (MVA) | Total | CLZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
CLZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CLZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
CLZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CLZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | Summer
CLZ | Sub-transmission lines capacity | Total (winter) | CLZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 |  | Summer
CLZ | Sub-transmission lines capacity | Firm delivery (winter) | CLZSub-transmission lines capacityFirm delivery (winter) | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 |  | Summer
CLZ | Sub-transmission lines capacity | Total (summer) | CLZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 |  | Summer
CLZ | Sub-transmission lines capacity | Firm delivery (summer) | CLZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  | Summer
CLZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(peak season)Maximum demand (MVA) | 22.118 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 |  | Summer
CLZ | Maximum demand forecast(peak season) | Power factor (coincident) | CLZMaximum demand forecast(peak season)Power factor (coincident) | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 |  | Summer
CLZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.6915 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 |  | Summer
CLZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CLZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 |  | Summer
CLZ | Hours exceeding | 95% of maximum demand | CLZHours exceeding95% of maximum demand | 1.5 | [12 empty] | Summer
CLZ | Load transfer capacity (MVA) | 1 | CLZLoad transfer capacity (MVA)1 | 4.2 | [11 empty] | Bridgewater | Summer
CLZ | Load transfer capacity (MVA) | 2 | CLZLoad transfer capacity (MVA)2 | 5.9 | [11 empty] | Chapel Street | Summer
CLZ | Load transfer capacity (MVA) | 3 | CLZLoad transfer capacity (MVA)3 | 0.8 | [11 empty] | New Norfolk | Summer
CLZ | Load transfer capacity (MVA) | 4 | CLZLoad transfer capacity (MVA)4 | [13 empty] | Summer
CLZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CLZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.318 | [12 empty] | Summer
CLZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CLZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
DPZ | Substation capacity (winter and summer) (MVA) | Total | DPZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 |  | Summer
DPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | DPZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
DPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
DPZ | Sub-transmission lines capacity | Total (winter) | DPZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 |  | Summer
DPZ | Sub-transmission lines capacity | Firm delivery (winter) | DPZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 |  | Summer
DPZ | Sub-transmission lines capacity | Total (summer) | DPZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 |  | Summer
DPZ | Sub-transmission lines capacity | Firm delivery (summer) | DPZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  | Summer
DPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(peak season)Maximum demand (MVA) | 19.1852 | 18.729 | 18.729 | 19.3124 | 19.6894 | 20.0474 | 20.1763 | 20.3339 | 20.559 | 20.97 | 22.0025 | 22.9386 |  | Summer
DPZ | Maximum demand forecast(peak season) | Power factor (coincident) | DPZMaximum demand forecast(peak season)Power factor (coincident) | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 | 0.98066 |  | Summer
DPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.9504 | 18.1439 | 18.1439 | 18.4202 | 19.0752 | 19.5339 | 19.6335 | 19.7377 | 19.8944 | 20.5274 | 21.8448 | 23.1634 |  | Summer
DPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | DPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 |  | Summer
DPZ | Hours exceeding | 95% of maximum demand | DPZHours exceeding95% of maximum demand | 5.5 | [12 empty] | Summer
DPZ | Load transfer capacity (MVA) | 1 | DPZLoad transfer capacity (MVA)1 | 13.9 | [11 empty] | Chapel Street | Summer
DPZ | Load transfer capacity (MVA) | 2 | DPZLoad transfer capacity (MVA)2 | 9.4 | [11 empty] | New Town | Summer
DPZ | Load transfer capacity (MVA) | 3 | DPZLoad transfer capacity (MVA)3 | [13 empty] | Summer
DPZ | Load transfer capacity (MVA) | 4 | DPZLoad transfer capacity (MVA)4 | [13 empty] | Summer
DPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | DPZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.786 | 0.786 | [11 empty] | Summer
DPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
EHZ | Substation capacity (winter and summer) (MVA) | Total | EHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Summer
EHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | EHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
EHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | Summer
EHZ | Sub-transmission lines capacity | Total (winter) | EHZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | Summer
EHZ | Sub-transmission lines capacity | Firm delivery (winter) | EHZSub-transmission lines capacityFirm delivery (winter) | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 |  | Summer
EHZ | Sub-transmission lines capacity | Total (summer) | EHZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 |  | Summer
EHZ | Sub-transmission lines capacity | Firm delivery (summer) | EHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 |  | Summer
EHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(peak season)Maximum demand (MVA) | 29.2574 | 27.121 | 27.121 | 27.9658 | 28.5118 | 29.0302 | 29.2169 | 29.4451 | 29.771 | 30.3662 | 31.8613 | 33.2169 |  | Summer
EHZ | Maximum demand forecast(peak season) | Power factor (coincident) | EHZMaximum demand forecast(peak season)Power factor (coincident) | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 | 0.97304 |  | Summer
EHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 23.8662 | 26.0751 | 26.0751 | 26.4722 | 27.4134 | 28.0726 | 28.2159 | 28.3656 | 28.5908 | 29.5005 | 31.3937 | 33.2888 |  | Summer
EHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | EHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 | 0.97267 |  | Summer
EHZ | Hours exceeding | 95% of maximum demand | EHZHours exceeding95% of maximum demand | 16 | [12 empty] | Summer
EHZ | Load transfer capacity (MVA) | 1 | EHZLoad transfer capacity (MVA)1 | 4.3 | [11 empty] | Geilston Bay | Summer
EHZ | Load transfer capacity (MVA) | 2 | EHZLoad transfer capacity (MVA)2 | 9.9 | [11 empty] | North Hobart | Summer
EHZ | Load transfer capacity (MVA) | 3 | EHZLoad transfer capacity (MVA)3 | 11.3 | [11 empty] | West Hobart | Summer
EHZ | Load transfer capacity (MVA) | 4 | EHZLoad transfer capacity (MVA)4 | [13 empty] | Summer
EHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | EHZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.356 | [12 empty] | Summer
EHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | EHZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
GBZ | Substation capacity (winter and summer) (MVA) | Total | GBZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 |  | Summer
GBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GBZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
GBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
GBZ | Sub-transmission lines capacity | Total (winter) | GBZSub-transmission lines capacityTotal (winter) | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 |  | Summer
GBZ | Sub-transmission lines capacity | Firm delivery (winter) | GBZSub-transmission lines capacityFirm delivery (winter) | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 |  | Summer
GBZ | Sub-transmission lines capacity | Total (summer) | GBZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | Summer
GBZ | Sub-transmission lines capacity | Firm delivery (summer) | GBZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  | Summer
GBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(peak season)Maximum demand (MVA) | 19.0827 | 18.8139 | 18.8139 | 19.4 | 19.7787 | 20.1383 | 20.2678 | 20.4262 | 20.6522 | 21.0651 | 22.1022 | 23.0426 |  | Summer
GBZ | Maximum demand forecast(peak season) | Power factor (coincident) | GBZMaximum demand forecast(peak season)Power factor (coincident) | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 |  | Summer
GBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 10.354 | 18.3822 | 18.3822 | 18.6622 | 19.3257 | 19.7904 | 19.8914 | 19.997 | 20.1557 | 20.797 | 22.1317 | 23.4677 |  | Summer
GBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983 |  | Summer
GBZ | Hours exceeding | 95% of maximum demand | GBZHours exceeding95% of maximum demand | 1.5 | [12 empty] | Summer
GBZ | Load transfer capacity (MVA) | 1 | GBZLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Bellerive | Summer
GBZ | Load transfer capacity (MVA) | 2 | GBZLoad transfer capacity (MVA)2 | 5.1 | [11 empty] | Derwent Park | Summer
GBZ | Load transfer capacity (MVA) | 3 | GBZLoad transfer capacity (MVA)3 | 3.8 | [11 empty] | West Hobart | Summer
GBZ | Load transfer capacity (MVA) | 4 | GBZLoad transfer capacity (MVA)4 | [13 empty] | Summer
GBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GBZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.491 | [12 empty] | Summer
GBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GBZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
GRZ | Substation capacity (winter and summer) (MVA) | Total | GRZSubstation capacity (winter and summer) (MVA)Total | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | Winter
GRZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GRZSubstation capacity (winter and summer) (MVA)Firm delivery | 1 | 1 | [11 empty] | Winter | bar: 2024 to 2033
GRZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GRZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 |  | Winter
GRZ | Sub-transmission lines capacity | Total (winter) | GRZSub-transmission lines capacityTotal (winter) | [13 empty] | Winter
GRZ | Sub-transmission lines capacity | Firm delivery (winter) | GRZSub-transmission lines capacityFirm delivery (winter) | [13 empty] | Winter
GRZ | Sub-transmission lines capacity | Total (summer) | GRZSub-transmission lines capacityTotal (summer) | [13 empty] | Winter
GRZ | Sub-transmission lines capacity | Firm delivery (summer) | GRZSub-transmission lines capacityFirm delivery (summer) | [13 empty] | Winter
GRZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(peak season)Maximum demand (MVA) | 1.9864 | 1.0903 | 1.0903 | 1.1069 | 1.1463 | 1.1739 | 1.1799 | 1.1861 | 1.1955 | 1.2336 | 1.3127 | 1.392 |  | Winter
GRZ | Maximum demand forecast(peak season) | Power factor (coincident) | GRZMaximum demand forecast(peak season)Power factor (coincident) | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 | 0.90942 |  | Winter
GRZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.31302 | 0.27031 | 0.27031 | 0.27873 | 0.28417 | 0.28934 | 0.2912 | 0.29347 | 0.29672 | 0.30265 | 0.31756 | 0.33107 |  | Winter
GRZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GRZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 | 0.98037 |  | Winter
GRZ | Hours exceeding | 95% of maximum demand | GRZHours exceeding95% of maximum demand | 0.5 | [12 empty] | Winter
GRZ | Load transfer capacity (MVA) | 1 | GRZLoad transfer capacity (MVA)1 | [13 empty] | Winter
GRZ | Load transfer capacity (MVA) | 2 | GRZLoad transfer capacity (MVA)2 | [13 empty] | Winter
GRZ | Load transfer capacity (MVA) | 3 | GRZLoad transfer capacity (MVA)3 | [13 empty] | Winter
GRZ | Load transfer capacity (MVA) | 4 | GRZLoad transfer capacity (MVA)4 | [13 empty] | Winter
GRZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GRZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.116 | [12 empty] | Winter
GRZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GRZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Winter
HOZ | Substation capacity (winter and summer) (MVA) | Total | HOZSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
HOZ | Substation capacity (winter and summer) (MVA) | Firm delivery | HOZSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
HOZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HOZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 |  | Summer
HOZ | Sub-transmission lines capacity | Total (winter) | HOZSub-transmission lines capacityTotal (winter) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 |  | Summer
HOZ | Sub-transmission lines capacity | Firm delivery (winter) | HOZSub-transmission lines capacityFirm delivery (winter) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 |  | Summer
HOZ | Sub-transmission lines capacity | Total (summer) | HOZSub-transmission lines capacityTotal (summer) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 |  | Summer
HOZ | Sub-transmission lines capacity | Firm delivery (summer) | HOZSub-transmission lines capacityFirm delivery (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 |  | Summer
HOZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(peak season)Maximum demand (MVA) | 21.2816 | 21.8542 | 21.8542 | 22.5349 | 22.9749 | 23.3926 | 23.543 | 23.7269 | 23.9896 | 24.4691 | 25.6739 | 26.7662 |  | Summer
HOZ | Maximum demand forecast(peak season) | Power factor (coincident) | HOZMaximum demand forecast(peak season)Power factor (coincident) | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 |  | Summer
HOZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.0396 | 19.0879 | 19.0879 | 19.3786 | 20.0676 | 20.5502 | 20.655 | 20.7646 | 20.9295 | 21.5954 | 22.9813 | 24.3686 |  | Summer
HOZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | HOZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 | 0.99857 |  | Summer
HOZ | Hours exceeding | 95% of maximum demand | HOZHours exceeding95% of maximum demand | 1.5 | [12 empty] | Summer
HOZ | Load transfer capacity (MVA) | 1 | HOZLoad transfer capacity (MVA)1 | 2.4 | [11 empty] | Bellerive | Summer
HOZ | Load transfer capacity (MVA) | 2 | HOZLoad transfer capacity (MVA)2 | 7.1 | [11 empty] | Rokeby | Summer
HOZ | Load transfer capacity (MVA) | 3 | HOZLoad transfer capacity (MVA)3 | [13 empty] | Summer
HOZ | Load transfer capacity (MVA) | 4 | HOZLoad transfer capacity (MVA)4 | [13 empty] | Summer
HOZ | Embedded generation capacity (MVA) | Units less than 100 kVA | HOZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.905 | [12 empty] | Summer
HOZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | HOZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
NTZ | Substation capacity (winter and summer) (MVA) | Total | NTZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
NTZ | Substation capacity (winter and summer) (MVA) | Firm delivery | NTZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
NTZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  | Summer
NTZ | Sub-transmission lines capacity | Total (winter) | NTZSub-transmission lines capacityTotal (winter) | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 |  | Summer
NTZ | Sub-transmission lines capacity | Firm delivery (winter) | NTZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 |  | Summer
NTZ | Sub-transmission lines capacity | Total (summer) | NTZSub-transmission lines capacityTotal (summer) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 |  | Summer
NTZ | Sub-transmission lines capacity | Firm delivery (summer) | NTZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  | Summer
NTZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(peak season)Maximum demand (MVA) | 22.067 | 21.6125 | 21.6125 | 22.2857 | 24.2697 | 24.7109 | 24.8698 | 25.0641 | 25.3415 | 25.8481 | 27.1207 | 28.2747 |  | Summer
NTZ | Maximum demand forecast(peak season) | Power factor (coincident) | NTZMaximum demand forecast(peak season)Power factor (coincident) | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 | 0.99063 |  | Summer
NTZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 17.1169 | 22.5695 | 22.5695 | 22.9132 | 25.4887 | 26.1016 | 26.2348 | 26.374 | 26.5834 | 27.4292 | 29.1895 | 30.9515 |  | Summer
NTZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | NTZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 | 0.98946 |  | Summer
NTZ | Hours exceeding | 95% of maximum demand | NTZHours exceeding95% of maximum demand | 12.5 | [12 empty] | Summer
NTZ | Load transfer capacity (MVA) | 1 | NTZLoad transfer capacity (MVA)1 | 3.9 | [11 empty] | Chapel Street | Summer
NTZ | Load transfer capacity (MVA) | 2 | NTZLoad transfer capacity (MVA)2 | 4.8 | [11 empty] | Derwent Park | Summer
NTZ | Load transfer capacity (MVA) | 3 | NTZLoad transfer capacity (MVA)3 | 3.9 | [11 empty] | East Hobart | Summer
NTZ | Load transfer capacity (MVA) | 4 | NTZLoad transfer capacity (MVA)4 | 7.7 | [11 empty] | North Hobart | Summer
NTZ | Embedded generation capacity (MVA) | Units less than 100 kVA | NTZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.446 | [12 empty] | Summer
NTZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
RIZ | Substation capacity (winter and summer) (MVA) | Total | RIZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | Summer
RIZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RIZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Summer
RIZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RIZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 |  | Summer
RIZ | Sub-transmission lines capacity | Total (winter) | RIZSub-transmission lines capacityTotal (winter) | [13 empty] | Summer
RIZ | Sub-transmission lines capacity | Firm delivery (winter) | RIZSub-transmission lines capacityFirm delivery (winter) | [13 empty] | Summer
RIZ | Sub-transmission lines capacity | Total (summer) | RIZSub-transmission lines capacityTotal (summer) | [13 empty] | Summer
RIZ | Sub-transmission lines capacity | Firm delivery (summer) | RIZSub-transmission lines capacityFirm delivery (summer) | [13 empty] | Summer
RIZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | RIZMaximum demand forecast(peak season)Maximum demand (MVA) | 3.8639 | 3.6172 | 5.2913 | 3.7298 | 3.8027 | 3.8718 | 3.8967 | 3.9271 | 3.9706 | 4.05 | 4.2494 | 4.4302 |  | Summer
RIZ | Maximum demand forecast(peak season) | Power factor (coincident) | RIZMaximum demand forecast(peak season)Power factor (coincident) | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 |  | Summer
RIZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RIZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 2.3693 | 2.9973 | 4.9005 | 3.0429 | 3.1511 | 3.2269 | 3.2434 | 3.2606 | 3.2865 | 3.391 | 3.6087 | 3.8265 |  | Summer
RIZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RIZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 | 0.98547 |  | Summer
RIZ | Hours exceeding | 95% of maximum demand | RIZHours exceeding95% of maximum demand | 8.5 | [12 empty] | Summer
RIZ | Load transfer capacity (MVA) | 1 | RIZLoad transfer capacity (MVA)1 | [13 empty] | Summer
RIZ | Load transfer capacity (MVA) | 2 | RIZLoad transfer capacity (MVA)2 | [13 empty] | Summer
RIZ | Load transfer capacity (MVA) | 3 | RIZLoad transfer capacity (MVA)3 | [13 empty] | Summer
RIZ | Load transfer capacity (MVA) | 4 | RIZLoad transfer capacity (MVA)4 | [13 empty] | Summer
RIZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RIZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.706 | [12 empty] | Summer
RIZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
RPZ | Substation capacity (winter and summer) (MVA) | Total | RPZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
RPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RPZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RPZ | Sub-transmission lines capacity | Total (winter) | RPZSub-transmission lines capacityTotal (winter) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 |  | Summer
RPZ | Sub-transmission lines capacity | Firm delivery (winter) | RPZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RPZ | Sub-transmission lines capacity | Total (summer) | RPZSub-transmission lines capacityTotal (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 |  | Summer
RPZ | Sub-transmission lines capacity | Firm delivery (summer) | RPZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
RPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(peak season)Maximum demand (MVA) | 15.1503 | 15.0204 | 15.0204 | 15.4882 | 15.7906 | 16.0777 | 16.1811 | 16.3075 | 16.488 | 16.8176 | 17.6457 | 18.3964 |  | Summer
RPZ | Maximum demand forecast(peak season) | Power factor (coincident) | RPZMaximum demand forecast(peak season)Power factor (coincident) | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 |  | Summer
RPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 9.8715 | 11.3639 | 11.3639 | 11.537 | 11.9472 | 12.2345 | 12.2969 | 12.3622 | 12.4603 | 12.8568 | 13.6819 | 14.5078 |  | Summer
RPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 | 0.99992 |  | Summer
RPZ | Hours exceeding | 95% of maximum demand | RPZHours exceeding95% of maximum demand | 7 | [12 empty] | Summer
RPZ | Load transfer capacity (MVA) | 1 | RPZLoad transfer capacity (MVA)1 | [13 empty] | Summer
RPZ | Load transfer capacity (MVA) | 2 | RPZLoad transfer capacity (MVA)2 | [13 empty] | Summer
RPZ | Load transfer capacity (MVA) | 3 | RPZLoad transfer capacity (MVA)3 | [13 empty] | Summer
RPZ | Load transfer capacity (MVA) | 4 | RPZLoad transfer capacity (MVA)4 | [13 empty] | Summer
RPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RPZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.342 | [12 empty] | Summer
RPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RPZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
SBZ | Substation capacity (winter and summer) (MVA) | Total | SBZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Summer
SBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SBZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
SBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | Summer
SBZ | Sub-transmission lines capacity | Total (winter) | SBZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | Summer
SBZ | Sub-transmission lines capacity | Firm delivery (winter) | SBZSub-transmission lines capacityFirm delivery (winter) | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 |  | Summer
SBZ | Sub-transmission lines capacity | Total (summer) | SBZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 |  | Summer
SBZ | Sub-transmission lines capacity | Firm delivery (summer) | SBZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 |  | Summer
SBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(peak season)Maximum demand (MVA) | 39.248 | 37.7031 | 39.5781 | 38.8775 | 39.6366 | 40.3572 | 40.6168 | 40.934 | 41.3871 | 42.2144 | 44.2929 | 46.1774 |  | Summer
SBZ | Maximum demand forecast(peak season) | Power factor (coincident) | SBZMaximum demand forecast(peak season)Power factor (coincident) | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 | 0.99933 |  | Summer
SBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 18.7989 | 36.1425 | 38.2741 | 36.6929 | 37.9975 | 38.9113 | 39.1098 | 39.3174 | 39.6295 | 40.8904 | 43.5146 | 46.1413 |  | Summer
SBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 | 0.99611 |  | Summer
SBZ | Hours exceeding | 95% of maximum demand | SBZHours exceeding95% of maximum demand | 3 | [12 empty] | Summer
SBZ | Load transfer capacity (MVA) | 1 | SBZLoad transfer capacity (MVA)1 | 1.7 | [11 empty] | Kingston | Summer
SBZ | Load transfer capacity (MVA) | 2 | SBZLoad transfer capacity (MVA)2 | 13.2 | [11 empty] | West Hobart | Summer
SBZ | Load transfer capacity (MVA) | 3 | SBZLoad transfer capacity (MVA)3 | [13 empty] | Summer
SBZ | Load transfer capacity (MVA) | 4 | SBZLoad transfer capacity (MVA)4 | [13 empty] | Summer
SBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SBZEmbedded generation capacity (MVA)Units less than 100 kVA | 3.212 | 3.212 | [11 empty] | Summer
SBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SBZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
SUZ | Substation capacity (winter and summer) (MVA) | Total | SUZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
SUZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SUZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SUZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SUZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SUZ | Sub-transmission lines capacity | Total (winter) | SUZSub-transmission lines capacityTotal (winter) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 |  | Summer
SUZ | Sub-transmission lines capacity | Firm delivery (winter) | SUZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SUZ | Sub-transmission lines capacity | Total (summer) | SUZSub-transmission lines capacityTotal (summer) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 |  | Summer
SUZ | Sub-transmission lines capacity | Firm delivery (summer) | SUZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
SUZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(peak season)Maximum demand (MVA) | 12.055 | 11.2897 | 11.2897 | 11.6414 | 11.8687 | 12.0844 | 12.1622 | 12.2572 | 12.3928 | 12.6406 | 13.2629 | 13.8272 |  | Summer
SUZ | Maximum demand forecast(peak season) | Power factor (coincident) | SUZMaximum demand forecast(peak season)Power factor (coincident) | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 | 0.99956 |  | Summer
SUZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 5.7946 | 7.5904 | 7.5904 | 7.706 | 7.98 | 8.1719 | 8.2136 | 8.2572 | 8.3228 | 8.5876 | 9.1387 | 9.6903 |  | Summer
SUZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SUZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 | 0.99911 |  | Summer
SUZ | Hours exceeding | 95% of maximum demand | SUZHours exceeding95% of maximum demand | 2.5 | [12 empty] | Summer
SUZ | Load transfer capacity (MVA) | 1 | SUZLoad transfer capacity (MVA)1 | 4.9 | [11 empty] | Kingston | Summer
SUZ | Load transfer capacity (MVA) | 2 | SUZLoad transfer capacity (MVA)2 | [13 empty] | Summer
SUZ | Load transfer capacity (MVA) | 3 | SUZLoad transfer capacity (MVA)3 | [13 empty] | Summer
SUZ | Load transfer capacity (MVA) | 4 | SUZLoad transfer capacity (MVA)4 | [13 empty] | Summer
SUZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SUZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.311 | [12 empty] | Summer
SUZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SUZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
THZ | Substation capacity (winter and summer) (MVA) | Total | THZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Summer
THZ | Substation capacity (winter and summer) (MVA) | Firm delivery | THZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Summer
THZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | THZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | Summer
THZ | Sub-transmission lines capacity | Total (winter) | THZSub-transmission lines capacityTotal (winter) | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 |  | Summer
THZ | Sub-transmission lines capacity | Firm delivery (winter) | THZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
THZ | Sub-transmission lines capacity | Total (summer) | THZSub-transmission lines capacityTotal (summer) | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 |  | Summer
THZ | Sub-transmission lines capacity | Firm delivery (summer) | THZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
THZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | THZMaximum demand forecast(peak season)Maximum demand (MVA) | 3.1466 | 2.5009 | 1.2286 | 2.5788 | 2.6292 | 2.677 | 2.6942 | 2.7152 | 2.7453 | 2.8002 | 2.938 | 3.0631 |  | Summer
THZ | Maximum demand forecast(peak season) | Power factor (coincident) | THZMaximum demand forecast(peak season)Power factor (coincident) | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 | 0.75751 |  | Summer
THZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | THZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 2.2437 | 7.5744 | 6.128 | 7.6898 | 7.9632 | 8.1547 | 8.1963 | 8.2398 | 8.3052 | 8.5695 | 9.1194 | 9.6699 |  | Summer
THZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | THZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 | 0.90922 |  | Summer
THZ | Hours exceeding | 95% of maximum demand | THZHours exceeding95% of maximum demand | 7 | [12 empty] | Summer
THZ | Load transfer capacity (MVA) | 1 | THZLoad transfer capacity (MVA)1 | [13 empty] | Summer
THZ | Load transfer capacity (MVA) | 2 | THZLoad transfer capacity (MVA)2 | [13 empty] | Summer
THZ | Load transfer capacity (MVA) | 3 | THZLoad transfer capacity (MVA)3 | [13 empty] | Summer
THZ | Load transfer capacity (MVA) | 4 | THZLoad transfer capacity (MVA)4 | [13 empty] | Summer
THZ | Embedded generation capacity (MVA) | Units less than 100 kVA | THZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.11 | [12 empty] | Summer
THZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | THZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
WHZ | Substation capacity (winter and summer) (MVA) | Total | WHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Summer
WHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Summer
WHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | Summer
WHZ | Sub-transmission lines capacity | Total (winter) | WHZSub-transmission lines capacityTotal (winter) | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 |  | Summer
WHZ | Sub-transmission lines capacity | Firm delivery (winter) | WHZSub-transmission lines capacityFirm delivery (winter) | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 |  | Summer
WHZ | Sub-transmission lines capacity | Total (summer) | WHZSub-transmission lines capacityTotal (summer) | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 |  | Summer
WHZ | Sub-transmission lines capacity | Firm delivery (summer) | WHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 |  | Summer
WHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(peak season)Maximum demand (MVA) | 37.7186 | 37.243 | 37.243 | 38.4031 | 39.1529 | 39.8647 | 40.1211 | 40.4345 | 40.8821 | 41.6993 | 43.7524 | 45.6139 |  | Summer
WHZ | Maximum demand forecast(peak season) | Power factor (coincident) | WHZMaximum demand forecast(peak season)Power factor (coincident) | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 | 0.99782 |  | Summer
WHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 26.2904 | 27.7002 | 27.7002 | 28.1221 | 29.1219 | 29.8222 | 29.9744 | 30.1335 | 30.3727 | 31.339 | 33.3503 | 35.3634 |  | Summer
WHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 | 0.99855 |  | Summer
WHZ | Hours exceeding | 95% of maximum demand | WHZHours exceeding95% of maximum demand | 1 | [12 empty] | Summer
WHZ | Load transfer capacity (MVA) | 1 | WHZLoad transfer capacity (MVA)1 | 8.5 | [11 empty] | East Hobart | Summer
WHZ | Load transfer capacity (MVA) | 2 | WHZLoad transfer capacity (MVA)2 | 6.4 | [11 empty] | North Hobart | Summer
WHZ | Load transfer capacity (MVA) | 3 | WHZLoad transfer capacity (MVA)3 | 8.5 | [11 empty] | Sandy Bay | Summer
WHZ | Load transfer capacity (MVA) | 4 | WHZLoad transfer capacity (MVA)4 | [13 empty] | Summer
WHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WHZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.957 | [12 empty] | Summer
WHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WHZEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.1 | [12 empty] | Summer
WYZ | Substation capacity (winter and summer) (MVA) | Total | WYZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | Summer
WYZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WYZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |  | Summer
WYZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WYZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | Summer
WYZ | Sub-transmission lines capacity | Total (winter) | WYZSub-transmission lines capacityTotal (winter) | [13 empty] | Summer
WYZ | Sub-transmission lines capacity | Firm delivery (winter) | WYZSub-transmission lines capacityFirm delivery (winter) | [13 empty] | Summer
WYZ | Sub-transmission lines capacity | Total (summer) | WYZSub-transmission lines capacityTotal (summer) | [13 empty] | Summer
WYZ | Sub-transmission lines capacity | Firm delivery (summer) | WYZSub-transmission lines capacityFirm delivery (summer) | [13 empty] | Summer
WYZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(peak season)Maximum demand (MVA) | 1.1687 | 1.2821 | 1.2821 | 1.322 | 1.3479 | 1.3724 | 1.3812 | 1.392 | 1.4074 | 1.4355 | 1.5062 | 1.5703 |  | Summer
WYZ | Maximum demand forecast(peak season) | Power factor (coincident) | WYZMaximum demand forecast(peak season)Power factor (coincident) | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 | 0.95562 |  | Summer
WYZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.2223 | 1.6743 | 1.6743 | 1.6998 | 1.7602 | 1.8025 | 1.8117 | 1.8213 | 1.8358 | 1.8942 | 2.0158 | 2.1374 |  | Summer
WYZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WYZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 | 0.96549 |  | Summer
WYZ | Hours exceeding | 95% of maximum demand | WYZHours exceeding95% of maximum demand | 5.5 | [12 empty] | Summer
WYZ | Load transfer capacity (MVA) | 1 | WYZLoad transfer capacity (MVA)1 | [13 empty] | Summer
WYZ | Load transfer capacity (MVA) | 2 | WYZLoad transfer capacity (MVA)2 | [13 empty] | Summer
WYZ | Load transfer capacity (MVA) | 3 | WYZLoad transfer capacity (MVA)3 | [13 empty] | Summer
WYZ | Load transfer capacity (MVA) | 4 | WYZLoad transfer capacity (MVA)4 | [13 empty] | Summer
WYZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WYZEmbedded generation capacity (MVA)Units less than 100 kVA | [13 empty] | Summer
WYZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WYZEmbedded generation capacity (MVA)Units greater than 100 kVA | [13 empty] | Summer
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculate

## Zone info
| Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Non-Peaking Season | Substation |  |  | Sub-transmission feeders | Source substation | Substation | Comment | Zone | hours above 95% of MD
BEZ | Bellerive | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Bellerive | 1 | Bellerive1 | 25305 | Lindisfarne | Bellerive | [1] We propose to replace the supply transformers due to asset condition in 2028 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Load reduction following transfer of load to new Rosny Park Zone Substation, as detailed in chapter 6 of this APR. | BEZ | 3
CAZ | Cambridge | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Bellerive | 2 | Bellerive2 | 25310 | Lindisfarne | Claremont | [1] We propose to replace the supply transformers due to asset condition in 2020 with new units of standard size, as detailed in Section 6.9.3 of this APR. | CAZ | 11
CLZ | Claremont | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Bellerive | 3 | Bellerive3 |  |  | Derwent Park | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Currently in summer, and from 2024 in winter, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. | CLZ | 1.5
DPZ | Derwent Park | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Cambridge | 1 | Cambridge1 | 25309 | Lindisfarne | East Hobart | [1] From summer 2018, load is forecast to exceed the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. | DPZ | 5.5
EHZ | East Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Summer | Cambridge | 2 | Cambridge2 | 24402 | Mornington | Geilston Bay | [1] We propose to replace the supply transformers due to asset condition in 2027 with new units of standard size, as detailed in Section 4.9 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. | EHZ | 16
GBZ | Geilston Bay | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Cambridge | 3 | Cambridge3 |  |  | Howrah | [1] From this data, the load at Howrah Zone has currently exceeds the firm rating of the sub-transmission lines. However we believe the assigned rating of these lines are overly conservative and are currently investigating this. Therefore this has not been identified as a constraint in this APR. | GBZ | 1.5
HOZ | Howrah | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Claremont | 1 | Claremont1 | 10007 | Creek Road | New Town | [1] Currently in summer, and in winter from 2024, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. [1] We propose to replace the supply transformers due to asset condition in 2022 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. | HOZ | 1.5
NTZ | New Town | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Summer | Claremont | 2 | Claremont2 | 10026 | Creek Road | Trial Harbour | [1] Load forecast step increase in 2018 from point load increase. | NTZ | 12.5
RPZ | Rosny Park | Greater Hobart | Distribution lines | 33/11 kV | 1 | Winter | Summer | Claremont | 3 | Claremont3 |  |  | Gretna rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. | RPZ | 7
SBZ | Sandy Bay | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Summer | Derwent Park | 1 | Derwent Park1 | 11021 | Risdon | New Norfolk rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] We propose to replace and rationalise the supply transformers due to asset condition in by 2019 with new 3 x 5 MVA units of standard size. | SBZ | 3
SUZ | Summerleas | Kingston-South | Distribution lines | 33/11 kV | 1 | Winter | Summer | Derwent Park | 2 | Derwent Park2 | 11025 | Risdon | Richmond rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] The supply transformers replacement is a committed project to commission in 2023 with new 2 x 5 MVA units of standard size. [3] Load currently exceeds the firm rating of the substation, however fast, remote load transfers exist to manage this. This has not been identified as a constraint in this APR. | SUZ | 2.5
THZ | Trial Harbour | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Summer | Derwent Park | 3 | Derwent Park3 |  |  | Wayatinah rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. | THZ | 7
WHZ | West Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Summer | East Hobart | 1 | East Hobart1 | 11004 | Risdon |  |  | WHZ | 1
GRZ | Gretna rural | Central | Distribution lines | 22/11 kV | 1 | Summer | Winter | East Hobart | 2 | East Hobart2 | 11005 | Risdon |  |  | GRZ | 0.5
RIZ | Richmond rural | Eastern | Distribution lines | 22/11 kV | 2 | Winter | Summer | East Hobart | 3 | East Hobart3 | 11006 | Risdon |  |  | NNZ | #N/A
WYZ | Wayatinah rural | Central | Distribution lines | 11/22 kV | 1 | Winter | Summer | Geilston Bay | 1 | Geilston Bay1 | 25307 | Lindisfarne |  |  | RIZ | 8.5
[8 empty] | Geilston Bay | 2 | Geilston Bay2 | 25308 | Lindisfarne |  |  | WYZ | 5.5
[8 empty] | Geilston Bay | 3 | Geilston Bay3
[8 empty] | Howrah | 1 | Howrah1 | 24401 | Mornington
[8 empty] | Howrah | 2 | Howrah2 | 24406 | Mornington
[8 empty] | Howrah | 3 | Howrah3
[8 empty] | New Town | 1 | New Town1 | 11023 | Risdon
[8 empty] | New Town | 2 | New Town2 | 11027 | Risdon
[8 empty] | New Town | 3 | New Town3
[8 empty] | Rosny Park | 1 | Rosny Park1 | 24405 | Mornington
[8 empty] | Rosny Park | 2 | Rosny Park2
[8 empty] | Rosny Park | 3 | Rosny Park3
[8 empty] | Sandy Bay | 1 | Sandy Bay1 | 10008 | Creek Road
[8 empty] | Sandy Bay | 2 | Sandy Bay2 | 10022 | Creek Road
[8 empty] | Sandy Bay | 3 | Sandy Bay3 | 10024 | Creek Road
[8 empty] | Summerleas | 1 | Summerleas1 | 36240 | Kingston
[8 empty] | Summerleas | 2 | Summerleas2
[8 empty] | Summerleas | 3 | Summerleas3
[8 empty] | Trial Harbour | 1 | Trial Harbour1 | 97013 | 50[1]
[8 empty] | Trial Harbour | 2 | Trial Harbour2
[8 empty] | Trial Harbour | 3 | Trial Harbour3
[8 empty] | West Hobart | 1 | West Hobart1 | 10001 | Creek Road
Bellerive | BEZ | [6 empty] | West Hobart | 2 | West Hobart2 | 10002 | Creek Road
Cambridge | CAZ | [6 empty] | West Hobart | 3 | West Hobart3 | 10003 | Creek Road
Claremont | CLZ | [6 empty] | Gretna rural | 1 | Gretna rural1 | [1]
Derwent Park | DPZ | [6 empty] | Gretna rural | 2 | Gretna rural2
East Hobart | EHZ | [6 empty] | Gretna rural | 3 | Gretna rural3
Geilston Bay | GBZ | [6 empty] | New Norfolk rural | 1 | New Norfolk rural1 | [1]
Howrah | HOZ | [6 empty] | New Norfolk rural | 2 | New Norfolk rural2
New Town | NTZ | [6 empty] | New Norfolk rural | 3 | New Norfolk rural3
Rosny Park | RPZ | [6 empty] | Richmond rural | 1 | Richmond rural1 | [1]
Sandy Bay | SBZ | [6 empty] | Richmond rural | 2 | Richmond rural2
Summerleas | SUZ | [6 empty] | Richmond rural | 3 | Richmond rural3
Trial Harbour | THZ | [6 empty] | Wayatinah rural | 1 | Wayatinah rural1 | [1]
West Hobart | WHZ | [6 empty] | Wayatinah rural | 2 | Wayatinah rural2
Gretna rural | GRZ | [6 empty] | Wayatinah rural | 3 | Wayatinah rural3
Richmond rural | RIZ
Wayatinah rural | WYZ

## Substation DER
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26
[8 empty] | NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [10 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Substation | Abbreviation | [6 empty] | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
0 | [7 empty] | 1.8576 | 3.1313 | 4.6455 | 6.3838 | 8.213 | 10.2811 | 12.6303 | 17.7702 | 22.0962 | 26.184 |  | -13.8169 | -16.6384 | -19.6983 | -22.6399 | -25.1841 | -27.4244 | -29.4758 | -31.4685 | -33.5737 | -35.3764
Arthurs Lake | AL | Embedded generation forecast capacity (MVA) | ALEmbedded generation forecast capacity (MVA) |  |  |  |  | 0.64963 | 0.72359 | 0.78166 | 0.83891 | 0.89536 | 0.94917 | 1.0008 | 1.0507 | 1.0986 | 1.1448 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoca | AV | Embedded generation forecast capacity (MVA) | AVEmbedded generation forecast capacity (MVA) |  |  |  |  | 229.8202 | 263.3029 | 294.3801 | 325.0065 | 354.8484 | 383.1086 | 410.0514 | 435.8071 | 460.3999 | 483.9619 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgewater | BW | Embedded generation forecast capacity (MVA) | BWEmbedded generation forecast capacity (MVA) |  |  |  |  | 2974.4873 | 3300.0833 | 3556.1955 | 3808.7784 | 4057.986 | 4295.6773 | 4524.1312 | 4744.4679 | 4956.5053 | 5161.3921 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Burnie | BU | Embedded generation forecast capacity (MVA) | BUEmbedded generation forecast capacity (MVA) |  |  |  |  | 1682.5056 | 1862.9759 | 2003.7295 | 2136.33 | 2262.8173 | 2378.9627 | 2486.3559 | 2586.1192 | 2676.9508 | 2759.8075 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | CS | Embedded generation forecast capacity (MVA) | CSEmbedded generation forecast capacity (MVA) |  |  |  |  | 1991.1388 | 2268.9419 | 2505.3563 | 2733.8643 | 2956.5449 | 3166.2394 | 3365.1137 | 3554.5277 | 3734.4091 | 3905.9659 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Creek Road | CR | Embedded generation forecast capacity (MVA) | CREmbedded generation forecast capacity (MVA) |  |  |  |  | 4567.3771 | 5158.4752 | 5631.5337 | 6090.7118 | 6538.4676 | 6960.3251 | 7360.6932 | 7742.2333 | 8104.8567 | 8450.9187 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | DE | Embedded generation forecast capacity (MVA) | DEEmbedded generation forecast capacity (MVA) |  |  |  |  | 570.2145 | 639.9426 | 705.3971 | 770.9849 | 835.2516 | 898.1035 | 959.9018 | 1020.7374 | 1080.847 | 1139.8649 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | DB | Embedded generation forecast capacity (MVA) | DBEmbedded generation forecast capacity (MVA) |  |  |  |  | 10.0513 | 11.2637 | 12.2484 | 13.23 | 14.2054 | 15.1664 | 16.1173 | 17.0633 | 18.005 | 18.9376 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Devonport | DP | Embedded generation forecast capacity (MVA) | DPEmbedded generation forecast capacity (MVA) |  |  |  |  | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | EL | Embedded generation forecast capacity (MVA) | ELEmbedded generation forecast capacity (MVA) |  |  |  |  | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay | EB | Embedded generation forecast capacity (MVA) | EBEmbedded generation forecast capacity (MVA) |  |  |  |  | 265.5134 | 293.6355 | 314.422 | 334.3744 | 353.8118 | 371.8791 | 388.8847 | 404.9452 | 420.0605 | 434.3536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fisher |  | Embedded generation forecast capacity (MVA) | Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | GT | Embedded generation forecast capacity (MVA) | GTEmbedded generation forecast capacity (MVA) |  |  |  |  | 136.5015 | 151.5159 | 165.7462 | 179.1831 | 192.1189 | 204.0912 | 215.2525 | 225.706 | 235.2999 | 244.125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gordon |  | Embedded generation forecast capacity (MVA) | Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna | GRZ | Embedded generation forecast capacity (MVA) | GRZEmbedded generation forecast capacity (MVA) |  |  |  |  | 12.6656 | 14.1833 | 15.416 | 16.6448 | 17.866 | 19.069 | 20.2593 | 21.4435 | 22.6225 | 23.7899 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hadspen | HA | Embedded generation forecast capacity (MVA) | HAEmbedded generation forecast capacity (MVA) |  |  |  |  | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | HR | Embedded generation forecast capacity (MVA) | HREmbedded generation forecast capacity (MVA) |  |  |  |  | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | KE | Embedded generation forecast capacity (MVA) | KEEmbedded generation forecast capacity (MVA) |  |  |  |  | 383.0144 | 431.113 | 470.8754 | 510.0173 | 548.559 | 585.2413 | 620.4212 | 654.2594 | 686.7421 | 718.0464 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (11kV) | KI11 | Embedded generation forecast capacity (MVA) | KI11Embedded generation forecast capacity (MVA) |  |  |  |  | 3197.5977 | 3612.887 | 3977.4075 | 4342.1369 | 4705.5296 | 5064.7637 | 5421.604 | 5777.8997 | 6133.8497 | 6487.6286 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston (33 kV) | KI33 | Embedded generation forecast capacity (MVA) | KI33Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Knights Road | KR | Embedded generation forecast capacity (MVA) | KREmbedded generation forecast capacity (MVA) |  |  |  |  | 106.283 | 119.1528 | 129.4229 | 139.2966 | 148.8434 | 157.7501 | 166.1198 | 174.0091 | 181.3041 | 188.0626 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne | LF | Embedded generation forecast capacity (MVA) | LFEmbedded generation forecast capacity (MVA) |  |  |  |  | 2512.8723 | 2866.0671 | 3139.8628 | 3408.7188 | 3672.159 | 3922.715 | 4162.3225 | 4392.3221 | 4612.6714 | 4824.5536 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | MB | Embedded generation forecast capacity (MVA) | MBEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington | MT | Embedded generation forecast capacity (MVA) | MTEmbedded generation forecast capacity (MVA) |  |  |  |  | 3597.132 | 4123.1508 | 4530.6172 | 4930.625 | 5322.4274 | 5694.9681 | 6051.1176 | 6392.8766 | 6720.1961 | 7034.8374 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mowbray | MY | Embedded generation forecast capacity (MVA) | MYEmbedded generation forecast capacity (MVA) |  |  |  |  | 1787.6644 | 1979.4335 | 2166.4847 | 2351.8779 | 2535.0288 | 2714.0391 | 2890.0886 | 3064.112 | 3236.2179 | 3405.5324 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk Terminal | NN | Embedded generation forecast capacity (MVA) | NNEmbedded generation forecast capacity (MVA) |  |  |  |  | 252.5741 | 282.1063 | 305.2396 | 327.7966 | 349.8276 | 370.6672 | 390.4942 | 409.4423 | 427.5048 | 444.7906 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | NT | Embedded generation forecast capacity (MVA) | NTEmbedded generation forecast capacity (MVA) |  |  |  |  | 0.14998 | 0.1679 | 0.1777 | 0.18725 | 0.19655 | 0.20533 | 0.21367 | 0.22162 | 0.22919 | 0.23641 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | NH | Embedded generation forecast capacity (MVA) | NHEmbedded generation forecast capacity (MVA) |  |  |  |  | 800.8598 | 905.6161 | 988.9926 | 1071.7342 | 1153.7735 | 1234.1302 | 1313.3419 | 1391.8128 | 1469.5996 | 1546.3023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | NW | Embedded generation forecast capacity (MVA) | NWEmbedded generation forecast capacity (MVA) |  |  |  |  | 1631.8478 | 1810.9378 | 1975.5555 | 2131.9918 | 2281.2469 | 2418.8879 | 2546.6736 | 2665.787 | 2774.6763 | 2874.3881 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palmerston | PM | Embedded generation forecast capacity (MVA) | PMEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Latta | PL | Embedded generation forecast capacity (MVA) | PLEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queenstown | QT | Embedded generation forecast capacity (MVA) | QTEmbedded generation forecast capacity (MVA) |  |  |  |  | 253.2898 | 283.563 | 300.1179 | 316.2359 | 331.9441 | 346.7759 | 360.8598 | 374.2889 | 387.0642 | 399.2639 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton | RA | Embedded generation forecast capacity (MVA) | RAEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Richmond | RIZ | Embedded generation forecast capacity (MVA) | RIZEmbedded generation forecast capacity (MVA) |  |  |  |  | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon | RI | Embedded generation forecast capacity (MVA) | RIEmbedded generation forecast capacity (MVA) |  |  |  |  | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | RK | Embedded generation forecast capacity (MVA) | RKEmbedded generation forecast capacity (MVA) |  |  |  |  | 3154.2152 | 3620.9045 | 3982.4067 | 4337.283 | 4684.8696 | 5015.3617 | 5331.3046 | 5634.4744 | 5924.8281 | 6203.9285 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery (22 kV) | RB22 | Embedded generation forecast capacity (MVA) | RB22Embedded generation forecast capacity (MVA) |  |  |  |  | 38.3669 | 63.9523 | 79.5141 | 94.6533 | 109.3705 | 123.2394 | 136.3824 | 148.8869 | 160.7587 | 172.072 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery (44 kV) | RB44 | Embedded generation forecast capacity (MVA) | RB44Embedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River | SR | Embedded generation forecast capacity (MVA) | SREmbedded generation forecast capacity (MVA) |  |  |  |  | 85.3539 | 95.5332 | 104.3439 | 113.0892 | 121.6936 | 130.0988 | 138.3456 | 146.4726 | 154.494 | 162.365 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scottsdale | SD | Embedded generation forecast capacity (MVA) | SDEmbedded generation forecast capacity (MVA) |  |  |  |  | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | SH | Embedded generation forecast capacity (MVA) | SHEmbedded generation forecast capacity (MVA) |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smithton | ST | Embedded generation forecast capacity (MVA) | STEmbedded generation forecast capacity (MVA) |  |  |  |  | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sorell | SO | Embedded generation forecast capacity (MVA) | SOEmbedded generation forecast capacity (MVA) |  |  |  |  | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | SL | Embedded generation forecast capacity (MVA) | SLEmbedded generation forecast capacity (MVA) |  |  |  |  | 2445.2478 | 2691.4474 | 2924.5604 | 3150.4488 | 3369.6634 | 3575.3479 | 3769.7605 | 3954.305 | 4128.9861 | 4295.0076 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | SM | Embedded generation forecast capacity (MVA) | SMEmbedded generation forecast capacity (MVA) |  |  |  |  | 1898.6453 | 2086.4955 | 2246.545 | 2406.5867 | 2565.6267 | 2721.0932 | 2874.592 | 3026.7091 | 3177.5624 | 3326.4117 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | TR | Embedded generation forecast capacity (MVA) | TREmbedded generation forecast capacity (MVA) |  |  |  |  | 3452.6345 | 3870.7926 | 4261.5278 | 4632.6151 | 4987.3204 | 5315.3177 | 5620.2699 | 5905.1422 | 6166.0336 | 6405.3899 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Triabunna | TB | Embedded generation forecast capacity (MVA) | TBEmbedded generation forecast capacity (MVA) |  |  |  |  | 314.5736 | 349.7207 | 376.9904 | 403.7344 | 429.9495 | 454.7816 | 478.4858 | 501.1987 | 522.9075 | 543.7407 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trial Harbour Road | THZ | Embedded generation forecast capacity (MVA) | THZEmbedded generation forecast capacity (MVA) |  |  |  |  | 23.0469 | 37.7745 | 46.3308 | 54.8547 | 63.3041 | 71.6151 | 79.8235 | 87.9717 | 96.0683 | 104.0691 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | TU | Embedded generation forecast capacity (MVA) | TUEmbedded generation forecast capacity (MVA) |  |  |  |  | 71.5148 | 79.8894 | 86.4482 | 92.8402 | 99.0801 | 104.9803 | 110.5911 | 115.9508 | 121.0576 | 125.9425 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ulverstone | UL | Embedded generation forecast capacity (MVA) | ULEmbedded generation forecast capacity (MVA) |  |  |  |  | 4122.7459 | 4602.4241 | 5015.6745 | 5425.9173 | 5831.1119 | 6227.4053 | 6616.9844 | 7001.8209 | 7382.3667 | 7756.573 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wayatinah | WA | Embedded generation forecast capacity (MVA) | WAEmbedded generation forecast capacity (MVA) |  |  |  |  | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wesley Vale | WV | Embedded generation forecast capacity (MVA) | WVEmbedded generation forecast capacity (MVA) |  |  |  |  | 735.0057 | 831.1439 | 921.5004 | 1010.4842 | 1097.8487 | 1181.2098 | 1261.1601 | 1338.1141 | 1412.0384 | 1483.3205 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#N/A | [7 empty] | 115.0778 | 209.4838 | 321.9403 | 451.4632 | 588.1434 | 743.0459 | 919.2364 | 1305.4575 | 1629.8736 | 1936.2611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## DERdataMAX
[16 empty] | MW | [9 empty] | kW
Index | constraint | planning_region | final_ss_code | final_name | scenario | max_min | series | coincidence | Type | season | category | subcategory | units | Transmission Customer | LoadType_MI_or_RT | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
48 | PMA | North | TAV2 | Avoca 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.22982 | 0.2633 | 0.29438 | 0.32501 | 0.35485 | 0.38311 | 0.41005 | 0.43581 | 0.4604 | 0.48396 | 229.8202 | 263.3029 | 294.3801 | 325.0065 | 354.8484 | 383.1086 | 410.0514 | 435.8071 | 460.3999 | 483.9619
48 | PMA | George Town | TSW1 | Starwood | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00064963 | 0.00072359 | 0.00078166 | 0.00083891 | 0.00089536 | 0.00094917 | 0.0010008 | 0.0010507 | 0.0010986 | 0.0011448 | 0.64963 | 0.72359 | 0.78166 | 0.83891 | 0.89536 | 0.94917 | 1.0008 | 1.0507 | 1.0986 | 1.1448
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | BEZ | Bellerive | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.0428 | 1.1957 | 1.3141 | 1.4303 | 1.5442 | 1.6524 | 1.7559 | 1.8552 | 1.9503 | 2.0417 | 1042.8348 | 1195.6916 | 1314.0961 | 1430.3304 | 1544.1772 | 1652.425 | 1755.9076 | 1855.2065 | 1950.3078 | 2041.7233
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9745 | 3.3001 | 3.5562 | 3.8088 | 4.058 | 4.2957 | 4.5241 | 4.7445 | 4.9565 | 5.1614 | 2974.4873 | 3300.0833 | 3556.1955 | 3808.7784 | 4057.986 | 4295.6773 | 4524.1312 | 4744.4679 | 4956.5053 | 5161.3921
48 | PMA | Northwest | TBU3 | Burnie 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6837 | 1.8692 | 2.0193 | 2.164 | 2.3046 | 2.4362 | 2.5604 | 2.6782 | 2.7894 | 2.895 | 1683.7161 | 1869.2441 | 2019.2942 | 2164.0092 | 2304.5677 | 2436.2131 | 2560.4248 | 2678.1535 | 2789.3982 | 2894.9569
48 | PMA | Northwest | TBU3 | Burnie 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6837 | 1.8692 | 2.0193 | 2.164 | 2.3046 | 2.4362 | 2.5604 | 2.6782 | 2.7894 | 2.895 | 1683.7161 | 1869.2441 | 2019.2942 | 2164.0092 | 2304.5677 | 2436.2131 | 2560.4248 | 2678.1535 | 2789.3982 | 2894.9569
48 | PMA | Southern | CAZ | Cambridge | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.41248 | 0.4744 | 0.52243 | 0.56958 | 0.61577 | 0.65969 | 0.70169 | 0.74198 | 0.78058 | 0.81769 | 412.4758 | 474.404 | 522.4339 | 569.5839 | 615.7718 | 659.6932 | 701.6852 | 741.9845 | 780.5843 | 817.6923
48 | PMA | Southern | CAZ | Cambridge | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.41248 | 0.4744 | 0.52243 | 0.56958 | 0.61577 | 0.65969 | 0.70169 | 0.74198 | 0.78058 | 0.81769 | 412.4758 | 474.404 | 522.4339 | 569.5839 | 615.7718 | 659.6932 | 701.6852 | 741.9845 | 780.5843 | 817.6923
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCS3 | Chapel St 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.9911 | 2.2689 | 2.5054 | 2.7339 | 2.9565 | 3.1662 | 3.3651 | 3.5545 | 3.7344 | 3.906 | 1991.1388 | 2268.9419 | 2505.3563 | 2733.8643 | 2956.5449 | 3166.2394 | 3365.1137 | 3554.5277 | 3734.4091 | 3905.9659
48 | PMA | Southern | CLZ | Claremont | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.612 | 1.8302 | 2.0161 | 2.196 | 2.3715 | 2.5369 | 2.694 | 2.8437 | 2.9861 | 3.1221 | 1612.0006 | 1830.1552 | 2016.0695 | 2195.9771 | 2371.4661 | 2536.9033 | 2693.9782 | 2843.7426 | 2986.1296 | 3122.0818
48 | PMA | George Town | TC01 | Comalco | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 4.5674 | 5.1585 | 5.6315 | 6.0907 | 6.5385 | 6.9603 | 7.3607 | 7.7422 | 8.1049 | 8.4509 | 4567.3771 | 5158.4752 | 5631.5337 | 6090.7118 | 6538.4676 | 6960.3251 | 7360.6932 | 7742.2333 | 8104.8567 | 8450.9187
48 | PMA | North | TDE2 | Derby 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.56972 | 0.63738 | 0.69887 | 0.75911 | 0.8171 | 0.87153 | 0.92297 | 0.9716 | 1.0176 | 1.0612 | 569.7175 | 637.3842 | 698.8694 | 759.1078 | 817.1015 | 871.5325 | 922.973 | 971.5971 | 1017.576 | 1061.1874
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.010044 | 0.011225 | 0.01215 | 0.013052 | 0.013932 | 0.014764 | 0.015556 | 0.016312 | 0.017032 | 0.017721 | 10.0441 | 11.2253 | 12.1505 | 13.052 | 13.9322 | 14.7644 | 15.5558 | 16.3118 | 17.0321 | 17.7211
48 | PMA | Southern | DPZ | Derwent Park | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.55339 | 0.62646 | 0.68835 | 0.74836 | 0.80696 | 0.86227 | 0.91485 | 0.96505 | 1.0128 | 1.0585 | 553.3881 | 626.4567 | 688.3531 | 748.357 | 806.9558 | 862.2674 | 914.8512 | 965.05 | 1012.8387 | 1058.5277
48 | PMA | Northwest | TDP2 | Devonport 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.4445 | 3.831 | 4.1601 | 4.4805 | 4.7922 | 5.0856 | 5.364 | 5.6289 | 5.8804 | 6.1201 | 3444.509 | 3831.0399 | 4160.0934 | 4480.4894 | 4792.1505 | 5085.647 | 5364.0209 | 5628.8832 | 5880.3892 | 6120.1366
48 | PMA | Southern | EHZ | East Hobart | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.29633 | 0.33485 | 0.36441 | 0.39309 | 0.42102 | 0.44728 | 0.47216 | 0.49582 | 0.51827 | 0.53966 | 296.3315 | 334.8535 | 364.4136 | 393.0883 | 421.0199 | 447.2793 | 472.1567 | 495.8207 | 518.2709 | 539.6557
48 | PMA | Southern | TEL2 | Electrona 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.4684 | 0.52294 | 0.56908 | 0.61421 | 0.65839 | 0.70029 | 0.74029 | 0.77864 | 0.8153 | 0.8505 | 468.3989 | 522.9404 | 569.0825 | 614.2135 | 658.3853 | 700.2891 | 740.2938 | 778.64 | 815.3037 | 850.4996
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.26551 | 0.29364 | 0.31442 | 0.33437 | 0.35381 | 0.37188 | 0.38888 | 0.40495 | 0.42006 | 0.43435 | 265.5134 | 293.6355 | 314.422 | 334.3744 | 353.8118 | 371.8791 | 388.8847 | 404.9452 | 420.0605 | 434.3536
48 | PMA | Southern | TBYA | Boyer SWA | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | GBZ | Geilston Bay | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.569 | 1.7764 | 1.937 | 2.0948 | 2.2495 | 2.3967 | 2.5375 | 2.6727 | 2.8022 | 2.9268 | 1569.0201 | 1776.3658 | 1937.0253 | 2094.8438 | 2249.538 | 2396.7012 | 2537.4793 | 2672.6522 | 2802.192 | 2926.7926
48 | PMA | George Town | TGT3 | George Town 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.13662 | 0.15214 | 0.16731 | 0.18198 | 0.19636 | 0.20993 | 0.22284 | 0.23517 | 0.24693 | 0.25817 | 136.6215 | 152.1445 | 167.3131 | 181.9791 | 196.3551 | 209.926 | 222.8364 | 235.1733 | 246.9252 | 258.1691
48 | PMA | George Town | TGT3 | George Town 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.13662 | 0.15214 | 0.16731 | 0.18198 | 0.19636 | 0.20993 | 0.22284 | 0.23517 | 0.24693 | 0.25817 | 136.6215 | 152.1445 | 167.3131 | 181.9791 | 196.3551 | 209.926 | 222.8364 | 235.1733 | 246.9252 | 258.1691
48 | PMA | Western | TGO2 | Gordon | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | GRZ | Gretna | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.012657 | 0.014135 | 0.015293 | 0.016422 | 0.017524 | 0.018566 | 0.019556 | 0.020503 | 0.021405 | 0.022267 | 12.6566 | 14.1353 | 15.2934 | 16.4221 | 17.5239 | 18.5657 | 19.5564 | 20.5028 | 21.4045 | 22.2671
48 | PMA | North | THA3 | Hadspen 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 5.6001 | 6.4082 | 7.1944 | 7.9642 | 8.7121 | 9.419 | 10.0908 | 10.7316 | 11.3416 | 11.9245 | 5600.0615 | 6408.155 | 7194.3764 | 7964.2157 | 8712.0619 | 9419.0044 | 10090.8278 | 10731.5548 | 11341.6024 | 11924.4879
48 | PMA | Northwest | THM2 | Hampshire | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | HOZ | Howrah | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.7309 | 1.9869 | 2.1853 | 2.38 | 2.5707 | 2.7521 | 2.9254 | 3.0918 | 3.2511 | 3.4042 | 1730.8706 | 1986.9391 | 2185.2947 | 2380.0143 | 2570.734 | 2752.0737 | 2925.4302 | 3091.778 | 3251.0935 | 3404.2342
48 | PMA | Southern | THR2 | Huon River | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.0014081 | 0.0015862 | 0.0017336 | 0.0018786 | 0.0020214 | 0.0021572 | 0.0022875 | 0.0024128 | 0.0025331 | 0.002649 | 1.4081 | 1.5862 | 1.7336 | 1.8786 | 2.0214 | 2.1572 | 2.2875 | 2.4128 | 2.5331 | 2.649
48 | PMA | Southern | TKE2 | Kermandie 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.38301 | 0.43111 | 0.47088 | 0.51002 | 0.54856 | 0.58524 | 0.62042 | 0.65426 | 0.68674 | 0.71805 | 383.0144 | 431.113 | 470.8754 | 510.0173 | 548.559 | 585.2413 | 620.4212 | 654.2594 | 686.7421 | 718.0464
48 | PMA | Southern | TK12 | Kingston 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1949 | 3.5987 | 3.9412 | 4.2761 | 4.604 | 4.9151 | 5.2121 | 5.4968 | 5.7691 | 6.0304 | 3194.9084 | 3598.6732 | 3941.1535 | 4276.1486 | 4604.0193 | 4915.0952 | 5212.0948 | 5496.8078 | 5769.0512 | 6030.418
48 | PMA | Southern | TK13 | Kingston 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.10637 | 0.1196 | 0.13056 | 0.14133 | 0.15194 | 0.16204 | 0.17172 | 0.18103 | 0.18997 | 0.19858 | 106.3701 | 119.6041 | 130.5555 | 141.3333 | 151.9433 | 162.0402 | 171.7219 | 181.0332 | 189.9701 | 198.5816
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.10637 | 0.1196 | 0.13056 | 0.14133 | 0.15194 | 0.16204 | 0.17172 | 0.18103 | 0.18997 | 0.19858 | 106.3701 | 119.6041 | 130.5555 | 141.3333 | 151.9433 | 162.0402 | 171.7219 | 181.0332 | 189.9701 | 198.5816
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5129 | 2.8661 | 3.1399 | 3.4087 | 3.6722 | 3.9227 | 4.1623 | 4.3923 | 4.6127 | 4.8246 | 2512.8723 | 2866.0671 | 3139.8628 | 3408.7188 | 3672.159 | 3922.715 | 4162.3225 | 4392.3221 | 4612.6714 | 4824.5536
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.5971 | 4.1232 | 4.5306 | 4.9306 | 5.3224 | 5.695 | 6.0511 | 6.3929 | 6.7202 | 7.0348 | 3597.132 | 4123.1508 | 4530.6172 | 4930.625 | 5322.4274 | 5694.9681 | 6051.1176 | 6392.8766 | 6720.1961 | 7034.8374
48 | PMA | North | TMY2 | Mowbray 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.7863 | 1.9721 | 2.1478 | 2.3181 | 2.4834 | 2.6384 | 2.785 | 2.924 | 3.0557 | 3.1808 | 1786.2562 | 1972.0528 | 2147.8151 | 2318.1095 | 2483.3738 | 2638.418 | 2784.9554 | 2924.0452 | 3055.6902 | 3180.7997
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.25257 | 0.28211 | 0.30524 | 0.3278 | 0.34983 | 0.37067 | 0.39049 | 0.40944 | 0.4275 | 0.44479 | 252.5741 | 282.1063 | 305.2396 | 327.7966 | 349.8276 | 370.6672 | 390.4942 | 409.4423 | 427.5048 | 444.7906
48 | PMA | Southern | NTZ | New Town | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.80441 | 0.91251 | 1.0019 | 1.0883 | 1.1725 | 1.2518 | 1.3269 | 1.3985 | 1.4664 | 1.5311 | 804.413 | 912.5136 | 1001.8638 | 1088.3025 | 1172.5211 | 1251.7861 | 1326.9327 | 1398.4742 | 1466.3907 | 1531.1369
48 | PMA | Western | TNT2 | Newton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.00014998 | 0.0001679 | 0.0001777 | 0.00018725 | 0.00019655 | 0.00020533 | 0.00021367 | 0.00022162 | 0.00022919 | 0.00023641 | 0.14998 | 0.1679 | 0.1777 | 0.18725 | 0.19655 | 0.20533 | 0.21367 | 0.22162 | 0.22919 | 0.23641
48 | PMA | Southern | TNH2 | North Hobart 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.80024 | 0.90234 | 0.98068 | 1.0567 | 1.1307 | 1.2003 | 1.2662 | 1.3289 | 1.3884 | 1.4451 | 800.2384 | 902.3378 | 980.6819 | 1056.6788 | 1130.7059 | 1200.3009 | 1266.2329 | 1328.9487 | 1388.4472 | 1445.1221
48 | PMA | North | TNW2 | Norwood 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6332 | 1.8182 | 1.9937 | 2.1644 | 2.3303 | 2.4863 | 2.6341 | 2.7747 | 2.908 | 3.0351 | 1633.2376 | 1818.1748 | 1993.6828 | 2164.4032 | 2330.2653 | 2486.2815 | 2634.083 | 2774.6516 | 2908.0213 | 3035.0574
48 | PMA | North | TNW2 | Norwood 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6332 | 1.8182 | 1.9937 | 2.1644 | 2.3303 | 2.4863 | 2.6341 | 2.7747 | 2.908 | 3.0351 | 1633.2376 | 1818.1748 | 1993.6828 | 2164.4032 | 2330.2653 | 2486.2815 | 2634.083 | 2774.6516 | 2908.0213 | 3035.0574
48 | PMA | North | TPM3 | Palmerston 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT3 | Queenstown 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.25329 | 0.28356 | 0.30012 | 0.31624 | 0.33194 | 0.34678 | 0.36086 | 0.37429 | 0.38706 | 0.39926 | 253.2898 | 283.563 | 300.1179 | 316.2359 | 331.9441 | 346.7759 | 360.8598 | 374.2889 | 387.0642 | 399.2639
48 | PMA | Northwest | TRA2 | Railton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | RIZ | Richmond | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.57949 | 0.65973 | 0.72465 | 0.78832 | 0.85081 | 0.91011 | 0.96678 | 1.0212 | 1.0732 | 1.1233 | 579.4926 | 659.7259 | 724.6472 | 788.3178 | 850.8105 | 910.1062 | 966.7845 | 1021.1656 | 1073.2224 | 1123.2577
48 | PMA | Southern | TR13 | Risdon 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.6358 | 1.8536 | 2.0333 | 2.2073 | 2.377 | 2.5368 | 2.6884 | 2.8329 | 2.9702 | 3.1011 | 1635.8153 | 1853.5789 | 2033.2975 | 2207.3248 | 2376.9981 | 2536.8123 | 2688.4399 | 2832.9011 | 2970.1504 | 3101.0968
48 | PMA | Southern | TRK2 | Rokeby 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1542 | 3.6209 | 3.9824 | 4.3373 | 4.6849 | 5.0154 | 5.3313 | 5.6345 | 5.9248 | 6.2039 | 3154.2152 | 3620.9045 | 3982.4067 | 4337.283 | 4684.8696 | 5015.3617 | 5331.3046 | 5634.4744 | 5924.8281 | 6203.9285
48 | PMA | Western | RBZ | Rosebery 22 kV | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.038367 | 0.063952 | 0.079514 | 0.094653 | 0.10937 | 0.12324 | 0.13638 | 0.14889 | 0.16076 | 0.17207 | 38.3669 | 63.9523 | 79.5141 | 94.6533 | 109.3705 | 123.2394 | 136.3824 | 148.8869 | 160.7587 | 172.072
48 | PMA | Western | TRB2 | Rosebery 44 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | RPZ | Rosny Park | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.1682 | 1.3327 | 1.46 | 1.5851 | 1.7076 | 1.824 | 1.9354 | 2.0422 | 2.1446 | 2.243 | 1168.2491 | 1332.667 | 1460.0315 | 1585.0722 | 1707.5563 | 1824.0244 | 1935.3747 | 2042.2321 | 2144.5805 | 2242.9704
48 | PMA | Southern | SBZ | Sandy Bay | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 2.4663 | 2.78 | 3.026 | 3.2651 | 3.4982 | 3.7179 | 3.9263 | 4.1249 | 4.3136 | 4.4937 | 2466.3089 | 2779.9909 | 3026.0225 | 3265.1114 | 3498.2364 | 3717.8521 | 3926.2664 | 4124.8598 | 4313.5998 | 4493.7025
48 | PMA | Western | TSR2 | Savage River | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.085288 | 0.095187 | 0.10346 | 0.1115 | 0.11926 | 0.12654 | 0.13341 | 0.1399 | 0.14604 | 0.15185 | 85.2882 | 95.1874 | 103.4647 | 111.4974 | 119.2616 | 126.5416 | 133.4061 | 139.9019 | 146.0377 | 151.854
48 | PMA | Southern | SUZ | Summerleas Road | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.2596 | 1.4236 | 1.5629 | 1.6991 | 1.8323 | 1.9587 | 2.0794 | 2.195 | 2.3056 | 2.4117 | 1259.6358 | 1423.58 | 1562.8686 | 1699.0663 | 1832.3232 | 1958.7338 | 2079.3951 | 2195.0441 | 2305.6048 | 2411.7264
48 | PMA | North | TSD2 | Scottsdale 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.1459 | 1.2768 | 1.3982 | 1.5168 | 1.6312 | 1.7386 | 1.8403 | 1.9364 | 2.0274 | 2.1138 | 1145.8772 | 1276.7922 | 1398.1869 | 1516.7855 | 1631.1942 | 1738.6447 | 1840.2506 | 1936.4079 | 2027.402 | 2113.7906
48 | PMA | Northwest | TSH3 | Sheffield | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.21334 | 0.24885 | 0.2854 | 0.32151 | 0.35578 | 0.38809 | 0.41848 | 0.44709 | 0.47409 | 0.49959 | 213.3376 | 248.8493 | 285.4014 | 321.5137 | 355.7832 | 388.0945 | 418.4788 | 447.0898 | 474.0852 | 499.5924
48 | PMA | Southern | TS02 | Sorell | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.4769 | 1.6772 | 1.8336 | 1.987 | 2.1378 | 2.2815 | 2.4191 | 2.5515 | 2.6786 | 2.801 | 1476.906 | 1677.1502 | 1833.5518 | 1986.9946 | 2137.8332 | 2281.5013 | 2419.1064 | 2551.5051 | 2678.5637 | 2800.9859
48 | PMA | total terminal |  | total terminal | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 61.9642 | 69.7367 | 76.3889 | 82.881 | 89.2137 | 95.1982 | 100.8906 | 106.3258 | 111.504 | 116.4565 | 61964.2366 | 69736.7443 | 76388.9474 | 82880.9959 | 89213.7486 | 95198.2252 | 100890.6231 | 106325.8163 | 111503.9545 | 116456.4676
48 | PMA | total zone |  | total zone | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 14.8543 | 17.0459 | 18.7832 | 20.4795 | 22.1378 | 23.7082 | 25.2048 | 26.6366 | 28.0034 | 29.3132 | 14854.3482 | 17045.941 | 18783.2292 | 20479.4719 | 22137.8271 | 23708.219 | 25204.7757 | 26636.622 | 28003.3957 | 29313.1788
48 | PMA | North | TSL2 | St Leonards 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.4452 | 2.6914 | 2.9246 | 3.1504 | 3.3697 | 3.5753 | 3.7698 | 3.9543 | 4.129 | 4.295 | 2445.2478 | 2691.4474 | 2924.5604 | 3150.4488 | 3369.6634 | 3575.3479 | 3769.7605 | 3954.305 | 4128.9861 | 4295.0076
48 | PMA | North | TSM2 | St Marys 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8974 | 2.0801 | 2.2304 | 2.3774 | 2.5209 | 2.6556 | 2.7833 | 2.9049 | 3.0203 | 3.1303 | 1897.3817 | 2080.0645 | 2230.4409 | 2377.4267 | 2520.9398 | 2655.5784 | 2783.3421 | 2904.9175 | 3020.3027 | 3130.2847
48 | PMA | North | TTR2 | Trevallyn 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 3.4559 | 3.8879 | 4.3045 | 4.7095 | 5.1037 | 5.4755 | 5.8282 | 6.1644 | 6.484 | 6.7889 | 3455.9106 | 3887.9385 | 4304.532 | 4709.5075 | 5103.6976 | 5475.4869 | 5828.213 | 6164.4044 | 6483.9599 | 6788.914
48 | PMA | North | TTR2 | Trevallyn 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 3.4559 | 3.8879 | 4.3045 | 4.7095 | 5.1037 | 5.4755 | 5.8282 | 6.1644 | 6.484 | 6.7889 | 3455.9106 | 3887.9385 | 4304.532 | 4709.5075 | 5103.6976 | 5475.4869 | 5828.213 | 6164.4044 | 6483.9599 | 6788.914
48 | PMA | Southern | TTB2 | Triabunna 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.31457 | 0.34972 | 0.37699 | 0.40373 | 0.42995 | 0.45478 | 0.47849 | 0.5012 | 0.52291 | 0.54374 | 314.5736 | 349.7207 | 376.9904 | 403.7344 | 429.9495 | 454.7816 | 478.4858 | 501.1987 | 522.9075 | 543.7407
48 | PMA | Western | THZ | Trial Harbour | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.022984 | 0.037442 | 0.045481 | 0.053311 | 0.060936 | 0.068134 | 0.074967 | 0.081479 | 0.087673 | 0.093585 | 22.9844 | 37.4419 | 45.4812 | 53.3109 | 60.9355 | 68.1337 | 74.9666 | 81.4791 | 87.6726 | 93.585
48 | PMA | George Town | TC01 | Comalco | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00065009 | 0.000726 | 0.00078782 | 0.00085016 | 0.00091273 | 0.00097487 | 0.001037 | 0.0010993 | 0.0011619 | 0.0012246 | 0.65009 | 0.726 | 0.78782 | 0.85016 | 0.91273 | 0.97487 | 1.037 | 1.0993 | 1.1619 | 1.2246
48 | PMA | North | TAV2 | Avoca 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.23006 | 0.26458 | 0.29766 | 0.33101 | 0.36408 | 0.39672 | 0.42909 | 0.46132 | 0.49347 | 0.52536 | 230.0605 | 264.5789 | 297.6622 | 331.006 | 364.0789 | 396.7152 | 429.0859 | 461.3166 | 493.4705 | 525.3624
48 | PMA | North | TDE2 | Derby 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.57021 | 0.63994 | 0.7054 | 0.77098 | 0.83525 | 0.8981 | 0.9599 | 1.0207 | 1.0808 | 1.1399 | 570.2145 | 639.9426 | 705.3971 | 770.9849 | 835.2516 | 898.1035 | 959.9018 | 1020.7374 | 1080.847 | 1139.8649
48 | PMA | North | THA3 | Hadspen 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 5.6062 | 6.4405 | 7.2775 | 8.1156 | 8.9444 | 9.7607 | 10.5679 | 11.3697 | 12.1672 | 12.9562 | 5606.1559 | 6440.5326 | 7277.4532 | 8115.5615 | 8944.3936 | 9760.7355 | 10567.8906 | 11369.6502 | 12167.239 | 12956.1578
48 | PMA | North | TMY2 | Mowbray 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.7877 | 1.9794 | 2.1665 | 2.3519 | 2.535 | 2.714 | 2.8901 | 3.0641 | 3.2362 | 3.4055 | 1787.6644 | 1979.4335 | 2166.4847 | 2351.8779 | 2535.0288 | 2714.0391 | 2890.0886 | 3064.112 | 3236.2179 | 3405.5324
48 | PMA | North | TPM3 | Palmerston 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.1469 | 1.2818 | 1.4111 | 1.5402 | 1.667 | 1.7911 | 1.9131 | 2.0334 | 2.1524 | 2.2693 | 1146.8519 | 1281.8409 | 1411.0618 | 1540.1924 | 1666.9784 | 1791.0514 | 1913.1177 | 2033.4258 | 2152.3861 | 2269.2954
48 | PMA | North | TSL2 | St Leonards 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.4471 | 2.7012 | 2.9493 | 3.1952 | 3.4382 | 3.6757 | 3.9092 | 4.1401 | 4.3685 | 4.5932 | 2447.1146 | 2701.2337 | 2949.3201 | 3195.2363 | 3438.177 | 3675.6559 | 3909.2226 | 4140.1175 | 4368.4868 | 4593.1691
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8986 | 2.0865 | 2.2465 | 2.4066 | 2.5656 | 2.7211 | 2.8746 | 3.0267 | 3.1776 | 3.3264 | 1898.6453 | 2086.4955 | 2246.545 | 2406.5867 | 2565.6267 | 2721.0932 | 2874.592 | 3026.7091 | 3177.5624 | 3326.4117
48 | PMA | Northwest | TDP2 | Devonport 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.4472 | 3.8448 | 4.1951 | 4.5439 | 4.8893 | 5.2282 | 5.5626 | 5.8941 | 6.2229 | 6.5473 | 3447.1559 | 3844.8331 | 4195.0594 | 4543.9051 | 4889.3045 | 5228.203 | 5562.6477 | 5894.0552 | 6222.8714 | 6547.3466
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.26569 | 0.29454 | 0.31665 | 0.33838 | 0.35992 | 0.38078 | 0.40121 | 0.4213 | 0.44106 | 0.4604 | 265.6896 | 294.5358 | 316.6524 | 338.3779 | 359.9169 | 380.775 | 401.205 | 421.2965 | 441.0566 | 460.398
48 | PMA | Northwest | THM2 | Hampshire | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.21361 | 0.25031 | 0.28924 | 0.32855 | 0.36653 | 0.40384 | 0.44034 | 0.47614 | 0.51143 | 0.54594 | 213.6084 | 250.3066 | 289.2431 | 328.5539 | 366.5325 | 403.8407 | 440.3413 | 476.1373 | 511.4276 | 545.9435
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 4.1227 | 4.6024 | 5.0157 | 5.4259 | 5.8311 | 6.2274 | 6.617 | 7.0018 | 7.3824 | 7.7566 | 4122.7459 | 4602.4241 | 5015.6745 | 5425.9173 | 5831.1119 | 6227.4053 | 6616.9844 | 7001.8209 | 7382.3667 | 7756.573
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.73572 | 0.83489 | 0.93107 | 1.028 | 1.1248 | 1.2211 | 1.3171 | 1.4135 | 1.5101 | 1.6066 | 735.7172 | 834.8863 | 931.0746 | 1027.9644 | 1124.7992 | 1221.0765 | 1317.1389 | 1413.4503 | 1510.1082 | 1606.6015
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9765 | 3.3107 | 3.5834 | 3.8584 | 4.1346 | 4.4091 | 4.6836 | 4.9594 | 5.2366 | 5.514 | 2976.5082 | 3310.7254 | 3583.3509 | 3858.3889 | 4134.6013 | 4409.1277 | 4683.6234 | 4959.3899 | 5236.6371 | 5513.9944
48 | PMA | Southern | TBYA | Boyer SWA | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 4.5711 | 5.1782 | 5.6817 | 6.1816 | 6.6778 | 7.165 | 7.646 | 8.1234 | 8.5975 | 9.0658 | 4571.1244 | 5178.2437 | 5681.6821 | 6181.6139 | 6677.8458 | 7164.952 | 7645.9676 | 8123.3743 | 8597.4674 | 9065.8376
48 | PMA | Southern | TCS3 | Chapel St 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.993 | 2.2788 | 2.5304 | 2.7792 | 3.026 | 3.2681 | 3.507 | 3.744 | 3.9792 | 4.2114 | 1993.0181 | 2278.8396 | 2530.4072 | 2779.1957 | 3025.9875 | 3268.11 | 3507.0442 | 3744.0476 | 3979.2236 | 4211.4122
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.010051 | 0.011264 | 0.012248 | 0.01323 | 0.014205 | 0.015166 | 0.016117 | 0.017063 | 0.018005 | 0.018938 | 10.0513 | 11.2637 | 12.2484 | 13.23 | 14.2054 | 15.1664 | 16.1173 | 17.0633 | 18.005 | 18.9376
48 | PMA | Southern | TEL2 | Electrona 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.46876 | 0.52486 | 0.57397 | 0.6231 | 0.67206 | 0.72045 | 0.76852 | 0.8165 | 0.86444 | 0.91208 | 468.7614 | 524.8559 | 573.9674 | 623.1045 | 672.0618 | 720.4527 | 768.5177 | 816.5048 | 864.4414 | 912.0817
48 | PMA | Southern | THR2 | Huon River | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.0014093 | 0.0015924 | 0.0017492 | 0.0019071 | 0.0020654 | 0.0022223 | 0.0023788 | 0.0025357 | 0.0026929 | 0.0028498 | 1.4093 | 1.5924 | 1.7492 | 1.9071 | 2.0654 | 2.2223 | 2.3788 | 2.5357 | 2.6929 | 2.8498
48 | PMA | Southern | TK12 | Kingston 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1976 | 3.6129 | 3.9774 | 4.3421 | 4.7055 | 5.0648 | 5.4216 | 5.7779 | 6.1338 | 6.4876 | 3197.5977 | 3612.887 | 3977.4075 | 4342.1369 | 4705.5296 | 5064.7637 | 5421.604 | 5777.8997 | 6133.8497 | 6487.6286
48 | PMA | Southern | TK13 | Kingston 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.38333 | 0.43277 | 0.4751 | 0.51772 | 0.56044 | 0.6028 | 0.64507 | 0.68742 | 0.72989 | 0.77227 | 383.3308 | 432.7709 | 475.0972 | 517.7204 | 560.438 | 602.8041 | 645.0736 | 687.4226 | 729.8944 | 772.2698
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.515 | 2.8773 | 3.1688 | 3.4615 | 3.7535 | 4.0429 | 4.3307 | 4.6186 | 4.9067 | 5.1935 | 2514.981 | 2877.3266 | 3168.7786 | 3461.5128 | 3753.4964 | 4042.8575 | 4330.7461 | 4618.5853 | 4906.6903 | 5193.4974
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.6003 | 4.1399 | 4.5736 | 5.0092 | 5.4434 | 5.8737 | 6.3016 | 6.7293 | 7.1572 | 7.5831 | 3600.2687 | 4139.9041 | 4573.6461 | 5009.1787 | 5443.4315 | 5873.6675 | 6301.5803 | 6729.2815 | 7157.2482 | 7583.1493
48 | PMA | Southern | TNH2 | North Hobart 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.80086 | 0.90562 | 0.98899 | 1.0717 | 1.1538 | 1.2341 | 1.3133 | 1.3918 | 1.4696 | 1.5463 | 800.8598 | 905.6161 | 988.9926 | 1071.7342 | 1153.7735 | 1234.1302 | 1313.3419 | 1391.8128 | 1469.5996 | 1546.3023
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.25275 | 0.28307 | 0.30769 | 0.33225 | 0.35667 | 0.38073 | 0.40455 | 0.42826 | 0.45188 | 0.47527 | 252.7541 | 283.0655 | 307.6887 | 332.2479 | 356.665 | 380.7292 | 404.5507 | 428.2614 | 451.8768 | 475.2732
48 | PMA | Southern | TR13 | Risdon 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.6372 | 1.8611 | 2.0523 | 2.2418 | 2.4299 | 2.6144 | 2.7966 | 2.9773 | 3.1568 | 3.334 | 1637.2424 | 1861.099 | 2052.346 | 2241.8197 | 2429.8636 | 2614.3943 | 2796.5647 | 2977.3224 | 3156.7618 | 3333.9881
48 | PMA | Southern | TRK2 | Rokeby 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.157 | 3.6358 | 4.0206 | 4.407 | 4.7922 | 5.1739 | 5.5535 | 5.9329 | 6.3125 | 6.6903 | 3156.998 | 3635.7676 | 4020.5813 | 4406.9742 | 4792.2205 | 5173.8957 | 5553.5005 | 5932.9081 | 6312.5424 | 6690.3349
48 | PMA | Southern | TS02 | Sorell | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.4781 | 1.6836 | 1.8501 | 2.0172 | 2.1844 | 2.3503 | 2.5156 | 2.6813 | 2.8475 | 3.0132 | 1478.1231 | 1683.6239 | 1850.1068 | 2017.1793 | 2184.367 | 2350.2871 | 2515.6231 | 2681.3225 | 2847.4537 | 3013.1728
48 | PMA | Southern | TTB2 | Triabunna 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.31479 | 0.35086 | 0.37989 | 0.40901 | 0.43806 | 0.46674 | 0.49522 | 0.52364 | 0.55203 | 0.58022 | 314.7922 | 350.8629 | 379.8897 | 409.0089 | 438.0632 | 466.7396 | 495.2197 | 523.6427 | 552.026 | 580.2249
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.071566 | 0.080161 | 0.087143 | 0.094102 | 0.10102 | 0.10783 | 0.11457 | 0.12128 | 0.12796 | 0.13457 | 71.5658 | 80.1613 | 87.1425 | 94.1018 | 101.0176 | 107.8307 | 114.5718 | 121.2786 | 127.9554 | 134.5671
48 | PMA | Southern | TWA2 | Waddamana 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.032973 | 0.036831 | 0.039975 | 0.043144 | 0.046325 | 0.049484 | 0.05264 | 0.055809 | 0.058993 | 0.062175 | 32.9727 | 36.8312 | 39.9745 | 43.144 | 46.325 | 49.484 | 52.6404 | 55.8092 | 58.9927 | 62.1753
48 | PMA | Western | TGO2 | Gordon | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.00015005 | 0.00016831 | 0.00017874 | 0.00018913 | 0.00019944 | 0.00020958 | 0.00021959 | 0.00022954 | 0.00023943 | 0.00024921 | 0.15005 | 0.16831 | 0.17874 | 0.18913 | 0.19944 | 0.20958 | 0.21959 | 0.22954 | 0.23943 | 0.24921
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.25342 | 0.28425 | 0.30187 | 0.31941 | 0.33682 | 0.35395 | 0.37087 | 0.38767 | 0.40437 | 0.42088 | 253.4186 | 284.2483 | 301.8675 | 319.4145 | 336.8221 | 353.9467 | 370.8658 | 387.668 | 404.3687 | 420.8777
48 | PMA | Western | TQT3 | Queenstown 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.085354 | 0.095533 | 0.10434 | 0.11309 | 0.12169 | 0.1301 | 0.13835 | 0.14647 | 0.15449 | 0.16237 | 85.3539 | 95.5332 | 104.3439 | 113.0892 | 121.6936 | 130.0988 | 138.3456 | 146.4726 | 154.494 | 162.365
48 | PMA | Southern | BEZ | Bellerive | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.0437 | 1.2006 | 1.3266 | 1.4532 | 1.5793 | 1.7044 | 1.8287 | 1.953 | 2.0773 | 2.201 | 1043.7463 | 1200.5598 | 1326.5996 | 1453.1567 | 1579.3384 | 1704.3505 | 1828.6845 | 1952.9541 | 2077.298 | 2201.0388
48 | PMA | Southern | CLZ | Claremont | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.6135 | 1.8379 | 2.0358 | 2.2316 | 2.4261 | 2.6172 | 2.8059 | 2.9933 | 3.1794 | 3.3634 | 1613.4777 | 1837.9342 | 2035.7678 | 2231.6445 | 2426.1368 | 2617.1621 | 2805.8784 | 2993.2745 | 3179.4324 | 3363.4367
48 | PMA | Southern | DPZ | Derwent Park | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.55388 | 0.62904 | 0.69491 | 0.76024 | 0.82519 | 0.88906 | 0.95223 | 1.015 | 1.0775 | 1.1394 | 553.8793 | 629.0444 | 694.911 | 760.2419 | 825.1866 | 889.055 | 952.2319 | 1015.0459 | 1077.526 | 1139.3649
48 | PMA | Southern | EHZ | East Hobart | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.29657 | 0.33609 | 0.36755 | 0.39877 | 0.42972 | 0.46004 | 0.48993 | 0.51954 | 0.54889 | 0.57783 | 296.566 | 336.0904 | 367.5494 | 398.7689 | 429.7236 | 460.0436 | 489.9317 | 519.5404 | 548.8912 | 577.833
48 | PMA | Southern | GBZ | Geilston Bay | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.5703 | 1.783 | 1.954 | 2.1258 | 2.2973 | 2.4672 | 2.6364 | 2.8056 | 2.9749 | 3.1436 | 1570.2582 | 1782.974 | 1953.9943 | 2125.8301 | 2297.2854 | 2467.2416 | 2636.387 | 2805.5535 | 2974.9263 | 3143.5884
48 | PMA | Southern | GRZ | Gretna | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.012666 | 0.014183 | 0.015416 | 0.016645 | 0.017866 | 0.019069 | 0.020259 | 0.021444 | 0.022622 | 0.02379 | 12.6656 | 14.1833 | 15.416 | 16.6448 | 17.866 | 19.069 | 20.2593 | 21.4435 | 22.6225 | 23.7899
48 | PMA | Southern | HOZ | Howrah | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.7324 | 1.9951 | 2.2062 | 2.4183 | 2.6296 | 2.8391 | 3.0473 | 3.2555 | 3.4638 | 3.6711 | 1732.3976 | 1995.0945 | 2206.2411 | 2418.2538 | 2629.6372 | 2839.0609 | 3047.3483 | 3255.5275 | 3463.8308 | 3671.1233
48 | PMA | Southern | NTZ | New Town | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.80512 | 0.91625 | 1.0113 | 1.1054 | 1.1988 | 1.2903 | 1.3806 | 1.4701 | 1.5589 | 1.6465 | 805.1229 | 916.254 | 1011.3344 | 1105.4446 | 1198.7811 | 1290.3036 | 1380.5868 | 1470.102 | 1558.8952 | 1646.5232
48 | PMA | Southern | RIZ | Richmond | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.58001 | 0.66243 | 0.73154 | 0.80087 | 0.87013 | 0.93861 | 1.0067 | 1.0748 | 1.1428 | 1.2106 | 580.0075 | 662.4337 | 731.5382 | 800.8658 | 870.1281 | 938.6057 | 1006.7044 | 1074.7594 | 1142.8228 | 1210.5504
48 | PMA | Southern | RPZ | Rosny Park | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.1692 | 1.3379 | 1.4735 | 1.6096 | 1.7454 | 1.8799 | 2.0137 | 2.1474 | 2.2812 | 2.4144 | 1169.2297 | 1337.9038 | 1473.4816 | 1609.6272 | 1745.3821 | 1879.8877 | 2013.675 | 2147.4039 | 2281.2234 | 2414.405
48 | PMA | Southern | SBZ | Sandy Bay | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 2.4683 | 2.7903 | 3.0521 | 3.3124 | 3.5708 | 3.8244 | 4.0748 | 4.3233 | 4.57 | 4.8138 | 2468.2555 | 2790.2666 | 3052.1082 | 3312.4162 | 3570.7788 | 3824.3628 | 4074.7582 | 4323.2504 | 4570.0082 | 4813.7634
48 | PMA | Southern | SUZ | Summerleas Road | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.2607 | 1.4294 | 1.5776 | 1.7259 | 1.8736 | 2.0196 | 2.1645 | 2.3093 | 2.4538 | 2.5975 | 1260.7287 | 1429.3593 | 1577.6108 | 1725.8961 | 1873.5902 | 2019.5697 | 2164.5421 | 2309.2671 | 2453.8215 | 2597.4643
48 | PMA | Southern | TWY2 | Wayatinah | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.0030024 | 0.0058459 | 0.0081553 | 0.010458 | 0.012745 | 0.014999 | 0.017229 | 0.019448 | 0.021657 | 0.023844 | 3.0024 | 5.8459 | 8.1553 | 10.4576 | 12.7454 | 14.9993 | 17.2293 | 19.4481 | 21.6569 | 23.8441
48 | PMA | Southern | WHZ | West Hobart Zone | high | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.14543 | 0.28724 | 0.40229 | 0.51664 | 0.63012 | 0.74148 | 0.85142 | 0.96051 | 1.0688 | 1.1758 | 145.4257 | 287.2431 | 402.287 | 516.6365 | 630.1199 | 741.4804 | 851.4214 | 960.5067 | 1068.811 | 1175.7777
48 | PMA | Western | THZ | Trial Harbour | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.023047 | 0.037774 | 0.046331 | 0.054855 | 0.063304 | 0.071615 | 0.079823 | 0.087972 | 0.096068 | 0.10407 | 23.0469 | 37.7745 | 46.3308 | 54.8547 | 63.3041 | 71.6151 | 79.8235 | 87.9717 | 96.0683 | 104.0691
48 | PMA | Western | RBZ | Rosebery 22 kV | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.038489 | 0.064598 | 0.081161 | 0.097643 | 0.11395 | 0.12996 | 0.14575 | 0.1614 | 0.17692 | 0.19223 | 38.4886 | 64.5979 | 81.1609 | 97.6427 | 113.9521 | 129.9649 | 145.7539 | 161.399 | 176.9188 | 192.2284
48 | PMA | total terminal |  | total terminal | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 62.0167 | 70.0135 | 77.0939 | 84.1622 | 91.1807 | 98.0913 | 104.9304 | 111.7316 | 118.5017 | 125.2048 | 62016.6784 | 70013.4574 | 77093.8724 | 84162.1809 | 91180.7204 | 98091.2566 | 104930.3978 | 111731.6167 | 118501.6559 | 125204.8092
48 | PMA | total zone |  | total zone | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 14.8679 | 17.118 | 18.9671 | 20.8139 | 22.6519 | 24.4653 | 26.2634 | 28.0552 | 29.8422 | 31.615 | 14867.9277 | 17117.9707 | 18967.0529 | 20813.8937 | 22651.8675 | 24465.3218 | 26263.3881 | 28055.1679 | 29842.1544 | 31614.9842
48 | PMA | George Town | TC01 | Comalco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00064917 | 0.0007212 | 0.00077566 | 0.00082811 | 0.00087891 | 0.00092637 | 0.00097104 | 0.0010132 | 0.0010523 | 0.0010886 | 0.64917 | 0.7212 | 0.77566 | 0.82811 | 0.87891 | 0.92637 | 0.97104 | 1.0132 | 1.0523 | 1.0886
48 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.22958 | 0.26204 | 0.29118 | 0.31925 | 0.3461 | 0.37103 | 0.39432 | 0.41615 | 0.43622 | 0.45472 | 229.5798 | 262.0416 | 291.1835 | 319.246 | 346.0993 | 371.0291 | 394.3222 | 416.1455 | 436.222 | 454.715
48 | PMA | North | TDE2 | Derby 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.56922 | 0.63485 | 0.69251 | 0.7477 | 0.79989 | 0.84791 | 0.89239 | 0.93359 | 0.97114 | 1.0054 | 569.2204 | 634.8544 | 692.5107 | 747.7021 | 799.8929 | 847.9126 | 892.3895 | 933.5934 | 971.1352 | 1005.3678
48 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 5.594 | 6.3762 | 7.1135 | 7.8189 | 8.4918 | 9.1155 | 9.6963 | 10.2392 | 10.7373 | 11.1948 | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564
48 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.7848 | 1.9648 | 2.1296 | 2.2857 | 2.4344 | 2.5712 | 2.6979 | 2.8157 | 2.9232 | 3.0214 | 1784.8481 | 1964.7566 | 2129.6241 | 2285.6724 | 2434.3915 | 2571.1787 | 2697.8737 | 2815.7368 | 2923.2225 | 3021.4243
48 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.1449 | 1.2718 | 1.3856 | 1.4943 | 1.5973 | 1.6921 | 1.7799 | 1.8614 | 1.9357 | 2.0035 | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982
48 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.4434 | 2.6818 | 2.9004 | 3.1074 | 3.3047 | 3.4862 | 3.6542 | 3.8106 | 3.9533 | 4.0836 | 2443.3811 | 2681.7732 | 2900.4355 | 3107.427 | 3304.695 | 3486.1592 | 3654.2466 | 3810.6275 | 3953.2512 | 4083.5657
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8961 | 2.0737 | 2.2147 | 2.3494 | 2.4786 | 2.5973 | 2.7078 | 2.8108 | 2.905 | 2.9914 | 1896.118 | 2073.7058 | 2214.748 | 2349.417 | 2478.5671 | 2597.346 | 2707.8062 | 2810.8256 | 2905.03 | 2991.3556
48 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.4419 | 3.8174 | 4.126 | 4.4196 | 4.7 | 4.959 | 5.1996 | 5.4241 | 5.6294 | 5.8176 | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.26534 | 0.29275 | 0.31225 | 0.33053 | 0.34802 | 0.36396 | 0.37866 | 0.39227 | 0.40462 | 0.41584 | 265.3371 | 292.7451 | 312.2479 | 330.5276 | 348.0208 | 363.9613 | 378.6647 | 392.275 | 404.6173 | 415.8369
48 | PMA | Northwest | THM2 | Hampshire | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.21307 | 0.24741 | 0.28166 | 0.31476 | 0.3456 | 0.3741 | 0.40037 | 0.42462 | 0.44666 | 0.46668 | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 4.1166 | 4.5701 | 4.9342 | 5.2795 | 5.6085 | 5.9113 | 6.1917 | 6.4523 | 6.69 | 6.907 | 4116.5699 | 4570.097 | 4934.2228 | 5279.4811 | 5608.5022 | 5911.3163 | 6191.6824 | 6452.3257 | 6689.9917 | 6907.033
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.73429 | 0.82744 | 0.91217 | 0.9937 | 1.0723 | 1.1458 | 1.215 | 1.2802 | 1.3405 | 1.3964 | 734.2942 | 827.4446 | 912.1748 | 993.7003 | 1072.3061 | 1145.8406 | 1214.9565 | 1280.1575 | 1340.4996 | 1396.4433
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9725 | 3.2896 | 3.5297 | 3.7611 | 3.9854 | 4.195 | 4.3925 | 4.5792 | 4.7523 | 4.9131 | 2972.4663 | 3289.5635 | 3529.7436 | 3761.1438 | 3985.3753 | 4195.0464 | 4392.539 | 4579.2239 | 4752.2984 | 4913.0967
48 | PMA | Southern | TBYA | Boyer SWA | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 4.5636 | 5.1389 | 5.5827 | 6.0034 | 6.4063 | 6.7785 | 7.1246 | 7.4479 | 7.744 | 8.0156 | 4563.6299 | 5138.933 | 5582.673 | 6003.4019 | 6406.3186 | 6778.4881 | 7124.6308 | 7447.9318 | 7743.9852 | 8015.6085
48 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.9893 | 2.2592 | 2.4809 | 2.6903 | 2.8907 | 3.0757 | 3.2476 | 3.4081 | 3.555 | 3.6897 | 1989.2595 | 2259.1565 | 2480.9457 | 2690.32 | 2890.6985 | 3075.6964 | 3247.6354 | 3408.1374 | 3554.9975 | 3689.6523
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.010037 | 0.011187 | 0.012055 | 0.012881 | 0.013673 | 0.014407 | 0.015091 | 0.015732 | 0.01632 | 0.016861 | 10.0369 | 11.1874 | 12.0551 | 12.8811 | 13.6731 | 14.4073 | 15.0915 | 15.7321 | 16.3201 | 16.8609
48 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.46804 | 0.52105 | 0.56432 | 0.60568 | 0.64542 | 0.68239 | 0.71697 | 0.74946 | 0.77939 | 0.80702 | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167
48 | PMA | Southern | THR2 | Huon River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.001407 | 0.0015801 | 0.0017183 | 0.0018512 | 0.0019797 | 0.0020995 | 0.0022121 | 0.0023183 | 0.0024165 | 0.0025074 | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074
48 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1922 | 3.5846 | 3.9058 | 4.2128 | 4.5078 | 4.7822 | 5.039 | 5.2802 | 5.5025 | 5.7076 | 3192.219 | 3584.623 | 3905.8354 | 4212.7778 | 4507.7941 | 4782.2149 | 5038.9766 | 5280.2171 | 5502.459 | 5707.5939
48 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.3827 | 0.42947 | 0.46676 | 0.50262 | 0.5373 | 0.56966 | 0.60007 | 0.62874 | 0.65526 | 0.67982 | 382.698 | 429.4741 | 466.7629 | 502.6209 | 537.3003 | 569.6585 | 600.071 | 628.7414 | 655.2563 | 679.8248
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5108 | 2.8549 | 3.1117 | 3.358 | 3.5951 | 3.8161 | 4.0232 | 4.2181 | 4.398 | 4.5643 | 2510.7635 | 2854.9382 | 3111.6989 | 3358.0279 | 3595.0685 | 3816.0948 | 4023.2369 | 4218.1141 | 4397.9871 | 4564.2812
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.594 | 4.1066 | 4.4887 | 4.8552 | 5.2077 | 5.5364 | 5.8443 | 6.1338 | 6.401 | 6.648 | 3593.9952 | 4106.5919 | 4488.7071 | 4855.2004 | 5207.7406 | 5536.3757 | 5844.2698 | 6133.8407 | 6401.0359 | 6647.9801
48 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.79962 | 0.8991 | 0.97258 | 1.0422 | 1.1088 | 1.1702 | 1.2272 | 1.2804 | 1.329 | 1.3734 | 799.6171 | 899.097 | 972.5847 | 1042.2182 | 1108.834 | 1170.2327 | 1227.2359 | 1280.3796 | 1328.9571 | 1373.442
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.25239 | 0.28116 | 0.30285 | 0.32352 | 0.34335 | 0.36173 | 0.37887 | 0.39493 | 0.40967 | 0.42324 | 252.3942 | 281.1583 | 302.854 | 323.5219 | 343.3459 | 361.7304 | 378.8717 | 394.927 | 409.6728 | 423.24
48 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.6344 | 1.8461 | 2.0147 | 2.1742 | 2.3269 | 2.4679 | 2.599 | 2.7214 | 2.8334 | 2.9362 | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986
48 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1514 | 3.6062 | 3.9452 | 4.2704 | 4.5831 | 4.8747 | 5.1478 | 5.4047 | 5.6417 | 5.8607 | 3151.4324 | 3606.2137 | 3945.2245 | 4270.3678 | 4583.123 | 4874.6652 | 5147.8004 | 5404.6749 | 5641.6945 | 5860.7448
48 | PMA | Southern | TS02 | Sorell | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.4757 | 1.6708 | 1.8174 | 1.958 | 2.0937 | 2.2205 | 2.3394 | 2.4516 | 2.5553 | 2.6514 | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958
48 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.31435 | 0.34859 | 0.37417 | 0.39867 | 0.42226 | 0.44416 | 0.46466 | 0.4839 | 0.50162 | 0.51798 | 314.355 | 348.5916 | 374.1659 | 398.6692 | 422.2581 | 444.1642 | 464.657 | 483.9021 | 501.6239 | 517.9751
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.071464 | 0.079621 | 0.085772 | 0.091629 | 0.097243 | 0.10245 | 0.1073 | 0.11184 | 0.11601 | 0.11984 | 71.4638 | 79.6206 | 85.7719 | 91.6286 | 97.2434 | 102.4486 | 107.2993 | 111.8408 | 116.0099 | 119.844
48 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.032926 | 0.036587 | 0.039356 | 0.042023 | 0.044605 | 0.047018 | 0.049289 | 0.051434 | 0.053422 | 0.055267 | 32.926 | 36.5869 | 39.3562 | 42.0228 | 44.6052 | 47.018 | 49.289 | 51.4342 | 53.4216 | 55.2667
48 | PMA | Western | TGO2 | Gordon | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0001499 | 0.0001675 | 0.00017669 | 0.00018544 | 0.00019381 | 0.00020156 | 0.00020877 | 0.00021551 | 0.00022168 | 0.00022735 | 0.1499 | 0.1675 | 0.17669 | 0.18544 | 0.19381 | 0.20156 | 0.20877 | 0.21551 | 0.22168 | 0.22735
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.25316 | 0.28289 | 0.29841 | 0.31318 | 0.32732 | 0.34041 | 0.35258 | 0.36396 | 0.37439 | 0.38397 | 253.161 | 282.8856 | 298.4135 | 313.183 | 327.3193 | 340.4054 | 352.5829 | 363.9633 | 374.3942 | 383.9707
48 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.085222 | 0.094846 | 0.10261 | 0.10997 | 0.11696 | 0.12338 | 0.12931 | 0.13482 | 0.13983 | 0.14439 | 85.2224 | 94.8455 | 102.6082 | 109.9685 | 116.9556 | 123.3784 | 129.3135 | 134.8181 | 139.8281 | 144.3936
48 | PMA | Southern | BEZ | Bellerive | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.0419 | 1.1909 | 1.3019 | 1.4084 | 1.5109 | 1.6063 | 1.6958 | 1.7799 | 1.8576 | 1.9293 | 1041.9233 | 1190.8799 | 1301.9176 | 1408.4133 | 1510.8517 | 1606.342 | 1695.8035 | 1779.9391 | 1857.5716 | 1929.3185
48 | PMA | Southern | CLZ | Claremont | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.6105 | 1.8225 | 1.9969 | 2.1617 | 2.3196 | 2.4656 | 2.6014 | 2.7283 | 2.8445 | 2.9512 | 1610.5236 | 1822.4644 | 1996.875 | 2161.7167 | 2319.6286 | 2465.5801 | 2601.3797 | 2728.283 | 2844.5293 | 2951.2371
48 | PMA | Southern | DPZ | Derwent Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5529 | 0.6239 | 0.68196 | 0.73694 | 0.78967 | 0.83847 | 0.88393 | 0.92646 | 0.96548 | 1.0013 | 552.8968 | 623.8984 | 681.963 | 736.9414 | 789.6705 | 838.4667 | 883.9278 | 926.4634 | 965.4778 | 1001.3383
48 | PMA | Southern | EHZ | East Hobart | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.2961 | 0.33363 | 0.36136 | 0.38763 | 0.41277 | 0.43593 | 0.45744 | 0.47749 | 0.49582 | 0.51261 | 296.0971 | 333.6307 | 361.3585 | 387.6322 | 412.7673 | 435.9341 | 457.4425 | 477.4948 | 495.8242 | 512.6094
48 | PMA | Southern | GBZ | Geilston Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.5678 | 1.7698 | 1.9205 | 2.0651 | 2.2043 | 2.3341 | 2.4558 | 2.5703 | 2.6761 | 2.7739 | 1567.7819 | 1769.8343 | 1920.4975 | 2065.0921 | 2204.284 | 2334.1028 | 2455.806 | 2570.3368 | 2676.0808 | 2773.8724
48 | PMA | Southern | GRZ | Gretna | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.012648 | 0.014088 | 0.015174 | 0.016208 | 0.0172 | 0.018119 | 0.018975 | 0.019777 | 0.020513 | 0.02119 | 12.6476 | 14.0878 | 15.174 | 16.2081 | 17.1996 | 18.1186 | 18.9752 | 19.7771 | 20.5132 | 21.1902
48 | PMA | Southern | HOZ | Howrah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.7293 | 1.9789 | 2.1649 | 2.3433 | 2.5149 | 2.6749 | 2.8247 | 2.9657 | 3.0957 | 3.2159 | 1729.3437 | 1978.8783 | 2164.8929 | 2343.2981 | 2514.9059 | 2674.874 | 2824.7421 | 2965.6878 | 3095.7393 | 3215.9308
48 | PMA | Southern | NTZ | New Town | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.8037 | 0.90882 | 0.99264 | 1.0718 | 1.1476 | 1.2176 | 1.2825 | 1.3431 | 1.3986 | 1.4494 | 803.7032 | 908.8158 | 992.6356 | 1071.8366 | 1147.6213 | 1217.5511 | 1282.5203 | 1343.142 | 1398.5913 | 1449.4108
48 | PMA | Southern | RIZ | Richmond | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.57898 | 0.65705 | 0.71793 | 0.77627 | 0.8325 | 0.88481 | 0.93381 | 0.97988 | 1.0224 | 1.0616 | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487
48 | PMA | Southern | RPZ | Rosny Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.1673 | 1.3275 | 1.4469 | 1.5615 | 1.6717 | 1.7744 | 1.8707 | 1.9612 | 2.0448 | 2.122 | 1167.2685 | 1327.4908 | 1446.9312 | 1561.4952 | 1671.7053 | 1774.447 | 1870.7102 | 1961.25 | 2044.7983 | 2122.019
48 | PMA | Southern | SBZ | Sandy Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 2.4644 | 2.7698 | 3.0006 | 3.2197 | 3.4295 | 3.6232 | 3.8034 | 3.9717 | 4.1258 | 4.2671 | 2464.3623 | 2769.833 | 3000.6076 | 3219.6772 | 3429.4579 | 3623.2062 | 3803.3935 | 3971.6735 | 4125.7653 | 4267.1277
48 | PMA | Southern | SUZ | Summerleas Road | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.2585 | 1.4179 | 1.5485 | 1.6733 | 1.7932 | 1.9047 | 2.009 | 2.107 | 2.1973 | 2.2806 | 1258.5428 | 1417.8673 | 1548.5069 | 1673.3006 | 1793.2045 | 1904.72 | 2009.0342 | 2107.025 | 2197.2799 | 2280.5702
48 | PMA | Southern | TWY2 | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.0029686 | 0.005667 | 0.0077019 | 0.0096394 | 0.011497 | 0.013219 | 0.014824 | 0.016326 | 0.017705 | 0.018973 | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735
48 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.14371 | 0.27826 | 0.37966 | 0.47589 | 0.56804 | 0.65312 | 0.73224 | 0.80611 | 0.87374 | 0.93578 | 143.7146 | 278.2634 | 379.658 | 475.892 | 568.0367 | 653.121 | 732.236 | 806.1095 | 873.7421 | 935.7763
48 | PMA | Southern | WTZ | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | Zs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | THZ | Trial Harbour | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.022922 | 0.037113 | 0.044654 | 0.051828 | 0.05869 | 0.065041 | 0.070949 | 0.076468 | 0.081525 | 0.086166 | 22.9219 | 37.1133 | 44.6536 | 51.8283 | 58.6899 | 65.0408 | 70.9488 | 76.4677 | 81.5247 | 86.1658
48 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.038245 | 0.063314 | 0.07791 | 0.091782 | 0.10503 | 0.11726 | 0.12863 | 0.13922 | 0.14892 | 0.1578 | 38.2451 | 63.3141 | 77.9097 | 91.7823 | 105.0266 | 117.2629 | 128.6268 | 139.2235 | 148.9168 | 157.7974
48 | PMA | total terminal |  | total terminal | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 61.9118 | 69.4632 | 75.7022 | 81.6506 | 87.349 | 92.6285 | 97.5498 | 102.1553 | 106.3826 | 110.2698 | 61911.7947 | 69463.2134 | 75702.2217 | 81650.5982 | 87349.0349 | 92628.4765 | 97549.8173 | 102155.2594 | 106382.6267 | 110269.7574
48 | PMA | total zone |  | total zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 14.8408 | 16.9747 | 18.6042 | 20.1583 | 21.6505 | 23.0359 | 24.3297 | 25.543 | 26.6587 | 27.6867 | 14840.7687 | 16974.7407 | 18604.154 | 20158.3179 | 21650.5385 | 23035.9046 | 24329.7252 | 25542.9628 | 26658.7429 | 27686.7492
48 | PMA | George Town | TC01 | Comalco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Camalco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TSW1 | Starwood | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Starwood | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | George Town | TTE1 | Temco | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Temco | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TAL2 | Ax-Arthurs Lake 6.6 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0.00064917 | 0.0007212 | 0.00077566 | 0.00082811 | 0.00087891 | 0.00092637 | 0.00097104 | 0.0010132 | 0.0010523 | 0.0010886 | 0.64917 | 0.7212 | 0.77566 | 0.82811 | 0.87891 | 0.92637 | 0.97104 | 1.0132 | 1.0523 | 1.0886
48 | PMA | North | TAV2 | Avoca 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.22958 | 0.26204 | 0.29118 | 0.31925 | 0.3461 | 0.37103 | 0.39432 | 0.41615 | 0.43622 | 0.45472 | 229.5798 | 262.0416 | 291.1835 | 319.246 | 346.0993 | 371.0291 | 394.3222 | 416.1455 | 436.222 | 454.715
48 | PMA | North | TDE2 | Derby 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.56922 | 0.63485 | 0.69251 | 0.7477 | 0.79989 | 0.84791 | 0.89239 | 0.93359 | 0.97114 | 1.0054 | 569.2204 | 634.8544 | 692.5107 | 747.7021 | 799.8929 | 847.9126 | 892.3895 | 933.5934 | 971.1352 | 1005.3678
48 | PMA | North | THA3 | Hadspen 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 5.594 | 6.3762 | 7.1135 | 7.8189 | 8.4918 | 9.1155 | 9.6963 | 10.2392 | 10.7373 | 11.1948 | 5593.967 | 6376.1529 | 7113.4569 | 7818.8826 | 8491.8215 | 9115.4758 | 9696.3055 | 10239.2168 | 10737.2588 | 11194.7564
48 | PMA | North | TMY2 | Mowbray 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.7848 | 1.9648 | 2.1296 | 2.2857 | 2.4344 | 2.5712 | 2.6979 | 2.8157 | 2.9232 | 3.0214 | 1784.8481 | 1964.7566 | 2129.6241 | 2285.6724 | 2434.3915 | 2571.1787 | 2697.8737 | 2815.7368 | 2923.2225 | 3021.4243
48 | PMA | North | TPM3 | Palmerston 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSD2 | Scottsdale 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.1449 | 1.2718 | 1.3856 | 1.4943 | 1.5973 | 1.6921 | 1.7799 | 1.8614 | 1.9357 | 2.0035 | 1144.9025 | 1271.8 | 1385.6446 | 1494.3068 | 1597.2659 | 1692.0602 | 1779.9103 | 1861.393 | 1935.6886 | 2003.4982
48 | PMA | North | TSL2 | St Leonards 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.4434 | 2.6818 | 2.9004 | 3.1074 | 3.3047 | 3.4862 | 3.6542 | 3.8106 | 3.9533 | 4.0836 | 2443.3811 | 2681.7732 | 2900.4355 | 3107.427 | 3304.695 | 3486.1592 | 3654.2466 | 3810.6275 | 3953.2512 | 4083.5657
48 | PMA | North | TSL3 | St Leonards 22 kV (scheduled load) | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Firmus Grid | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | North | TSM2 | St Marys 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.8961 | 2.0737 | 2.2147 | 2.3494 | 2.4786 | 2.5973 | 2.7078 | 2.8108 | 2.905 | 2.9914 | 1896.118 | 2073.7058 | 2214.748 | 2349.417 | 2478.5671 | 2597.346 | 2707.8062 | 2810.8256 | 2905.03 | 2991.3556
48 | PMA | Northwest | TDP2 | Devonport 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.4419 | 3.8174 | 4.126 | 4.4196 | 4.7 | 4.959 | 5.1996 | 5.4241 | 5.6294 | 5.8176 | 3441.8621 | 3817.4032 | 4126.0268 | 4419.5824 | 4700.0363 | 4958.9612 | 5199.635 | 5424.0693 | 5629.4072 | 5817.586
48 | PMA | Northwest | TEB2 | Emu Bay 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Emu Bay | MI | 0.26534 | 0.29275 | 0.31225 | 0.33053 | 0.34802 | 0.36396 | 0.37866 | 0.39227 | 0.40462 | 0.41584 | 265.3371 | 292.7451 | 312.2479 | 330.5276 | 348.0208 | 363.9613 | 378.6647 | 392.275 | 404.6173 | 415.8369
48 | PMA | Northwest | THM2 | Hampshire | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Hampshire | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TPL2 | Port Latta | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Port Latta | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TRA2 | Railton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TSH3 | Sheffield | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Northwest | TST2 | Smithton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.21307 | 0.24741 | 0.28166 | 0.31476 | 0.3456 | 0.3741 | 0.40037 | 0.42462 | 0.44666 | 0.46668 | 213.0668 | 247.4094 | 281.6624 | 314.7564 | 345.5951 | 374.1009 | 400.3736 | 424.6187 | 446.6622 | 466.6846
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 4.1166 | 4.5701 | 4.9342 | 5.2795 | 5.6085 | 5.9113 | 6.1917 | 6.4523 | 6.69 | 6.907 | 4116.5699 | 4570.097 | 4934.2228 | 5279.4811 | 5608.5022 | 5911.3163 | 6191.6824 | 6452.3257 | 6689.9917 | 6907.033
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.73429 | 0.82744 | 0.91217 | 0.9937 | 1.0723 | 1.1458 | 1.215 | 1.2802 | 1.3405 | 1.3964 | 734.2942 | 827.4446 | 912.1748 | 993.7003 | 1072.3061 | 1145.8406 | 1214.9565 | 1280.1575 | 1340.4996 | 1396.4433
48 | PMA | Southern | TBW2 | Bridgewater 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 2.9725 | 3.2896 | 3.5297 | 3.7611 | 3.9854 | 4.195 | 4.3925 | 4.5792 | 4.7523 | 4.9131 | 2972.4663 | 3289.5635 | 3529.7436 | 3761.1438 | 3985.3753 | 4195.0464 | 4392.539 | 4579.2239 | 4752.2984 | 4913.0967
48 | PMA | Southern | TBYA | Boyer SWA | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TBYB | Boyer SWB | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Boyer | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TCR2 | Creek Rd 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 4.5636 | 5.1389 | 5.5827 | 6.0034 | 6.4063 | 6.7785 | 7.1246 | 7.4479 | 7.744 | 8.0156 | 4563.6299 | 5138.933 | 5582.673 | 6003.4019 | 6406.3186 | 6778.4881 | 7124.6308 | 7447.9318 | 7743.9852 | 8015.6085
48 | PMA | Southern | TCS3 | Chapel St 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.9893 | 2.2592 | 2.4809 | 2.6903 | 2.8907 | 3.0757 | 3.2476 | 3.4081 | 3.555 | 3.6897 | 1989.2595 | 2259.1565 | 2480.9457 | 2690.32 | 2890.6985 | 3075.6964 | 3247.6354 | 3408.1374 | 3554.9975 | 3689.6523
48 | PMA | Southern | TDB2 | Derwent Bridge 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.010037 | 0.011187 | 0.012055 | 0.012881 | 0.013673 | 0.014407 | 0.015091 | 0.015732 | 0.01632 | 0.016861 | 10.0369 | 11.1874 | 12.0551 | 12.8811 | 13.6731 | 14.4073 | 15.0915 | 15.7321 | 16.3201 | 16.8609
48 | PMA | Southern | TEL2 | Electrona 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.46804 | 0.52105 | 0.56432 | 0.60568 | 0.64542 | 0.68239 | 0.71697 | 0.74946 | 0.77939 | 0.80702 | 468.0364 | 521.047 | 564.3236 | 605.6753 | 645.4209 | 682.387 | 716.9719 | 749.463 | 779.3929 | 807.0167
48 | PMA | Southern | THR2 | Huon River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Huon River | MI | 0.001407 | 0.0015801 | 0.0017183 | 0.0018512 | 0.0019797 | 0.0020995 | 0.0022121 | 0.0023183 | 0.0024165 | 0.0025074 | 1.407 | 1.5801 | 1.7183 | 1.8512 | 1.9797 | 2.0995 | 2.2121 | 2.3183 | 2.4165 | 2.5074
48 | PMA | Southern | TK12 | Kingston 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1922 | 3.5846 | 3.9058 | 4.2128 | 4.5078 | 4.7822 | 5.039 | 5.2802 | 5.5025 | 5.7076 | 3192.219 | 3584.623 | 3905.8354 | 4212.7778 | 4507.7941 | 4782.2149 | 5038.9766 | 5280.2171 | 5502.459 | 5707.5939
48 | PMA | Southern | TK13 | Kingston 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TKE2 | Kermandie 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.3827 | 0.42947 | 0.46676 | 0.50262 | 0.5373 | 0.56966 | 0.60007 | 0.62874 | 0.65526 | 0.67982 | 382.698 | 429.4741 | 466.7629 | 502.6209 | 537.3003 | 569.6585 | 600.071 | 628.7414 | 655.2563 | 679.8248
48 | PMA | Southern | TLF2 | Lindisfarne 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 2.5108 | 2.8549 | 3.1117 | 3.358 | 3.5951 | 3.8161 | 4.0232 | 4.2181 | 4.398 | 4.5643 | 2510.7635 | 2854.9382 | 3111.6989 | 3358.0279 | 3595.0685 | 3816.0948 | 4023.2369 | 4218.1141 | 4397.9871 | 4564.2812
48 | PMA | Southern | TMB2 | Meadowbank 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TMT2 | Mornington 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.594 | 4.1066 | 4.4887 | 4.8552 | 5.2077 | 5.5364 | 5.8443 | 6.1338 | 6.401 | 6.648 | 3593.9952 | 4106.5919 | 4488.7071 | 4855.2004 | 5207.7406 | 5536.3757 | 5844.2698 | 6133.8407 | 6401.0359 | 6647.9801
48 | PMA | Southern | TNH2 | North Hobart 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.79962 | 0.8991 | 0.97258 | 1.0422 | 1.1088 | 1.1702 | 1.2272 | 1.2804 | 1.329 | 1.3734 | 799.6171 | 899.097 | 972.5847 | 1042.2182 | 1108.834 | 1170.2327 | 1227.2359 | 1280.3796 | 1328.9571 | 1373.442
48 | PMA | Southern | TNN2 | New Norfolk 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Brynn Estyn | MI | 0.25239 | 0.28116 | 0.30285 | 0.32352 | 0.34335 | 0.36173 | 0.37887 | 0.39493 | 0.40967 | 0.42324 | 252.3942 | 281.1583 | 302.854 | 323.5219 | 343.3459 | 361.7304 | 378.8717 | 394.927 | 409.6728 | 423.24
48 | PMA | Southern | TR13 | Risdon 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Risdon | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Southern | TR14 | Risdon 33 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 1.6344 | 1.8461 | 2.0147 | 2.1742 | 2.3269 | 2.4679 | 2.599 | 2.7214 | 2.8334 | 2.9362 | 1634.3882 | 1846.1445 | 2014.7367 | 2174.1912 | 2326.8722 | 2467.8637 | 2598.9549 | 2721.3655 | 2833.419 | 2936.1986
48 | PMA | Southern | TRK2 | Rokeby 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 3.1514 | 3.6062 | 3.9452 | 4.2704 | 4.5831 | 4.8747 | 5.1478 | 5.4047 | 5.6417 | 5.8607 | 3151.4324 | 3606.2137 | 3945.2245 | 4270.3678 | 4583.123 | 4874.6652 | 5147.8004 | 5404.6749 | 5641.6945 | 5860.7448
48 | PMA | Southern | TS02 | Sorell | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.4757 | 1.6708 | 1.8174 | 1.958 | 2.0937 | 2.2205 | 2.3394 | 2.4516 | 2.5553 | 2.6514 | 1475.689 | 1670.7518 | 1817.4261 | 1958.011 | 2093.729 | 2220.4639 | 2339.4214 | 2451.6002 | 2555.3157 | 2651.3958
48 | PMA | Southern | TTB2 | Triabunna 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.31435 | 0.34859 | 0.37417 | 0.39867 | 0.42226 | 0.44416 | 0.46466 | 0.4839 | 0.50162 | 0.51798 | 314.355 | 348.5916 | 374.1659 | 398.6692 | 422.2581 | 444.1642 | 464.657 | 483.9021 | 501.6239 | 517.9751
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.071464 | 0.079621 | 0.085772 | 0.091629 | 0.097243 | 0.10245 | 0.1073 | 0.11184 | 0.11601 | 0.11984 | 71.4638 | 79.6206 | 85.7719 | 91.6286 | 97.2434 | 102.4486 | 107.2993 | 111.8408 | 116.0099 | 119.844
48 | PMA | Southern | TWA2 | Waddamana 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.032926 | 0.036587 | 0.039356 | 0.042023 | 0.044605 | 0.047018 | 0.049289 | 0.051434 | 0.053422 | 0.055267 | 32.926 | 36.5869 | 39.3562 | 42.0228 | 44.6052 | 47.018 | 49.289 | 51.4342 | 53.4216 | 55.2667
48 | PMA | Western | TGO2 | Gordon | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TNT2 | Newton 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.0001499 | 0.0001675 | 0.00017669 | 0.00018544 | 0.00019381 | 0.00020156 | 0.00020877 | 0.00021551 | 0.00022168 | 0.00022735 | 0.1499 | 0.1675 | 0.17669 | 0.18544 | 0.19381 | 0.20156 | 0.20877 | 0.21551 | 0.22168 | 0.22735
48 | PMA | Western | TNT3 | Ax-Newton 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | Ax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQT2 | Queenstown 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.25316 | 0.28289 | 0.29841 | 0.31318 | 0.32732 | 0.34041 | 0.35258 | 0.36396 | 0.37439 | 0.38397 | 253.161 | 282.8856 | 298.4135 | 313.183 | 327.3193 | 340.4054 | 352.5829 | 363.9633 | 374.3942 | 383.9707
48 | PMA | Western | TQT3 | Queenstown 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Queenstown 11 kV | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TQU2 | Que | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Que | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TRB2 | Rosebery 44 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Rosebery | MI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | PMA | Western | TSR2 | Savage River | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | Savage River | MI | 0.085222 | 0.094846 | 0.10261 | 0.10997 | 0.11696 | 0.12338 | 0.12931 | 0.13482 | 0.13983 | 0.14439 | 85.2224 | 94.8455 | 102.6082 | 109.9685 | 116.9556 | 123.3784 | 129.3135 | 134.8181 | 139.8281 | 144.3936
48 | PMA | Southern | BEZ | Bellerive | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.0419 | 1.1909 | 1.3019 | 1.4084 | 1.5109 | 1.6063 | 1.6958 | 1.7799 | 1.8576 | 1.9293 | 1041.9233 | 1190.8799 | 1301.9176 | 1408.4133 | 1510.8517 | 1606.342 | 1695.8035 | 1779.9391 | 1857.5716 | 1929.3185
48 | PMA | Southern | CLZ | Claremont | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.6105 | 1.8225 | 1.9969 | 2.1617 | 2.3196 | 2.4656 | 2.6014 | 2.7283 | 2.8445 | 2.9512 | 1610.5236 | 1822.4644 | 1996.875 | 2161.7167 | 2319.6286 | 2465.5801 | 2601.3797 | 2728.283 | 2844.5293 | 2951.2371
48 | PMA | Southern | DPZ | Derwent Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.5529 | 0.6239 | 0.68196 | 0.73694 | 0.78967 | 0.83847 | 0.88393 | 0.92646 | 0.96548 | 1.0013 | 552.8968 | 623.8984 | 681.963 | 736.9414 | 789.6705 | 838.4667 | 883.9278 | 926.4634 | 965.4778 | 1001.3383
48 | PMA | Southern | EHZ | East Hobart | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.2961 | 0.33363 | 0.36136 | 0.38763 | 0.41277 | 0.43593 | 0.45744 | 0.47749 | 0.49582 | 0.51261 | 296.0971 | 333.6307 | 361.3585 | 387.6322 | 412.7673 | 435.9341 | 457.4425 | 477.4948 | 495.8242 | 512.6094
48 | PMA | Southern | GBZ | Geilston Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.5678 | 1.7698 | 1.9205 | 2.0651 | 2.2043 | 2.3341 | 2.4558 | 2.5703 | 2.6761 | 2.7739 | 1567.7819 | 1769.8343 | 1920.4975 | 2065.0921 | 2204.284 | 2334.1028 | 2455.806 | 2570.3368 | 2676.0808 | 2773.8724
48 | PMA | Southern | GRZ | Gretna | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.012648 | 0.014088 | 0.015174 | 0.016208 | 0.0172 | 0.018119 | 0.018975 | 0.019777 | 0.020513 | 0.02119 | 12.6476 | 14.0878 | 15.174 | 16.2081 | 17.1996 | 18.1186 | 18.9752 | 19.7771 | 20.5132 | 21.1902
48 | PMA | Southern | HOZ | Howrah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 1.7293 | 1.9789 | 2.1649 | 2.3433 | 2.5149 | 2.6749 | 2.8247 | 2.9657 | 3.0957 | 3.2159 | 1729.3437 | 1978.8783 | 2164.8929 | 2343.2981 | 2514.9059 | 2674.874 | 2824.7421 | 2965.6878 | 3095.7393 | 3215.9308
48 | PMA | Southern | NTZ | New Town | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.8037 | 0.90882 | 0.99264 | 1.0718 | 1.1476 | 1.2176 | 1.2825 | 1.3431 | 1.3986 | 1.4494 | 803.7032 | 908.8158 | 992.6356 | 1071.8366 | 1147.6213 | 1217.5511 | 1282.5203 | 1343.142 | 1398.5913 | 1449.4108
48 | PMA | Southern | RIZ | Richmond | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.57898 | 0.65705 | 0.71793 | 0.77627 | 0.8325 | 0.88481 | 0.93381 | 0.97988 | 1.0224 | 1.0616 | 578.9777 | 657.0494 | 717.9344 | 776.2682 | 832.4996 | 884.8076 | 933.8064 | 979.8838 | 1022.3787 | 1061.6487
48 | PMA | Southern | RPZ | Rosny Park | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.1673 | 1.3275 | 1.4469 | 1.5615 | 1.6717 | 1.7744 | 1.8707 | 1.9612 | 2.0448 | 2.122 | 1167.2685 | 1327.4908 | 1446.9312 | 1561.4952 | 1671.7053 | 1774.447 | 1870.7102 | 1961.25 | 2044.7983 | 2122.019
48 | PMA | Southern | SBZ | Sandy Bay | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 2.4644 | 2.7698 | 3.0006 | 3.2197 | 3.4295 | 3.6232 | 3.8034 | 3.9717 | 4.1258 | 4.2671 | 2464.3623 | 2769.833 | 3000.6076 | 3219.6772 | 3429.4579 | 3623.2062 | 3803.3935 | 3971.6735 | 4125.7653 | 4267.1277
48 | PMA | Southern | SUZ | Summerleas Road | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 1.2585 | 1.4179 | 1.5485 | 1.6733 | 1.7932 | 1.9047 | 2.009 | 2.107 | 2.1973 | 2.2806 | 1258.5428 | 1417.8673 | 1548.5069 | 1673.3006 | 1793.2045 | 1904.72 | 2009.0342 | 2107.025 | 2197.2799 | 2280.5702
48 | PMA | Southern | TWY2 | Wayatinah | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.0029686 | 0.005667 | 0.0077019 | 0.0096394 | 0.011497 | 0.013219 | 0.014824 | 0.016326 | 0.017705 | 0.018973 | 2.9686 | 5.667 | 7.7019 | 9.6394 | 11.4969 | 13.2188 | 14.8235 | 16.3259 | 17.7051 | 18.9735
48 | PMA | Southern | WHZ | West Hobart Zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.14371 | 0.27826 | 0.37966 | 0.47589 | 0.56804 | 0.65312 | 0.73224 | 0.80611 | 0.87374 | 0.93578 | 143.7146 | 278.2634 | 379.658 | 475.892 | 568.0367 | 653.121 | 732.236 | 806.1095 | 873.7421 | 935.7763
48 | PMA | Western | THZ | Trial Harbour | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.022922 | 0.037113 | 0.044654 | 0.051828 | 0.05869 | 0.065041 | 0.070949 | 0.076468 | 0.081525 | 0.086166 | 22.9219 | 37.1133 | 44.6536 | 51.8283 | 58.6899 | 65.0408 | 70.9488 | 76.4677 | 81.5247 | 86.1658
48 | PMA | Western | RBZ | Rosebery 22 kV | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.038245 | 0.063314 | 0.07791 | 0.091782 | 0.10503 | 0.11726 | 0.12863 | 0.13922 | 0.14892 | 0.1578 | 38.2451 | 63.3141 | 77.9097 | 91.7823 | 105.0266 | 117.2629 | 128.6268 | 139.2235 | 148.9168 | 157.7974
48 | PMA | total terminal |  | total terminal | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 61.9118 | 69.4632 | 75.7022 | 81.6506 | 87.349 | 92.6285 | 97.5498 | 102.1553 | 106.3826 | 110.2698 | 61911.7947 | 69463.2134 | 75702.2217 | 81650.5982 | 87349.0349 | 92628.4765 | 97549.8173 | 102155.2594 | 106382.6267 | 110269.7574
48 | PMA | total zone |  | total zone | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | #N/A | #N/A | 14.8408 | 16.9747 | 18.6042 | 20.1583 | 21.6505 | 23.0359 | 24.3297 | 25.543 | 26.6587 | 27.6867 | 14840.7687 | 16974.7407 | 18604.154 | 20158.3179 | 21650.5385 | 23035.9046 | 24329.7252 | 25542.9628 | 26658.7429 | 27686.7492
48 | PMA | George Town | TGT3 | George Town 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.1365 | 0.15152 | 0.16575 | 0.17918 | 0.19212 | 0.20409 | 0.21525 | 0.22571 | 0.2353 | 0.24412 | 136.5015 | 151.5159 | 165.7462 | 179.1831 | 192.1189 | 204.0912 | 215.2525 | 225.706 | 235.2999 | 244.125
48 | PMA | North | TNW2 | Norwood 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6318 | 1.8109 | 1.9756 | 2.132 | 2.2812 | 2.4189 | 2.5467 | 2.6658 | 2.7747 | 2.8744 | 1631.8478 | 1810.9378 | 1975.5555 | 2131.9918 | 2281.2469 | 2418.8879 | 2546.6736 | 2665.787 | 2774.6763 | 2874.3881
48 | PMA | North | TTR2 | Trevallyn 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 3.4526 | 3.8708 | 4.2615 | 4.6326 | 4.9873 | 5.3153 | 5.6203 | 5.9051 | 6.166 | 6.4054 | 3452.6345 | 3870.7926 | 4261.5278 | 4632.6151 | 4987.3204 | 5315.3177 | 5620.2699 | 5905.1422 | 6166.0336 | 6405.3899
48 | PMA | Northwest | TBU3 | Burnie 22 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6825 | 1.863 | 2.0037 | 2.1363 | 2.2628 | 2.379 | 2.4864 | 2.5861 | 2.677 | 2.7598 | 1682.5056 | 1862.9759 | 2003.7295 | 2136.33 | 2262.8173 | 2378.9627 | 2486.3559 | 2586.1192 | 2676.9508 | 2759.8075
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | low | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.10628 | 0.11915 | 0.12942 | 0.1393 | 0.14884 | 0.15775 | 0.16612 | 0.17401 | 0.1813 | 0.18806 | 106.283 | 119.1528 | 129.4229 | 139.2966 | 148.8434 | 157.7501 | 166.1198 | 174.0091 | 181.3041 | 188.0626
48 | PMA | Southern | CAZ | Cambridge | low | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.41211 | 0.47245 | 0.51749 | 0.56069 | 0.60225 | 0.641 | 0.6773 | 0.71145 | 0.74295 | 0.77208 | 412.1061 | 472.452 | 517.4937 | 560.6932 | 602.2526 | 640.9977 | 677.3 | 711.4454 | 742.9549 | 772.0788
48 | PMA | Southern | TTU2 | Tungatinah 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.071515 | 0.079889 | 0.086448 | 0.09284 | 0.09908 | 0.10498 | 0.11059 | 0.11595 | 0.12106 | 0.12594 | 71.5148 | 79.8894 | 86.4482 | 92.8402 | 99.0801 | 104.9803 | 110.5911 | 115.9508 | 121.0576 | 125.9425
48 | PMA | Northwest | TUL2 | Ulverstone 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 4.1197 | 4.5862 | 4.9744 | 5.3512 | 5.7168 | 6.0601 | 6.3844 | 6.6919 | 6.983 | 7.2595 | 4119.6579 | 4586.1667 | 4974.4162 | 5351.2219 | 5716.8459 | 6060.0787 | 6384.3523 | 6691.9362 | 6983.0196 | 7259.5299
48 | PMA | Southern | TWA2 | Waddamana 22 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.032949 | 0.036708 | 0.039661 | 0.042572 | 0.045442 | 0.048177 | 0.050804 | 0.053336 | 0.055771 | 0.058122 | 32.9494 | 36.7083 | 39.6613 | 42.572 | 45.4421 | 48.1772 | 50.8042 | 53.3361 | 55.7709 | 58.1219
48 | PMA | Southern | TWY2 | Wayatinah | base | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | RT | 0.0029855 | 0.0057559 | 0.0079257 | 0.01004 | 0.012104 | 0.014056 | 0.015912 | 0.017686 | 0.019375 | 0.020991 | 2.9855 | 5.7559 | 7.9257 | 10.0402 | 12.1045 | 14.0563 | 15.9125 | 17.6855 | 19.375 | 20.991
48 | PMA | Northwest | TWV2 | Wesley Vale 11 kV | base | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | Wesley Vale | MI | 0.73501 | 0.83114 | 0.9215 | 1.0105 | 1.0978 | 1.1812 | 1.2612 | 1.3381 | 1.412 | 1.4833 | 735.0057 | 831.1439 | 921.5004 | 1010.4842 | 1097.8487 | 1181.2098 | 1261.1601 | 1338.1141 | 1412.0384 | 1483.3205
48 | PMA | Southern | WHZ | West Hobart Zone | base | maximum | PV | non-coincident | POE50 | summer | zone | zone plus embedded | MW | 0 | Zs | 0.14457 | 0.28273 | 0.39083 | 0.49585 | 0.59825 | 0.6947 | 0.7862 | 0.87338 | 0.95622 | 1.0353 | 144.5702 | 282.7273 | 390.8252 | 495.8534 | 598.2517 | 694.6954 | 786.2039 | 873.3845 | 956.2244 | 1035.2589
48 | PMA | George Town | TGT3 | George Town 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 0.13674 | 0.15278 | 0.16892 | 0.18489 | 0.20082 | 0.21649 | 0.23201 | 0.24744 | 0.26281 | 0.27803 | 136.7416 | 152.7804 | 168.9211 | 184.8901 | 200.823 | 216.4935 | 232.005 | 247.4426 | 262.8074 | 278.0262
48 | PMA | North | TNW2 | Norwood 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6346 | 1.8255 | 2.0123 | 2.1981 | 2.382 | 2.5621 | 2.7397 | 2.9156 | 3.0899 | 3.2619 | 1634.6275 | 1825.4959 | 2012.2889 | 2198.1486 | 2381.9643 | 2562.108 | 2739.679 | 2915.5619 | 3089.9266 | 3261.8557
48 | PMA | North | TTR2 | Trevallyn 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 3.4592 | 3.9053 | 4.3487 | 4.7896 | 5.2264 | 5.6557 | 6.0795 | 6.5002 | 6.918 | 7.3307 | 3459.1868 | 3905.2851 | 4348.6743 | 4789.5671 | 5226.4461 | 5655.7384 | 6079.5166 | 6500.1851 | 6917.973 | 7330.7104
48 | PMA | Northwest | TBU3 | Burnie 22 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal plus embedded | MW | 0 | RT | 1.6849 | 1.8756 | 2.0353 | 2.1928 | 2.3486 | 2.5006 | 2.6498 | 2.7971 | 2.9425 | 3.0854 | 1684.9267 | 1875.585 | 2035.2676 | 2192.8229 | 2348.5934 | 2500.5822 | 2649.8089 | 2797.1013 | 2942.5351 | 3085.3873
48 | PMA | Southern | TKR2 | Knights Rd 11 kV | high | maximum | PV | non-coincident | POE50 | summer | terminal | terminal | MW | 0 | RT | 0.10646 | 0.12006 | 0.13172 | 0.14345 | 0.15521 | 0.16688 | 0.17851 | 0.19016 | 0.20185 | 0.2135 | 106.4572 | 120.0606 | 131.7181 | 143.4544 | 155.214 | 166.8754 | 178.5082 | 190.1613 | 201.8465 | 213.5035
48 | PMA | Southern | CAZ | Cambridge | high | maximum | PV | non-coincident | POE50 | summer | zone | zone | MW | 0 | Zs | 0.41285 | 0.47638 | 0.52751 | 0.57884 | 0.63004 | 0.68076 | 0.73121 | 0.78165 | 0.83211 | 0.88234 | 412.8455 | 476.3789 | 527.506 | 578.8434 | 630.0357 | 680.7593 | 731.2125 | 781.646 | 832.1149 | 882.3446

## Feeder DER
| NET DER AVERAGE DAY MAX DEMAND IMPACT (kW) | [9 empty] | NET DER AVERAGE DAY MIN DEMAND IMPACT (kW)
Feeder | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
12017 | 54.2933 | 102.2039 | 158.3107 | 220.7165 | 284.3494 | 354.0076 | 431.3843 | 598.2703 | 738.3074 | 868.9035 | -486.3746 | -595.3591 | -714.055 | -829.7761 | -931.7136 | -1024.1476 | -1111.5569 | -1211.1373 | -1310.2904 | -1397.0625
12018 | 32.9689 | 62.1469 | 97.0035 | 137.1205 | 179.2653 | 227.3641 | 281.999 | 402.3861 | 502.1691 | 594.8805 | -273.9201 | -339.7522 | -411.9875 | -482.8333 | -545.5396 | -602.4505 | -656.3133 | -715.6078 | -774.8986 | -825.1967
12019 | 40.2314 | 75.8369 | 118.3718 | 167.3259 | 218.7545 | 277.4486 | 344.1188 | 491.0252 | 612.7887 | 725.9229 | -334.2601 | -414.5941 | -502.7416 | -589.1935 | -665.713 | -735.1604 | -800.8883 | -873.2445 | -945.596 | -1006.9739
12030 | 40.1108 | 78.0333 | 122.7522 | 173.0762 | 224.9365 | 282.2755 | 346.8155 | 486.6118 | 603.332 | 712.2669 | -348.5289 | -434.6431 | -528.7031 | -620.6053 | -701.6979 | -775.2374 | -844.7795 | -922.756 | -1001.2648 | -1069.2707
12031 | 54.2594 | 106.9521 | 168.6114 | 237.0603 | 306.7504 | 382.9378 | 467.3643 | 648.1011 | 801.2346 | 944.5103 | -485.1165 | -605.1924 | -735.9888 | -863.4962 | -975.798 | -1077.5944 | -1173.8128 | -1283.0736 | -1393.0631 | -1489.5553
12032 | 25.9172 | 48.8854 | 76.3211 | 107.894 | 141.0599 | 178.9087 | 221.8988 | 316.6229 | 395.1343 | 468.0795 | -215.432 | -267.2496 | -324.1029 | -379.858 | -429.2034 | -473.9849 | -516.3648 | -563.02 | -609.6656 | -649.232
12033 | 13.3228 | 25.103 | 39.1239 | 55.1612 | 71.9205 | 90.8745 | 112.403 | 159.409 | 198.6279 | 235.0918 | -112.3188 | -138.9381 | -168.1057 | -196.6804 | -221.9496 | -244.8797 | -266.5784 | -290.577 | -314.6395 | -335.138
12035 | 31.6386 | 59.6394 | 93.0895 | 131.5878 | 172.0321 | 218.1902 | 270.6206 | 386.1503 | 481.9071 | 570.8777 | -262.8677 | -326.0436 | -395.3642 | -463.3515 | -523.5276 | -578.1422 | -629.8317 | -686.7338 | -743.6322 | -791.9008
12036 | 0.071906 | 0.13554 | 0.21157 | 0.29906 | 0.39098 | 0.49589 | 0.61505 | 0.87761 | 1.0952 | 1.2974 | -0.59743 | -0.74101 | -0.89856 | -1.0531 | -1.1898 | -1.314 | -1.4314 | -1.5608 | -1.6901 | -1.7998
12037 | 8.4849 | 15.9942 | 24.9649 | 35.2895 | 46.1359 | 58.5146 | 72.5755 | 103.5585 | 129.2387 | 153.099 | -70.4963 | -87.439 | -106.0295 | -124.2624 | -140.4006 | -155.0472 | -168.9094 | -184.1695 | -199.4286 | -212.3734
12038 | 34.5554 | 66.0629 | 103.1682 | 144.8287 | 187.6697 | 234.9395 | 288.0551 | 402.9428 | 498.9333 | 588.4701 | -304.7631 | -376.3566 | -454.5254 | -530.8912 | -598.276 | -659.4108 | -717.2492 | -782.4129 | -847.7106 | -904.4695
12039 | 41.0023 | 77.9867 | 122.1155 | 172.8277 | 226.0383 | 286.7074 | 355.5773 | 507.243 | 632.934 | 749.6685 | -342.922 | -426.2852 | -517.6585 | -607.1726 | -686.3111 | -758.0618 | -825.899 | -900.6111 | -975.1688 | -1038.3199
13043 | 12.2294 | 24.8069 | 39.7159 | 56.7215 | 74.4599 | 94.6012 | 117.3941 | 167.5005 | 208.944 | 247.3363 | -109.4664 | -137.6047 | -168.2366 | -198.0169 | -224.135 | -247.6325 | -269.6725 | -293.8465 | -317.6991 | -337.6444
13044 | 9.2304 | 18.1183 | 28.8145 | 41.3312 | 54.6864 | 70.1919 | 87.9431 | 127.73 | 160.3671 | 190.7057 | -95.0164 | -114.7418 | -136.3115 | -157.3135 | -175.7279 | -192.2105 | -207.5824 | -223.3786 | -239.1969 | -252.3098
13045 | 40.5973 | 82.3793 | 132.039 | 188.9679 | 248.6225 | 316.6926 | 393.9094 | 564.4298 | 705.1509 | 835.5835 | -379.5919 | -472.8185 | -574.3286 | -672.9622 | -759.3797 | -836.9662 | -909.5777 | -987.9288 | -1065.6278 | -1130.268
13046 | 0.20925 | 0.41074 | 0.65322 | 0.93698 | 1.2397 | 1.5913 | 1.9937 | 2.8956 | 3.6355 | 4.3233 | -2.154 | -2.6012 | -3.0902 | -3.5663 | -3.9838 | -4.3574 | -4.7059 | -5.064 | -5.4226 | -5.7199
13047 | 4.1646 | 8.4724 | 13.5877 | 19.4428 | 25.5698 | 32.5515 | 40.4658 | 57.9223 | 72.3352 | 85.6912 | -38.6313 | -48.2469 | -58.7136 | -68.8822 | -77.7909 | -85.7909 | -93.2799 | -101.3931 | -109.4249 | -116.112
13048 | 9.1374 | 17.9358 | 28.5241 | 40.9147 | 54.1354 | 69.4847 | 87.057 | 126.4431 | 158.7513 | 188.7843 | -94.0591 | -113.5857 | -134.9381 | -155.7285 | -173.9574 | -190.2739 | -205.4909 | -221.128 | -236.7869 | -249.7676
13049 | 23.3665 | 45.8663 | 72.9434 | 104.6293 | 138.438 | 177.6898 | 222.6267 | 323.3468 | 405.9672 | 482.769 | -240.5327 | -290.4673 | -345.0707 | -398.237 | -444.8528 | -486.5782 | -525.4919 | -565.4799 | -605.5237 | -638.7188
13050 | 10.0474 | 18.9885 | 29.675 | 41.9882 | 54.9377 | 69.7349 | 86.5522 | 123.6544 | 154.3835 | 182.9358 | -84.7249 | -104.8757 | -126.9813 | -148.6513 | -167.8197 | -185.201 | -201.6358 | -219.6432 | -237.6674 | -252.9301
13052 | 21.2635 | 43.3917 | 69.5744 | 99.3487 | 130.322 | 165.3953 | 205.0292 | 291.9517 | 363.9126 | 430.5423 | -187.5498 | -237.0847 | -290.9722 | -343.3397 | -389.2564 | -430.5772 | -469.3478 | -512.1767 | -554.2965 | -589.5573
13053 | 22.6282 | 46.6191 | 74.9814 | 107.2026 | 140.695 | 178.5997 | 221.415 | 315.2922 | 392.9899 | 464.9062 | -201.5739 | -255.2257 | -313.5395 | -370.1509 | -419.7351 | -464.3098 | -506.0882 | -552.2149 | -597.5065 | -635.3546
13054 | 5.2897 | 10.5942 | 16.929 | 24.2493 | 31.9741 | 40.8506 | 50.9563 | 73.4067 | 91.8889 | 109.0398 | -51.4479 | -63.2594 | -76.1413 | -88.6681 | -99.6465 | -109.4917 | -118.6932 | -128.4266 | -138.144 | -146.205
13055 | 28.0107 | 57.751 | 92.9005 | 132.813 | 174.2818 | 221.1926 | 274.1684 | 390.2768 | 486.3903 | 575.3455 | -248.803 | -315.3214 | -387.6133 | -457.7922 | -519.2595 | -574.5212 | -626.3208 | -683.5824 | -739.7785 | -786.7511
13056 | 20.1354 | 38.564 | 60.5497 | 85.8233 | 112.3524 | 142.6205 | 176.9868 | 252.7335 | 315.4599 | 373.7065 | -171.3202 | -212.7964 | -258.2247 | -302.6842 | -341.9457 | -377.4944 | -411.0576 | -447.8705 | -484.6041 | -515.6409
13057 | 48.4501 | 97.9091 | 155.4446 | 218.9932 | 283.4427 | 353.7379 | 431.5883 | 599.3078 | 739.847 | 870.6418 | -475.6193 | -586.6659 | -706.6615 | -822.6286 | -923.8781 | -1014.9214 | -1100.3092 | -1196.9709 | -1292.7743 | -1375.6843
13058 | 0.62776 | 1.2322 | 1.9597 | 2.8109 | 3.7192 | 4.7738 | 5.981 | 8.6869 | 10.9066 | 12.9699 | -6.4621 | -7.8036 | -9.2706 | -10.6989 | -11.9513 | -13.0723 | -14.1177 | -15.192 | -16.2678 | -17.1596
14060 | 2.976 | 5.8417 | 9.2903 | 13.3259 | 17.6319 | 22.6311 | 28.3544 | 41.1825 | 51.7053 | 61.487 | -30.635 | -36.9948 | -43.9493 | -50.7207 | -56.6579 | -61.9722 | -66.9283 | -72.0213 | -77.1214 | -81.3493
14061 | 1.2555 | 2.4645 | 3.9193 | 5.6219 | 7.4385 | 9.5475 | 11.962 | 17.3739 | 21.8132 | 25.9398 | -12.9241 | -15.6072 | -18.5411 | -21.3978 | -23.9025 | -26.1445 | -28.2354 | -30.384 | -32.5356 | -34.3192
14062 | 0.25575 | 0.50202 | 0.79839 | 1.1452 | 1.5152 | 1.9449 | 2.4367 | 3.5391 | 4.4434 | 5.284 | -2.6327 | -3.1792 | -3.7769 | -4.3588 | -4.869 | -5.3257 | -5.7517 | -6.1893 | -6.6276 | -6.991
14063 | 5.8358 | 11.4552 | 18.2177 | 26.1313 | 34.5751 | 44.3783 | 55.6013 | 80.7563 | 101.3908 | 120.5721 | -60.0734 | -72.5446 | -86.1818 | -99.4602 | -111.1025 | -121.5235 | -131.2423 | -141.2293 | -151.2303 | -159.5208
14064 | 1.302 | 2.5557 | 4.0645 | 5.8301 | 7.714 | 9.9011 | 12.4051 | 18.0173 | 22.6211 | 26.9006 | -13.4028 | -16.1852 | -19.2278 | -22.1903 | -24.7878 | -27.1128 | -29.2811 | -31.5093 | -33.7406 | -35.5903
14065 | 7.1146 | 13.9653 | 22.2096 | 31.8573 | 42.1513 | 54.1026 | 67.7848 | 98.4519 | 123.6079 | 146.9923 | -73.2368 | -88.4408 | -105.0663 | -121.2542 | -135.4477 | -148.1522 | -160.0005 | -172.176 | -184.3684 | -194.4756
14066 | 1.8135 | 3.5598 | 5.6613 | 8.1205 | 10.7444 | 13.7909 | 17.2785 | 25.0956 | 31.5079 | 37.4686 | -18.6682 | -22.5437 | -26.7816 | -30.9079 | -34.5259 | -37.7643 | -40.7844 | -43.888 | -46.9959 | -49.5722
14067 | 2.697 | 5.294 | 8.4193 | 12.0766 | 15.9789 | 20.5095 | 25.6962 | 37.3216 | 46.8579 | 55.7226 | -27.763 | -33.5266 | -39.8291 | -45.9657 | -51.3462 | -56.1623 | -60.6538 | -65.2693 | -69.8913 | -73.7228
14068 | 3.8595 | 7.5759 | 12.0484 | 17.2821 | 22.8664 | 29.3498 | 36.7722 | 53.4085 | 67.0553 | 79.7409 | -39.7298 | -47.9777 | -56.9968 | -65.7784 | -73.4782 | -80.3701 | -86.7977 | -93.4027 | -100.0169 | -105.4998
14069 | 2.3837 | 4.6962 | 7.4753 | 10.7197 | 14.1738 | 18.1778 | 22.7563 | 33.0021 | 41.4122 | 49.2275 | -24.2902 | -29.4258 | -35.0388 | -40.5027 | -45.293 | -49.5823 | -53.5842 | -57.7194 | -61.8579 | -65.2891
14070 | 3.162 | 6.2068 | 9.8709 | 14.1588 | 18.7339 | 24.0456 | 30.1266 | 43.7564 | 54.9368 | 65.3299 | -32.5497 | -39.307 | -46.6961 | -53.8908 | -60.199 | -65.8454 | -71.1113 | -76.5227 | -81.9415 | -86.4336
14071 | 0.02325 | 0.045638 | 0.072581 | 0.10411 | 0.13775 | 0.17681 | 0.22152 | 0.32174 | 0.40395 | 0.48037 | -0.23934 | -0.28902 | -0.34335 | -0.39626 | -0.44264 | -0.48416 | -0.52288 | -0.56267 | -0.60251 | -0.63554
16091 | 30.3247 | 64.4743 | 105.4487 | 152.4436 | 201.6071 | 256.9337 | 319.7731 | 455.936 | 570.9496 | 679.2636 | -293.4069 | -372.5552 | -460.7117 | -548.8517 | -628.5693 | -702.6883 | -774.592 | -857.9249 | -943.0252 | -1018.9416
16092 | 16.8033 | 35.726 | 58.4305 | 84.4709 | 111.713 | 142.3702 | 177.1903 | 252.6399 | 316.3703 | 376.3885 | -162.5805 | -206.4375 | -255.2861 | -304.1256 | -348.2981 | -389.3684 | -429.2111 | -475.3869 | -522.5421 | -564.6083
16093 | 7.5352 | 16.0209 | 26.2024 | 37.8799 | 50.0963 | 63.8441 | 79.4588 | 113.2932 | 141.8723 | 168.7867 | -72.9072 | -92.5743 | -114.4799 | -136.3813 | -156.1899 | -174.6074 | -192.4744 | -213.1813 | -234.3275 | -253.1915
16094 | 28.3522 | 60.2671 | 98.5569 | 142.4685 | 188.4027 | 240.0923 | 298.7985 | 426.0024 | 533.442 | 634.6176 | -274.111 | -348.0729 | -430.4447 | -512.7921 | -587.2618 | -656.4937 | -723.6486 | -801.4701 | -880.9339 | -951.8072
16095 | 4.9461 | 10.3711 | 16.8431 | 24.22 | 31.8976 | 40.5053 | 50.2573 | 71.3547 | 89.1045 | 105.7595 | -45.5608 | -58.0566 | -71.8867 | -85.6151 | -97.937 | -109.3082 | -120.2558 | -132.862 | -145.6372 | -156.8755
16096 | 32.8853 | 67.591 | 108.9824 | 156.3207 | 205.7632 | 261.5648 | 324.8754 | 462.6771 | 578.1721 | 685.9383 | -305.894 | -385.0265 | -472.1798 | -558.1131 | -634.6498 | -704.6471 | -771.4165 | -846.4789 | -922.2181 | -987.7464
16097 | 6.3577 | 13.2462 | 21.4416 | 30.755 | 40.4238 | 51.2443 | 63.4882 | 89.9555 | 112.1797 | 132.9952 | -57.2191 | -73.0389 | -90.4946 | -107.7616 | -123.2016 | -137.3974 | -151.0122 | -166.6525 | -182.4122 | -196.1874
16098 | 32.4306 | 68.1062 | 110.7066 | 159.3196 | 209.9642 | 266.7939 | 331.2091 | 470.6317 | 587.995 | 698.1652 | -301.2808 | -383.5094 | -474.5991 | -565.1076 | -646.4271 | -721.545 | -793.9362 | -877.296 | -961.9256 | -1036.494
17100 | 1.5731 | 3.3115 | 5.3988 | 7.797 | 10.3098 | 13.1435 | 16.3646 | 23.3568 | 29.2598 | 34.8142 | -15.1059 | -19.1281 | -23.6065 | -28.081 | -32.1243 | -35.8792 | -39.5174 | -43.7139 | -48.0001 | -51.816
17101 | 16.8337 | 34.2829 | 54.4901 | 76.7592 | 99.3538 | 124.072 | 151.5162 | 209.9095 | 259.5426 | 306.1707 | -182.0786 | -220.4229 | -261.492 | -300.7192 | -334.5402 | -364.5245 | -392.247 | -422.4338 | -452.7082 | -479.0854
17102 | 0.026255 | 0.055822 | 0.091298 | 0.13199 | 0.17455 | 0.22245 | 0.27686 | 0.39475 | 0.49433 | 0.58811 | -0.25403 | -0.32256 | -0.39888 | -0.4752 | -0.54422 | -0.60839 | -0.67064 | -0.74279 | -0.81647 | -0.8822
17103 | 16.6633 | 34.4284 | 55.7892 | 80.4129 | 106.2946 | 135.5964 | 168.9588 | 241.6279 | 302.9119 | 360.4856 | -157.7659 | -198.7325 | -244.3117 | -289.7871 | -330.8101 | -368.8157 | -405.5527 | -447.5231 | -490.4018 | -528.4222
17104 | 3.5707 | 7.5918 | 12.4165 | 17.9501 | 23.739 | 30.2537 | 37.6529 | 53.686 | 67.2287 | 79.9825 | -34.5483 | -43.868 | -54.2483 | -64.6267 | -74.0134 | -82.7408 | -91.2074 | -101.0197 | -111.0402 | -119.9793
17105 | 23.908 | 49.9424 | 81.2201 | 117.204 | 154.9567 | 197.5981 | 246.1025 | 351.54 | 440.5135 | 524.1793 | -228.2456 | -288.4008 | -355.3581 | -422.2181 | -482.5941 | -538.6087 | -592.8311 | -655.1332 | -718.773 | -775.3395
17106 | 12.8125 | 27.2411 | 44.5532 | 64.4091 | 85.1812 | 108.5573 | 135.1076 | 192.6379 | 241.2324 | 286.9962 | -123.9676 | -157.4086 | -194.6557 | -231.8958 | -265.5773 | -296.8934 | -327.2735 | -362.4825 | -398.4383 | -430.5138
17107 | 4.6664 | 9.8949 | 16.1695 | 23.3694 | 30.9047 | 39.3893 | 49.0281 | 69.924 | 87.5717 | 104.1876 | -45.058 | -57.1706 | -70.6605 | -84.1453 | -96.3387 | -107.6721 | -118.6633 | -131.3856 | -144.3781 | -155.9624
17108 | 0.79382 | 1.6431 | 2.6642 | 3.8409 | 5.0773 | 6.4765 | 8.0693 | 11.5377 | 14.4629 | 17.2115 | -7.5262 | -9.4854 | -11.6653 | -13.8406 | -15.8033 | -17.622 | -19.3805 | -21.3914 | -23.4458 | -25.2681
17109 | 2.6518 | 5.638 | 9.2211 | 13.3306 | 17.6297 | 22.4678 | 27.9628 | 39.8697 | 49.9272 | 59.3988 | -25.6572 | -32.5784 | -40.2873 | -47.9948 | -54.9658 | -61.4472 | -67.7349 | -75.022 | -82.4637 | -89.1023
18131 | 12.9272 | 25.3748 | 40.3548 | 57.8845 | 76.5886 | 98.304 | 123.1646 | 178.8864 | 224.5948 | 267.0841 | -133.0708 | -160.6963 | -190.9048 | -220.3182 | -246.1076 | -269.1915 | -290.7199 | -312.8426 | -334.9962 | -353.3608
18132 | 0.53476 | 1.0497 | 1.6694 | 2.3945 | 3.1682 | 4.0665 | 5.0949 | 7.4 | 9.2908 | 11.0484 | -5.5047 | -6.6475 | -7.8971 | -9.1139 | -10.1807 | -11.1356 | -12.0262 | -12.9413 | -13.8578 | -14.6174
18133 | 3.3945 | 6.6632 | 10.5968 | 15.1999 | 20.1114 | 25.8136 | 32.3418 | 46.9738 | 58.9763 | 70.1336 | -34.9431 | -42.1972 | -50.1297 | -57.8533 | -64.6254 | -70.687 | -76.3401 | -82.1493 | -87.9666 | -92.789
18134 | 15.3452 | 30.1212 | 47.9031 | 68.7118 | 90.9145 | 116.6918 | 146.2026 | 212.3472 | 266.6053 | 317.0423 | -157.9618 | -190.7546 | -226.6136 | -261.5288 | -292.1421 | -319.5439 | -345.0992 | -371.3599 | -397.6574 | -419.4571
18135 | 16.5225 | 33.3003 | 53.3843 | 76.5731 | 101.0086 | 128.9258 | 160.7202 | 230.7541 | 289.0099 | 343.2247 | -160.766 | -198.6036 | -240.1567 | -280.9227 | -317.0061 | -349.7295 | -380.673 | -414.3123 | -448.1619 | -477.0054
18136 | 14.1278 | 29.3061 | 47.3781 | 67.9574 | 89.3635 | 113.3849 | 140.5896 | 199.5291 | 248.9899 | 295.2586 | -128.533 | -163.3111 | -201.663 | -239.5617 | -273.4078 | -304.4748 | -334.2196 | -368.16 | -402.3758 | -432.1885
18141 | 11.4856 | 22.5452 | 35.8548 | 51.4297 | 68.0481 | 87.3421 | 109.4304 | 158.9386 | 199.55 | 237.3014 | -118.232 | -142.7769 | -169.6169 | -195.7503 | -218.664 | -239.1738 | -258.3015 | -277.9573 | -297.6405 | -313.9573
18142 | 4.7663 | 9.3558 | 14.879 | 21.3423 | 28.2386 | 36.2452 | 45.4114 | 65.9563 | 82.8092 | 98.4753 | -49.0639 | -59.2495 | -70.3876 | -81.2324 | -90.7411 | -99.2523 | -107.1899 | -115.3466 | -123.5148 | -130.2859
18143 | 33.9919 | 66.723 | 106.1127 | 152.207 | 201.3893 | 258.4901 | 323.8609 | 470.3811 | 590.5711 | 702.2967 | -349.9093 | -422.5504 | -501.9835 | -579.3258 | -647.1391 | -707.8382 | -764.447 | -822.6185 | -880.8713 | -929.161
18144 | 54.1895 | 112.7462 | 182.4295 | 261.6697 | 343.9844 | 436.1836 | 540.5394 | 766.2841 | 955.8021 | 1133.238 | -489.3874 | -623.7682 | -772.0183 | -918.619 | -1049.6557 | -1170.0709 | -1285.4952 | -1417.8128 | -1551.1594 | -1667.6006
18145 | 5.8591 | 12.2073 | 19.7599 | 28.3429 | 37.2533 | 47.2252 | 58.5087 | 82.9001 | 103.3813 | 122.5642 | -52.7313 | -67.3103 | -83.3969 | -99.3097 | -113.5387 | -126.6212 | -139.1681 | -153.5818 | -168.1053 | -180.8002
18146 | 66.2648 | 134.1678 | 215.3799 | 308.9354 | 407.3139 | 519.3887 | 646.9159 | 926.9527 | 1160.4745 | 1377.8415 | -638.1674 | -791.7084 | -960.4435 | -1126.1842 | -1273.1092 | -1406.628 | -1533.1557 | -1671.8663 | -1811.5412 | -1931.023
20534 | 9.4116 | 19.6681 | 31.99 | 46.1648 | 61.0355 | 77.8303 | 96.9337 | 138.457 | 173.4973 | 206.4484 | -89.8781 | -113.5787 | -139.9596 | -166.303 | -190.0925 | -212.1646 | -233.5317 | -258.0877 | -283.1707 | -305.4678
20535 | 28.899 | 60.8034 | 99.113 | 143.131 | 189.258 | 241.2799 | 300.4181 | 428.8029 | 537.1838 | 639.1617 | -277.3993 | -351.2112 | -433.3921 | -515.4966 | -589.6871 | -658.5799 | -725.3288 | -802.2998 | -880.915 | -950.8985
20536 | 28.3281 | 59.1467 | 96.1734 | 138.7752 | 183.4747 | 233.9676 | 291.4057 | 416.2739 | 521.6411 | 620.7185 | -270.3429 | -341.5463 | -420.7996 | -499.9348 | -571.3924 | -637.6839 | -701.8505 | -775.5602 | -850.8529 | -917.7703
20537 | 22.7334 | 46.9657 | 76.1029 | 109.6914 | 144.9965 | 184.9676 | 230.4784 | 329.6103 | 413.2107 | 491.749 | -215.2223 | -271.1014 | -333.2719 | -395.3005 | -451.2554 | -503.0941 | -553.2018 | -610.4447 | -668.9266 | -720.7813
20539 | 4.8871 | 10.0965 | 16.3603 | 23.581 | 31.1707 | 39.7636 | 49.5473 | 70.8583 | 88.8303 | 105.7142 | -46.2676 | -58.2803 | -71.6454 | -84.98 | -97.009 | -108.1531 | -118.925 | -131.2309 | -143.8031 | -154.9506
20540 | 4.9695 | 10.2667 | 16.636 | 23.9784 | 31.6961 | 40.4337 | 50.3824 | 72.0525 | 90.3275 | 107.4959 | -47.0474 | -59.2625 | -72.8529 | -86.4123 | -98.644 | -109.9759 | -120.9294 | -133.4426 | -146.2267 | -157.5621
20541 | 22.1667 | 46.0591 | 74.6405 | 107.3411 | 141.4951 | 179.7852 | 223.3539 | 317.8093 | 397.1336 | 471.9277 | -205.1112 | -260.1897 | -321.2661 | -381.9938 | -436.5847 | -487.0111 | -535.6045 | -591.2111 | -647.9279 | -698.0935
20544 | 23.5297 | 48.6107 | 78.7683 | 113.5333 | 150.0749 | 191.4459 | 238.5507 | 341.1546 | 427.6831 | 508.9721 | -222.7603 | -280.5965 | -344.9445 | -409.1455 | -467.0603 | -520.7145 | -572.5772 | -631.825 | -692.3552 | -746.026
20545 | 11.6962 | 24.1635 | 39.1544 | 56.4355 | 74.5997 | 95.1645 | 118.5795 | 169.5821 | 212.5939 | 253.0013 | -110.7303 | -139.4797 | -171.466 | -203.3792 | -232.1676 | -258.8382 | -284.6183 | -314.0694 | -344.1579 | -370.8368
20547 | 42.9675 | 90.0275 | 146.5236 | 211.4436 | 279.4829 | 356.2465 | 443.5183 | 633.0655 | 793.0044 | 943.4134 | -409.9557 | -518.7194 | -639.7424 | -760.56 | -869.6384 | -970.832 | -1068.7823 | -1181.4986 | -1296.5695 | -1398.8305
20548 | 37.0505 | 77.0358 | 124.7293 | 179.1183 | 235.7557 | 299.3223 | 371.3626 | 527.3898 | 658.5469 | 781.4846 | -337.6739 | -429.5924 | -531.2204 | -631.9605 | -722.2356 | -805.3926 | -885.3008 | -976.9271 | -1069.6586 | -1150.9685
20549 | 30.3188 | 63.2459 | 102.4985 | 147.1777 | 193.638 | 245.3675 | 304.2016 | 431.3249 | 538.2479 | 638.3894 | -276.0904 | -351.9807 | -435.9466 | -519.2379 | -593.9344 | -662.7933 | -729.0087 | -804.8691 | -882.1559 | -950.3987
20551 | 5.9305 | 12.2519 | 19.8529 | 28.6152 | 37.8252 | 48.2524 | 60.1248 | 85.9853 | 107.7941 | 128.2824 | -56.1449 | -70.7221 | -86.9405 | -103.1219 | -117.7188 | -131.2419 | -144.3135 | -159.2464 | -174.5026 | -188.0299
20552 | 28.5266 | 58.9341 | 95.4963 | 137.6442 | 181.9461 | 232.1031 | 289.2114 | 413.6052 | 518.5096 | 617.0619 | -270.0676 | -340.1864 | -418.1999 | -496.0352 | -566.2493 | -631.298 | -694.1747 | -766.0049 | -839.3898 | -904.4587
20553 | 41.6288 | 82.4564 | 130.0004 | 182.235 | 234.867 | 291.7629 | 354.4472 | 487.838 | 601.0492 | 706.5427 | -384.5962 | -477.9938 | -579.8691 | -679.6289 | -768.0675 | -849.0318 | -926.3938 | -1018.0322 | -1109.2001 | -1190.1269
20554 | 11.4216 | 23.5963 | 38.2353 | 55.1107 | 72.8485 | 92.9306 | 115.7959 | 165.6013 | 207.6035 | 247.0623 | -108.131 | -136.2055 | -167.441 | -198.6051 | -226.7177 | -252.7622 | -277.9371 | -306.6968 | -336.0791 | -362.1317
21081 | 33.206 | 69.6583 | 112.9002 | 161.7596 | 212.2448 | 268.0963 | 331.1374 | 467.1154 | 581.7477 | 688.9791 | -295.3856 | -379.3761 | -472.0098 | -563.5947 | -645.4499 | -720.6894 | -792.8193 | -875.5953 | -959.789 | -1033.9462
21082 | 7.8271 | 16.4195 | 26.6122 | 38.129 | 50.0291 | 63.1941 | 78.0538 | 110.1058 | 137.1262 | 162.4022 | -69.6266 | -89.4244 | -111.2595 | -132.8473 | -152.1418 | -169.8768 | -186.8788 | -206.3903 | -226.236 | -243.7159
21083 | 10.6734 | 22.3902 | 36.2893 | 51.9941 | 68.2215 | 86.1738 | 106.437 | 150.1442 | 186.9903 | 221.4576 | -94.9454 | -121.9423 | -151.7175 | -181.1554 | -207.466 | -231.6501 | -254.8348 | -281.4414 | -308.5036 | -332.3399
21084 | 3.8627 | 8.1031 | 13.1333 | 18.8169 | 24.6897 | 31.1867 | 38.5201 | 54.3379 | 67.6727 | 80.1465 | -34.3612 | -44.1315 | -54.9073 | -65.561 | -75.0829 | -83.8353 | -92.2259 | -101.855 | -111.6489 | -120.2754
21085 | 49.7864 | 104.3982 | 169.2468 | 242.6902 | 318.7571 | 403.1248 | 498.2772 | 704.3559 | 878.0449 | 1040.6926 | -444.9331 | -570.4945 | -708.9076 | -845.5939 | -967.5773 | -1079.4609 | -1186.4825 | -1308.12 | -1432.2357 | -1541.4259
21086 | 24.193 | 50.751 | 82.2558 | 117.8534 | 154.6355 | 195.3273 | 241.2572 | 340.327 | 423.8447 | 501.9705 | -215.2095 | -276.4026 | -343.8929 | -410.619 | -470.2563 | -525.0737 | -577.6255 | -637.9337 | -699.2749 | -753.3037
21087 | 21.3806 | 44.8514 | 72.6939 | 104.1534 | 136.6596 | 172.6212 | 213.2119 | 300.7651 | 374.5743 | 443.6182 | -190.1921 | -244.2717 | -303.9165 | -362.886 | -415.5907 | -464.0357 | -510.4786 | -563.7762 | -617.9866 | -665.7348
21088 | 12.4692 | 26.1574 | 42.3952 | 60.7424 | 79.7001 | 100.6729 | 124.3455 | 175.4066 | 218.4522 | 258.7187 | -110.9203 | -142.4596 | -177.2445 | -211.6356 | -242.373 | -270.6262 | -297.7117 | -328.795 | -360.4106 | -388.2574
21089 | 29.1418 | 61.1317 | 99.0812 | 141.9634 | 186.2752 | 235.3006 | 290.6356 | 410.005 | 510.6351 | 604.7711 | -259.2637 | -332.9684 | -414.2568 | -494.6222 | -566.447 | -632.4631 | -695.7471 | -768.353 | -842.2087 | -907.2582
22323 | 17.6775 | 37.2412 | 60.3751 | 86.3275 | 112.9593 | 142.2117 | 174.9594 | 245.2154 | 304.7304 | 360.449 | -172.3616 | -217.7034 | -267.7563 | -317.3452 | -361.7862 | -402.7986 | -442.2763 | -488.3806 | -534.9796 | -576.555
22324 | 20.9184 | 43.569 | 70.3253 | 100.3594 | 131.2225 | 165.1988 | 203.1303 | 284.977 | 354.3382 | 419.3722 | -214.4061 | -266.4654 | -323.7625 | -380.3164 | -430.8089 | -477.2186 | -521.7253 | -573.1518 | -625.1707 | -671.6906
22325 | 31.3757 | 66.0994 | 107.1599 | 153.2226 | 200.4915 | 252.4115 | 310.5356 | 435.2329 | 540.8661 | 639.7611 | -305.9246 | -386.4019 | -475.2408 | -563.2561 | -642.1344 | -714.9273 | -784.9963 | -866.827 | -949.5356 | -1023.3276
22326 | 9.3532 | 19.6073 | 31.8326 | 45.6847 | 60.0203 | 75.873 | 93.7835 | 132.2556 | 164.9604 | 195.6627 | -85.8835 | -109.8103 | -136.4367 | -163.0579 | -187.1465 | -209.5836 | -231.3858 | -257.0314 | -283.2391 | -306.8231
22328 | 30.2841 | 63.7996 | 103.4315 | 147.8917 | 193.5159 | 243.6295 | 299.7313 | 420.0902 | 522.0481 | 617.5023 | -295.2808 | -372.9581 | -458.7061 | -543.6591 | -619.793 | -690.0533 | -757.6845 | -836.668 | -916.499 | -987.7236
22329 | 36.0132 | 75.8631 | 122.9848 | 175.8471 | 230.0938 | 289.6792 | 356.3827 | 499.4921 | 620.7225 | 734.2208 | -351.2852 | -443.6375 | -545.5826 | -646.5794 | -737.0886 | -820.6124 | -901.0083 | -994.8917 | -1089.7824 | -1174.4443
22330 | 2.0333 | 4.2625 | 6.9201 | 9.9315 | 13.0479 | 16.4941 | 20.3877 | 28.7512 | 35.861 | 42.5354 | -18.6703 | -23.8718 | -29.6602 | -35.4474 | -40.684 | -45.5617 | -50.3013 | -55.8764 | -61.5737 | -66.7007
22331 | 37.8474 | 79.7321 | 129.2611 | 184.8251 | 241.845 | 304.4766 | 374.594 | 525.0223 | 652.4515 | 771.7522 | -369.0175 | -466.0914 | -573.2517 | -679.4192 | -774.5656 | -862.3718 | -946.8927 | -1045.5994 | -1145.3659 | -1234.3765
22333 | 0.027111 | 0.056833 | 0.092268 | 0.13242 | 0.17397 | 0.21992 | 0.27184 | 0.38335 | 0.47815 | 0.56714 | -0.24894 | -0.31829 | -0.39547 | -0.47263 | -0.54245 | -0.60749 | -0.67068 | -0.74502 | -0.82098 | -0.88934
23340 | 3.7327 | 7.8637 | 12.7485 | 18.2285 | 23.852 | 30.0288 | 36.9436 | 51.7786 | 64.3455 | 76.1107 | -36.3951 | -45.9693 | -56.5382 | -67.0091 | -76.3931 | -85.0531 | -93.389 | -103.1242 | -112.9638 | -121.7427
23341 | 23.4526 | 49.4076 | 80.0993 | 114.5301 | 149.8623 | 188.6713 | 232.1175 | 325.3256 | 404.2838 | 478.2053 | -228.6709 | -288.8257 | -355.2305 | -421.0197 | -479.9792 | -534.3901 | -586.7649 | -647.9313 | -709.7539 | -764.9116
23342 | 29.4494 | 62.8152 | 102.2637 | 146.5481 | 192.0308 | 242.0479 | 298.0351 | 418.3911 | 520.2176 | 615.5584 | -291.3226 | -368.4623 | -453.5098 | -537.619 | -612.8435 | -682.0991 | -748.6017 | -825.7652 | -903.8174 | -973.2531
23343 | 28.7699 | 60.6097 | 98.26 | 140.4971 | 183.8401 | 231.4481 | 284.7447 | 399.0856 | 495.9457 | 586.6272 | -280.5167 | -354.3102 | -435.7708 | -516.4762 | -588.8034 | -655.5506 | -719.8002 | -794.8346 | -870.674 | -938.3375
23347 | 19.0996 | 40.248 | 65.2563 | 93.3132 | 122.1066 | 153.7359 | 189.1467 | 265.1228 | 329.4777 | 389.7271 | -186.3172 | -235.3263 | -289.4249 | -343.0183 | -391.0442 | -435.3607 | -478.0146 | -527.8136 | -578.1477 | -623.0492
23348 | 29.7207 | 63.637 | 103.7343 | 148.7564 | 195.0085 | 245.8898 | 302.8424 | 425.3481 | 528.954 | 625.9637 | -295.3192 | -373.673 | -460.0263 | -545.3806 | -621.6716 | -691.8578 | -759.204 | -837.1905 | -916.0941 | -986.2241
26161 | 27.7147 | 59.3528 | 96.7975 | 138.9308 | 182.3239 | 230.183 | 283.7182 | 399.2967 | 497.4749 | 589.6682 | -274.2574 | -346.9913 | -427.203 | -506.5685 | -577.6314 | -643.1455 | -706.1813 | -779.2535 | -853.8037 | -920.5518
26162 | 30.7387 | 65.8192 | 107.2929 | 153.8605 | 201.7005 | 254.3288 | 313.2368 | 439.9493 | 547.1127 | 647.4534 | -305.4481 | -386.491 | -475.8074 | -564.0902 | -642.9981 | -715.5915 | -785.2468 | -865.9056 | -947.5132 | -1020.0459
26163 | 19.7794 | 42.3525 | 69.0395 | 99.0043 | 129.7877 | 163.6523 | 201.5577 | 283.0932 | 352.0493 | 416.6153 | -196.546 | -248.6944 | -306.1667 | -362.9738 | -413.7485 | -460.4599 | -505.2809 | -557.1823 | -609.6941 | -656.3665
26164 | 45.2636 | 96.9205 | 157.9917 | 226.5638 | 297.0095 | 374.5061 | 461.2498 | 647.8375 | 805.6385 | 953.3929 | -449.7808 | -569.1185 | -700.6394 | -830.6383 | -946.8324 | -1053.7281 | -1156.2974 | -1275.0699 | -1395.2393 | -1502.0456
26165 | 9.4159 | 20.1593 | 32.8607 | 47.122 | 61.7729 | 77.89 | 95.9302 | 134.7344 | 167.5524 | 198.2809 | -93.5519 | -118.3719 | -145.7261 | -172.7643 | -196.9317 | -219.1655 | -240.5001 | -265.2064 | -290.2032 | -312.4209
26166 | 17.5274 | 37.5306 | 61.1792 | 87.7324 | 115.0111 | 145.0202 | 178.61 | 250.8624 | 311.9678 | 369.1828 | -174.1688 | -220.3801 | -271.309 | -321.6485 | -366.6424 | -408.0357 | -447.7537 | -493.746 | -540.2792 | -581.6379
26167 | 23.0926 | 50.1863 | 82.4949 | 119.1264 | 157.064 | 199.0506 | 246.5054 | 348.51 | 435.23 | 516.6971 | -220.4744 | -283.6068 | -353.847 | -424.0528 | -487.5651 | -546.7079 | -604.1702 | -671.6586 | -740.782 | -802.9982
27171 | 37.9391 | 79.9212 | 129.5634 | 185.252 | 242.398 | 305.1669 | 375.4331 | 526.1852 | 653.889 | 773.4469 | -370.1094 | -467.402 | -574.7988 | -681.1947 | -776.5406 | -864.526 | -949.2148 | -1048.1102 | -1148.0642 | -1237.2416
27173 | 11.5227 | 23.4772 | 37.3979 | 52.826 | 68.5436 | 85.7806 | 104.9428 | 145.832 | 180.6174 | 213.2337 | -140.9394 | -167.5487 | -196.2488 | -223.8852 | -247.9137 | -269.3944 | -289.4211 | -311.4581 | -333.5074 | -352.7503
27175 | 32.0471 | 67.5151 | 109.4557 | 156.5059 | 204.7881 | 257.8213 | 317.1915 | 444.5627 | 552.4608 | 653.4761 | -312.4779 | -394.6799 | -485.4226 | -575.3238 | -655.8919 | -730.244 | -801.8136 | -885.3959 | -969.875 | -1045.2464
27176 | 10.1319 | 21.3592 | 34.6354 | 49.5294 | 64.8141 | 81.604 | 100.3999 | 140.7286 | 174.8893 | 206.8711 | -98.867 | -124.8845 | -153.6032 | -182.0529 | -207.5464 | -231.0701 | -253.7105 | -280.142 | -306.8583 | -330.6906
27178 | 23.7695 | 50.0753 | 81.1817 | 116.0778 | 151.8875 | 191.2209 | 235.2542 | 329.7219 | 409.7471 | 484.6675 | -231.7611 | -292.7287 | -360.0309 | -426.7092 | -486.4654 | -541.6116 | -594.6942 | -656.6871 | -719.3451 | -775.2482
28221 | 22.2661 | 46.677 | 75.7803 | 108.7559 | 142.882 | 180.619 | 223.2542 | 314.8352 | 392.6868 | 465.7714 | -204.4722 | -261.4322 | -324.8178 | -388.1901 | -445.5327 | -498.9431 | -550.8415 | -611.8881 | -674.2717 | -730.4092
28222 | 62.3267 | 122.33 | 191.2193 | 265.9866 | 340.7338 | 421.3293 | 509.8485 | 695.5428 | 853.726 | 1002.108 | -615.6336 | -747.8365 | -888.9571 | -1023.4595 | -1139.2558 | -1242.0263 | -1337.167 | -1443.9557 | -1549.9558 | -1642.2763
28223 | 63.8397 | 129.6632 | 206.5243 | 291.5673 | 377.9126 | 472.0721 | 576.2551 | 798.2043 | 987.1764 | 1164.1078 | -689.8868 | -839.5204 | -1002.3407 | -1160.949 | -1300.5987 | -1427.2263 | -1546.9865 | -1683.6625 | -1820.0116 | -1941.3106
28224 | 25.8095 | 54.1047 | 87.8395 | 126.0633 | 165.6212 | 209.3654 | 258.7881 | 364.9489 | 455.195 | 539.9156 | -236.9886 | -303.0129 | -376.4863 | -449.9453 | -516.4159 | -578.3292 | -638.4907 | -709.2577 | -781.5758 | -846.6538
28225 | 0.34404 | 0.7245 | 1.1747 | 1.6801 | 2.1991 | 2.7695 | 3.4086 | 4.7796 | 5.9414 | 7.0294 | -3.3391 | -4.2213 | -5.1959 | -6.1621 | -7.0287 | -7.829 | -8.5999 | -9.5008 | -10.4123 | -11.226
28228 | 20.2518 | 42.454 | 68.9245 | 98.9173 | 129.957 | 164.2815 | 203.0617 | 286.3622 | 357.1751 | 423.6523 | -185.9564 | -237.7633 | -295.4152 | -353.0559 | -405.2129 | -453.7941 | -501.0006 | -556.5289 | -613.2743 | -664.3387
28229 | 2.0062 | 4.2056 | 6.8279 | 9.799 | 12.8739 | 16.2742 | 20.1159 | 28.3679 | 35.3828 | 41.9682 | -18.4214 | -23.5535 | -29.2647 | -34.9747 | -40.1416 | -44.9542 | -49.6306 | -55.1314 | -60.7527 | -65.8113
28231 | 36.4565 | 76.7813 | 124.4874 | 178.0361 | 233.0139 | 293.4252 | 361.0916 | 506.2714 | 629.2812 | 744.4629 | -354.2775 | -447.7725 | -551.0291 | -653.3825 | -745.1619 | -829.9069 | -911.5264 | -1006.8873 | -1103.3355 | -1189.4308
28232 | 73.264 | 139.4555 | 216.236 | 300.5974 | 385.8211 | 478.4756 | 580.8478 | 796.7562 | 981.5833 | 1155.2704 | -658.4493 | -806.7422 | -966.8125 | -1121.272 | -1255.946 | -1376.8763 | -1490.144 | -1617.6059 | -1745.9282 | -1858.8748
29481 | 15.277 | 31.3917 | 50.2333 | 71.183 | 92.5675 | 116.0292 | 142.1094 | 198.0035 | 245.4551 | 289.9295 | -177.3561 | -213.6146 | -252.9709 | -291.17 | -324.6696 | -354.8953 | -383.344 | -415.2256 | -447.0907 | -475.3514
29482 | 6.8795 | 13.7482 | 21.6693 | 30.3793 | 39.2105 | 48.8853 | 59.6426 | 82.6146 | 102.0133 | 120.2378 | -93.7735 | -108.6684 | -124.4816 | -139.4034 | -152.0861 | -163.1423 | -173.1777 | -183.6356 | -194.1343 | -202.8509
29483 | 39.0326 | 78.0041 | 122.9466 | 172.3649 | 222.4709 | 277.3633 | 338.398 | 468.7353 | 578.7991 | 682.2004 | -532.0484 | -616.5583 | -706.2786 | -790.941 | -862.9 | -925.6303 | -982.5683 | -1041.9042 | -1101.4714 | -1150.9269
29485 | 0.048791 | 0.097505 | 0.15368 | 0.21546 | 0.27809 | 0.3467 | 0.423 | 0.58592 | 0.7235 | 0.85275 | -0.66506 | -0.7707 | -0.88285 | -0.98868 | -1.0786 | -1.157 | -1.2282 | -1.3024 | -1.3768 | -1.4387
29486 | 2.2932 | 4.5827 | 7.2231 | 10.1264 | 13.0702 | 16.2951 | 19.8809 | 27.5382 | 34.0044 | 40.0793 | -31.2578 | -36.2228 | -41.4939 | -46.4678 | -50.6954 | -54.3808 | -57.7259 | -61.2119 | -64.7114 | -67.617
29488 | 23.9902 | 47.1278 | 73.8342 | 103.2569 | 133.1488 | 165.9661 | 202.5171 | 280.7375 | 346.8058 | 408.9295 | -301.9917 | -352.1053 | -405.2966 | -455.4494 | -498.0268 | -535.0718 | -568.6208 | -603.1963 | -638.0518 | -667.1025
29489 | 10.5876 | 21.1586 | 33.3493 | 46.754 | 60.3452 | 75.2348 | 91.7904 | 127.1444 | 156.9992 | 185.0469 | -144.3181 | -167.2414 | -191.5781 | -214.5427 | -234.0616 | -251.0772 | -266.5217 | -282.6165 | -298.7741 | -312.1889
29490 | 16.9304 | 33.8343 | 53.3281 | 74.7633 | 96.4967 | 120.3063 | 146.7801 | 203.3139 | 251.0541 | 295.9044 | -230.776 | -267.4322 | -306.3483 | -343.0707 | -374.2829 | -401.4921 | -426.189 | -451.926 | -477.7632 | -499.2146
29491 | 2.7323 | 5.4603 | 8.6063 | 12.0655 | 15.573 | 19.4154 | 23.6879 | 32.8115 | 40.5159 | 47.754 | -37.2434 | -43.1591 | -49.4395 | -55.3659 | -60.403 | -64.7941 | -68.7798 | -72.9333 | -77.103 | -80.5649
30603 | 62.9696 | 120.6693 | 188.7139 | 266.0489 | 346.8293 | 437.7382 | 540.8313 | 765.8745 | 956.5854 | 1137.5282 | -604.8902 | -732.0897 | -869.0429 | -999.6907 | -1111.6555 | -1209.344 | -1297.9049 | -1382.2985 | -1471.6844 | -1548.4242
30604 | 31.8835 | 61.098 | 95.5489 | 134.7015 | 175.5966 | 221.6177 | 273.8054 | 387.7237 | 484.2617 | 575.8536 | -306.2996 | -370.7 | -440.0361 | -506.1769 | -562.857 | -612.3077 | -657.1359 | -699.8537 | -745.096 | -783.9346
30605 | 54.4566 | 103.9869 | 161.748 | 226.4396 | 293.1923 | 367.5421 | 451.2015 | 632.45 | 785.5286 | 930.0572 | -534.4148 | -642.1614 | -756.9295 | -865.0155 | -956.4759 | -1035.252 | -1105.6543 | -1172.3344 | -1241.7765 | -1300.0311
30606 | 57.8249 | 111.9631 | 175.5733 | 247.5365 | 322.4347 | 406.4963 | 501.6687 | 709.0606 | 885.0153 | 1051.9465 | -540.9623 | -659.7849 | -787.2778 | -908.4336 | -1011.8477 | -1101.7245 | -1182.8655 | -1259.8861 | -1341.6015 | -1411.5142
30607 | 196.8105 | 273.5744 | 363.7468 | 465.887 | 572.3698 | 692.1412 | 827.9812 | 1124.7405 | 1376.4053 | 1615.3803 | -873.2856 | -1040.857 | -1220.2165 | -1390.0261 | -1534.3163 | -1658.9767 | -1770.768 | -1874.3999 | -1987.5598 | -2081.5126
30608 | 42.3118 | 81.0825 | 126.8044 | 178.7689 | 233.0485 | 294.1338 | 363.4062 | 514.6218 | 642.7681 | 764.3508 | -406.45 | -491.9204 | -583.9447 | -671.7322 | -746.9659 | -812.6066 | -872.1143 | -928.8217 | -988.8837 | -1040.4482
31002 | 22.521 | 43.3033 | 67.7834 | 95.565 | 124.5502 | 157.1399 | 194.076 | 274.6541 | 342.9593 | 407.7596 | -214.8826 | -260.64 | -309.8547 | -356.7482 | -396.8873 | -431.8672 | -463.5386 | -493.6905 | -525.6156 | -553.0244
31007 | 51.3321 | 102.443 | 162.1674 | 229.0263 | 297.9106 | 374.4 | 460.197 | 645.2262 | 801.5278 | 948.7258 | -520.6038 | -633.1526 | -753.5849 | -867.5119 | -964.4188 | -1048.3068 | -1123.6271 | -1196.081 | -1271.0809 | -1334.2363
31008 | 53.7978 | 107.3385 | 170.3623 | 241.7037 | 315.9261 | 399.0779 | 492.9753 | 696.9925 | 869.4131 | 1032.3602 | -535.899 | -654.1428 | -781.3369 | -902.3988 | -1005.9674 | -1096.103 | -1177.5314 | -1255.2341 | -1336.7229 | -1406.2062
31010 | 24.3332 | 48.1738 | 75.9458 | 106.9182 | 138.7308 | 173.9696 | 213.4274 | 298.3874 | 370.1003 | 437.5697 | -246.8396 | -299.0922 | -354.8244 | -407.3505 | -451.8606 | -490.2454 | -524.5686 | -557.4982 | -591.4539 | -619.8606
32374 | 48.7997 | 96.8625 | 153.3031 | 216.2173 | 280.508 | 351.0077 | 429.3285 | 596.8468 | 739.6 | 873.434 | -457.2893 | -567.3013 | -687.5657 | -805.2448 | -909.2794 | -1003.8866 | -1093.5912 | -1195.2805 | -1297.9974 | -1388.9555
32377 | 15.5771 | 30.9189 | 48.935 | 69.0174 | 89.5393 | 112.0431 | 137.0434 | 190.516 | 236.0834 | 278.8038 | -145.9686 | -181.0849 | -219.4738 | -257.0375 | -290.2458 | -320.4448 | -349.0789 | -381.5385 | -414.3262 | -443.3604
32379 | 63.5068 | 126.0964 | 199.5397 | 281.3093 | 364.7747 | 456.2037 | 557.693 | 774.6677 | 959.4947 | 1132.7068 | -593.6419 | -736.8867 | -893.417 | -1046.5361 | -1181.8705 | -1304.9389 | -1421.6317 | -1554.2022 | -1687.9659 | -1806.3553
33271 | 1248.201 | 1347.6605 | 1465.3356 | 1600.5337 | 1743.3344 | 1905.9843 | 2092.0611 | 2503.2357 | 2850.0032 | 3180.0033 | -2273.0514 | -2488.5914 | -2719.2892 | -2937.0321 | -3121.1412 | -3278.7873 | -3418.6547 | -3540.259 | -3673.6847 | -3782.0001
33272 | 508.4013 | 588.3939 | 681.4581 | 784.8901 | 890.7233 | 1007.5357 | 1138.1406 | 1418.4411 | 1656.2197 | 1880.4265 | -1283.1685 | -1459.7962 | -1649.0866 | -1829.4336 | -1984.1886 | -2120.2533 | -2244.782 | -2375.0189 | -2508.1019 | -2620.6457
33273 | 0.28553 | 0.57541 | 0.9077 | 1.2658 | 1.621 | 2.0002 | 2.4135 | 3.2727 | 4.011 | 4.699 | -2.9712 | -3.6203 | -4.3163 | -4.9842 | -5.5637 | -6.0831 | -6.569 | -7.1327 | -7.6864 | -8.1743
33274 | 67.9583 | 136.9488 | 216.035 | 301.2777 | 385.8138 | 476.089 | 574.4811 | 779.0275 | 954.7802 | 1118.5774 | -706.9101 | -861.4084 | -1027.0751 | -1186.064 | -1324.0323 | -1447.713 | -1563.3994 | -1697.6367 | -1829.5036 | -1945.687
33275 | 4.7968 | 9.6669 | 15.2493 | 21.2659 | 27.2323 | 33.6034 | 40.5473 | 54.9814 | 67.3843 | 78.9435 | -49.9162 | -60.8212 | -72.5136 | -83.7339 | -93.4698 | -102.1968 | -110.3591 | -119.8294 | -129.1322 | -137.3282
33276 | 362.8909 | 464.9038 | 582.4848 | 712.4897 | 845.3413 | 992.303 | 1156.9384 | 1512.343 | 1812.0929 | 2094.7054 | -1389.9274 | -1604.9033 | -1830.6566 | -2039.7859 | -2213.7764 | -2361.0646 | -2490.2666 | -2611.9995 | -2739.8412 | -2842.543
34251 | 37.1439 | 74.4729 | 117.5951 | 164.4042 | 211.0464 | 260.9547 | 315.3781 | 429.9249 | 527.5069 | 618.2838 | -362.0461 | -447.2683 | -539.667 | -629.5497 | -708.6771 | -780.6667 | -849.0071 | -930.1166 | -1010.013 | -1080.7703
34252 | 68.9024 | 136.7654 | 216.4566 | 305.2865 | 396.0584 | 495.595 | 606.1725 | 842.682 | 1044.2265 | 1233.1775 | -645.6753 | -801.0087 | -970.8176 | -1136.9759 | -1283.8687 | -1417.4509 | -1544.1115 | -1687.7002 | -1832.7372 | -1961.1707
34253 | 36.3397 | 72.7046 | 114.7745 | 160.4742 | 206.0142 | 254.7081 | 307.7625 | 419.6948 | 514.8492 | 603.2909 | -364.9698 | -448.449 | -539.2109 | -627.8164 | -706.1172 | -777.6461 | -845.8245 | -927.3938 | -1007.4611 | -1078.7098
34254 | 0.038243 | 0.075287 | 0.11753 | 0.16269 | 0.20714 | 0.25426 | 0.30536 | 0.41054 | 0.50108 | 0.58592 | -0.80901 | -0.89167 | -0.98002 | -1.0646 | -1.1377 | -1.2032 | -1.2644 | -1.336 | -1.4062 | -1.467
34256 | 41.9874 | 83.9233 | 132.6049 | 185.7885 | 239.0798 | 296.376 | 359.0684 | 491.8462 | 604.7006 | 709.7781 | -398.8041 | -495.1145 | -599.9999 | -702.5092 | -793.1664 | -875.9648 | -954.8556 | -1048.3524 | -1140.875 | -1222.9189
34259 | 68.9426 | 137.8237 | 217.4566 | 303.8947 | 389.9812 | 481.9935 | 582.224 | 793.4138 | 973.1206 | 1140.1743 | -730.3406 | -888.251 | -1059.8024 | -1227.1249 | -1374.8515 | -1509.6818 | -1638.0859 | -1791.5646 | -1941.6565 | -2075.6838
34260 | 17.0343 | 33.7884 | 53.4164 | 75.2242 | 97.4461 | 121.7542 | 148.713 | 206.206 | 255.2633 | 301.2383 | -176.2977 | -214.5674 | -256.3294 | -297.1228 | -333.1286 | -365.8331 | -396.8092 | -432.0055 | -467.2498 | -498.6629
34261 | 16.1681 | 32.092 | 50.7916 | 71.636 | 92.9365 | 116.2941 | 142.2429 | 197.7442 | 245.0405 | 289.3817 | -151.5067 | -187.9554 | -227.8008 | -266.7896 | -301.2578 | -332.6026 | -362.323 | -396.0142 | -430.0459 | -460.1816
34262 | 10.9216 | 21.6764 | 34.3021 | 48.3701 | 62.7408 | 78.4946 | 95.9923 | 133.404 | 165.2901 | 195.1826 | -103.6953 | -128.3057 | -155.2038 | -181.5178 | -204.7761 | -225.9237 | -245.9727 | -268.7069 | -291.6459 | -311.9753
34263 | 36.6547 | 72.7938 | 115.0768 | 161.9417 | 209.5825 | 261.5688 | 319.1146 | 441.7319 | 546.2934 | 644.1954 | -373.0356 | -455.6612 | -545.8053 | -633.873 | -711.6341 | -782.3294 | -849.3538 | -926.0159 | -1002.6648 | -1070.9062
34264 | 134.2159 | 177.7638 | 228.8138 | 286.2351 | 345.6378 | 411.8734 | 486.481 | 648.0101 | 784.992 | 914.5717 | -546.2102 | -642.3889 | -745.7958 | -844.495 | -929.237 | -1003.5374 | -1071.2953 | -1139.2144 | -1210.9892 | -1271.6071
37002 | 6.8321 | 13.6258 | 22.3113 | 33.6734 | 47.0137 | 63.6478 | 83.8393 | 131.6004 | 171.3398 | 209.9263 | -57.4576 | -70.9682 | -85.4662 | -98.69 | -109.2056 | -117.0688 | -122.8257 | -120.0108 | -120.5847 | -119.7666
38422 | 0.26215 | 0.50237 | 0.78565 | 1.1076 | 1.4439 | 1.8224 | 2.2516 | 3.1885 | 3.9825 | 4.7358 | -2.5183 | -3.0478 | -3.618 | -4.1619 | -4.628 | -5.0347 | -5.4034 | -5.7548 | -6.1269 | -6.4464
39010 | 35.0987 | 70.0005 | 114.6215 | 172.9927 | 241.5262 | 326.982 | 430.713 | 676.079 | 880.2346 | 1078.4678 | -295.1807 | -364.5896 | -439.0707 | -507.0063 | -561.029 | -601.4248 | -631.0002 | -616.5388 | -619.4874 | -615.2846
39011 | 29.5055 | 58.8454 | 96.3556 | 145.4249 | 203.037 | 274.8747 | 362.0753 | 568.3402 | 739.9619 | 906.605 | -248.1412 | -306.4892 | -369.1012 | -426.2107 | -471.6244 | -505.5828 | -530.4451 | -518.2882 | -520.767 | -517.2339
39012 | 20.9091 | 41.7009 | 68.2825 | 103.0555 | 143.8825 | 194.7903 | 256.5852 | 402.7551 | 524.375 | 642.4669 | -175.8456 | -217.194 | -261.564 | -302.0348 | -334.2173 | -358.282 | -375.9007 | -367.2857 | -369.0423 | -366.5385
39013 | 14.0847 | 28.0793 | 45.9558 | 69.3104 | 96.7046 | 130.8371 | 172.2502 | 270.1597 | 351.6339 | 430.7336 | -118.5593 | -146.4211 | -176.3196 | -203.605 | -225.3231 | -241.5991 | -253.5595 | -248.043 | -249.4465 | -247.9797
39565 | 63.403 | 126.4502 | 207.0542 | 312.4969 | 436.2971 | 590.6658 | 778.0473 | 1221.2806 | 1590.0708 | 1948.1626 | -533.2195 | -658.6008 | -793.1448 | -915.8649 | -1013.4524 | -1086.4241 | -1139.8496 | -1113.7262 | -1119.0527 | -1111.4606
39568 | 8.6289 | 17.8798 | 29.146 | 42.6342 | 57.3676 | 74.6165 | 94.7086 | 139.993 | 178.0579 | 214.4637 | -83.4945 | -103.6383 | -125.5705 | -146.5819 | -164.5899 | -180.1129 | -193.9766 | -204.7764 | -217.5027 | -228.1174
39569 | 0.18769 | 0.37433 | 0.61295 | 0.92509 | 1.2916 | 1.7486 | 2.3033 | 3.6154 | 4.7071 | 5.7672 | -1.5785 | -1.9497 | -2.348 | -2.7113 | -3.0002 | -3.2162 | -3.3743 | -3.297 | -3.3128 | -3.2903
39570 | 0.90093 | 1.7968 | 2.9422 | 4.4405 | 6.1996 | 8.3931 | 11.0557 | 17.3539 | 22.5943 | 27.6826 | -7.5768 | -9.3584 | -11.2703 | -13.0141 | -14.4007 | -15.4376 | -16.1968 | -15.8256 | -15.9013 | -15.7934
39571 | 32.6212 | 65.0593 | 106.5305 | 160.7814 | 224.4773 | 303.9009 | 400.3097 | 628.3557 | 818.1004 | 1002.3406 | -274.3444 | -338.8538 | -408.0775 | -471.2176 | -521.4269 | -558.9713 | -586.459 | -573.0184 | -575.7589 | -571.8527
40001 | 12.6805 | 23.7326 | 36.5252 | 50.7033 | 65.1968 | 81.2126 | 99.1423 | 137.76 | 170.4 | 201.1723 | -123.4786 | -147.3262 | -172.6203 | -196.4096 | -216.5307 | -233.9294 | -249.5726 | -265.1123 | -280.9991 | -294.4668
40002 | 36.0994 | 74.2471 | 120.7768 | 177.5774 | 240.9172 | 316.7979 | 406.6562 | 613.6837 | 786.782 | 953.6629 | -353.6572 | -431.7264 | -514.3282 | -589.6556 | -650.1668 | -697.4117 | -734.4812 | -741.003 | -758.9538 | -769.0727
40003 | 5.4521 | 10.6895 | 16.7211 | 23.3388 | 30.0366 | 37.3634 | 45.5045 | 62.8659 | 77.5814 | 91.4174 | -57.32 | -68.6672 | -80.704 | -92.0515 | -101.6872 | -110.0798 | -117.6902 | -125.6149 | -133.598 | -140.4357
41511 | 60.2903 | 124.4506 | 199.7223 | 282.919 | 367.0947 | 458.2473 | 558.9056 | 772.4641 | 954.7464 | 1125.0831 | -574.5162 | -724.1358 | -889.0468 | -1052.4423 | -1199.013 | -1334.7053 | -1465.7389 | -1622.7082 | -1779.9654 | -1921.2106
41512 | 18.9503 | 37.2116 | 58.4389 | 81.9116 | 105.7873 | 131.9472 | 161.0242 | 222.8952 | 275.4969 | 324.9398 | -187.7577 | -228.3463 | -272.0364 | -313.9874 | -350.3399 | -382.7106 | -412.7601 | -445.476 | -478.5225 | -507.4563
41513 | 64.052 | 127.8344 | 202.4631 | 285.6226 | 370.7587 | 464.5353 | 569.1807 | 792.6485 | 983.2176 | 1162.873 | -605.0348 | -748.714 | -904.3435 | -1054.6614 | -1185.5896 | -1302.5764 | -1411.4705 | -1528.6402 | -1648.6241 | -1753.8412
41514 | 35.8221 | 73.8278 | 118.8804 | 170.1715 | 223.7178 | 283.7643 | 351.5972 | 498.7152 | 623.5195 | 741.5179 | -355.4819 | -440.7205 | -533.4695 | -623.1384 | -701.2232 | -770.6273 | -834.8205 | -899.9375 | -968.2241 | -1027.7657
41515 | 116.0733 | 226.2441 | 359.1336 | 515.2979 | 683.0707 | 876.3235 | 1098.6962 | 1592.4582 | 2008.0923 | 2403.2255 | -969.0526 | -1211.4211 | -1475.3084 | -1728.6745 | -1947.0687 | -2137.3252 | -2309.3081 | -2458.9035 | -2626.988 | -2768.8806
41516 | 81.3369 | 161.5727 | 258.4118 | 373.4529 | 498.543 | 644.7065 | 814.7654 | 1198.128 | 1519.7654 | 1827.3546 | -754.5332 | -925.5511 | -1109.1337 | -1281.4954 | -1425.8434 | -1546.6143 | -1650.6734 | -1719.7243 | -1805.139 | -1872.9658
41517 | 92.5484 | 188.6052 | 299.6985 | 420.1508 | 539.9794 | 667.8699 | 807.0977 | 1097.5446 | 1347.6255 | 1580.7354 | -882.3011 | -1103.6728 | -1344.641 | -1580.1707 | -1788.5631 | -1979.1456 | -2160.9785 | -2378.4875 | -2594.0782 | -2786.4122
41518 | 97.9334 | 199.0329 | 316.0301 | 443.0686 | 569.647 | 704.9801 | 852.5195 | 1160.5356 | 1425.7791 | 1673.1742 | -930.8453 | -1163.5737 | -1416.8457 | -1664.2598 | -1883.003 | -2082.8313 | -2273.2675 | -2500.0046 | -2725.0608 | -2925.6924
43505 | 12.0764 | 23.7759 | 38.1174 | 55.6043 | 75.039 | 98.1937 | 125.5031 | 188.0201 | 240.4584 | 290.9178 | -109.6382 | -134.355 | -160.9643 | -185.9036 | -206.6572 | -223.747 | -238.1699 | -245.3543 | -255.7841 | -263.7394
43506 | 65.0302 | 128.0303 | 205.2578 | 299.4222 | 404.0758 | 528.7612 | 675.8191 | 1012.4656 | 1294.8398 | 1566.5573 | -590.3886 | -723.4856 | -866.7734 | -1001.0683 | -1112.8241 | -1204.8508 | -1282.5162 | -1321.2035 | -1377.3668 | -1420.2048
43507 | 64.9057 | 127.7852 | 204.8648 | 298.849 | 403.3022 | 527.7489 | 674.5253 | 1010.5272 | 1292.3609 | 1563.5581 | -589.2583 | -722.1005 | -865.1139 | -999.1518 | -1110.6937 | -1202.5441 | -1280.0608 | -1318.674 | -1374.7299 | -1417.4858
45001 | 6.7945 | 13.5509 | 22.1888 | 33.4884 | 46.7553 | 63.2981 | 83.3787 | 130.8773 | 170.3984 | 208.7729 | -57.1419 | -70.5783 | -84.9966 | -98.1477 | -108.6056 | -116.4256 | -122.1508 | -119.3514 | -119.9222 | -119.1086
45002 | 26.3962 | 54.6462 | 89.0929 | 130.4365 | 175.6975 | 228.7958 | 290.7339 | 430.5767 | 548.0716 | 660.5041 | -254.3714 | -315.7305 | -382.5027 | -446.3783 | -501.0147 | -547.9561 | -589.7157 | -621.3581 | -659.1009 | -690.4122
45003 | 30.1436 | 60.1181 | 98.4396 | 148.5702 | 207.4284 | 280.8198 | 369.9065 | 580.6325 | 755.9662 | 926.2135 | -253.5081 | -313.1181 | -377.0843 | -435.429 | -481.8249 | -516.5178 | -541.9178 | -529.498 | -532.0304 | -528.4209
48180 | 46.7069 | 96.3603 | 154.8802 | 221.1331 | 290.0089 | 367.0522 | 453.972 | 642.4807 | 801.9002 | 952.4004 | -472.9787 | -582.9526 | -701.9206 | -816.4181 | -915.6954 | -1003.7379 | -1085.0641 | -1168.593 | -1255.3829 | -1330.5152
48181 | 2.9944 | 6.2268 | 10.1462 | 14.7984 | 19.8412 | 25.7026 | 32.496 | 47.7133 | 60.5215 | 72.7474 | -29.3356 | -36.4277 | -44.1584 | -51.5923 | -57.9977 | -63.5694 | -68.5985 | -72.8209 | -77.6341 | -81.7028
48182 | 57.9983 | 120.6079 | 196.5229 | 286.6304 | 384.3056 | 497.834 | 629.4167 | 924.161 | 1172.2448 | 1409.0474 | -568.2019 | -705.5701 | -855.3063 | -999.2934 | -1123.3609 | -1231.2795 | -1328.6871 | -1410.4718 | -1503.6983 | -1582.506
48183 | 55.9269 | 114.9114 | 184.4913 | 263.7553 | 346.7503 | 440.3859 | 546.7432 | 779.5363 | 976.1994 | 1162.6447 | -586.9196 | -715.5856 | -853.8841 | -985.5887 | -1098.312 | -1196.5496 | -1285.5554 | -1370.1075 | -1459.8697 | -1536.6338
48184 | 44.3097 | 92.1423 | 150.1401 | 218.9807 | 293.6029 | 380.3366 | 480.8635 | 706.0431 | 895.5748 | 1076.4879 | -434.0965 | -539.0435 | -653.4393 | -763.443 | -858.2284 | -940.6763 | -1015.0941 | -1077.5762 | -1148.7996 | -1209.0074
48185 | 44.6564 | 92.796 | 151.2128 | 220.6586 | 296.041 | 383.7721 | 485.5463 | 713.774 | 905.82 | 1089.1944 | -435.9901 | -541.4752 | -656.4397 | -766.9251 | -862.0446 | -944.662 | -1019.1064 | -1080.871 | -1151.651 | -1211.3495
48188 | 23.9907 | 49.8888 | 81.2906 | 118.5632 | 158.966 | 205.9264 | 260.3549 | 382.2744 | 484.8929 | 582.845 | -235.0337 | -291.8554 | -353.7929 | -413.3525 | -464.6723 | -509.3123 | -549.6044 | -583.4342 | -621.9969 | -654.5953
48189 | 20.1408 | 41.8829 | 68.2455 | 99.5367 | 133.4558 | 172.8803 | 218.5743 | 320.9287 | 407.0795 | 489.3127 | -197.3166 | -245.0198 | -297.0178 | -347.0195 | -390.1038 | -427.5801 | -461.4064 | -489.8073 | -522.1817 | -549.5488
48190 | 39.1409 | 81.3936 | 132.6257 | 193.4359 | 259.3531 | 335.9691 | 424.7692 | 623.6809 | 791.1031 | 950.9121 | -383.4577 | -476.1623 | -577.2134 | -674.3848 | -758.1133 | -830.9434 | -896.6801 | -951.8734 | -1014.7884 | -1067.9727
48191 | 17.2632 | 35.7042 | 57.8023 | 83.5799 | 111.1237 | 142.751 | 179.1105 | 259.8069 | 327.8271 | 392.577 | -174.3178 | -214.6907 | -258.442 | -300.351 | -336.3711 | -367.742 | -396.1173 | -421.3298 | -449.1495 | -472.7974
48192 | 72.6474 | 147.8779 | 234.5767 | 329.5897 | 425.5781 | 530.2926 | 646.375 | 893.0202 | 1102.3615 | 1298.9493 | -795.2005 | -959.2868 | -1133.9715 | -1299.5332 | -1441.0275 | -1565.266 | -1678.9351 | -1800.4512 | -1922.2518 | -2027.7845
49101 | 27.5198 | 57.2276 | 93.2487 | 136.0041 | 182.3503 | 236.2187 | 298.6538 | 438.5079 | 556.2219 | 668.583 | -269.6078 | -334.788 | -405.8368 | -474.1576 | -533.0268 | -584.2334 | -630.4526 | -669.2589 | -713.4942 | -750.8879
49302 | 0.037539 | 0.074867 | 0.12259 | 0.18502 | 0.25832 | 0.34971 | 0.46066 | 0.72308 | 0.94143 | 1.1534 | -0.3157 | -0.38994 | -0.46959 | -0.54225 | -0.60003 | -0.64324 | -0.67487 | -0.6594 | -0.66255 | -0.65806
49303 | 10.5484 | 21.0376 | 34.4477 | 51.9903 | 72.587 | 98.2694 | 129.4442 | 203.1852 | 264.5411 | 324.1171 | -88.7121 | -109.5718 | -131.956 | -152.373 | -168.6087 | -180.7491 | -189.6375 | -185.2913 | -186.1775 | -184.9144
49304 | 0.037539 | 0.074867 | 0.12259 | 0.18502 | 0.25832 | 0.34971 | 0.46066 | 0.72308 | 0.94143 | 1.1534 | -0.3157 | -0.38994 | -0.46959 | -0.54225 | -0.60003 | -0.64324 | -0.67487 | -0.6594 | -0.66255 | -0.65806
49307 | 0.488 | 0.97327 | 1.5937 | 2.4052 | 3.3581 | 4.5463 | 5.9885 | 9.4 | 12.2386 | 14.9947 | -4.1041 | -5.0692 | -6.1047 | -7.0493 | -7.8004 | -8.3621 | -8.7733 | -8.5722 | -8.6132 | -8.5548
49411 | 2.3649 | 4.7166 | 7.7232 | 11.6562 | 16.274 | 22.0319 | 29.0213 | 45.554 | 59.3099 | 72.6668 | -19.8892 | -24.5659 | -29.5844 | -34.1619 | -37.802 | -40.5238 | -42.5166 | -41.5422 | -41.7409 | -41.4577
49412 | 0.97601 | 1.9465 | 3.1873 | 4.8105 | 6.7162 | 9.0925 | 11.977 | 18.8001 | 24.4771 | 29.9895 | -8.2082 | -10.1383 | -12.2095 | -14.0986 | -15.6008 | -16.7241 | -17.5465 | -17.1444 | -17.2264 | -17.1095
49621 | 1.5391 | 3.0695 | 5.0262 | 7.5858 | 10.591 | 14.3382 | 18.8869 | 29.6462 | 38.5985 | 47.2911 | -12.9438 | -15.9873 | -19.2534 | -22.2324 | -24.6013 | -26.3726 | -27.6695 | -27.0354 | -27.1647 | -26.9804
49801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51001 | 0.29553 | 0.53156 | 0.82427 | 1.1863 | 1.5925 | 2.0794 | 2.6548 | 3.975 | 5.0756 | 6.1315 | -3.2358 | -3.7341 | -4.2744 | -4.7829 | -5.2083 | -5.5592 | -5.8558 | -5.9953 | -6.2016 | -6.3477
51002 | 2.8896 | 5.1975 | 8.0595 | 11.5991 | 15.5715 | 20.3323 | 25.9583 | 38.8666 | 49.6284 | 59.952 | -31.6386 | -36.5115 | -41.7944 | -46.766 | -50.9253 | -54.3569 | -57.2572 | -58.6205 | -60.6376 | -62.0663
51003 | 17.994 | 33.3158 | 52.4342 | 76.4775 | 103.8628 | 137.1541 | 176.8777 | 269.1456 | 345.8027 | 419.6095 | -187.1562 | -218.5335 | -252.1777 | -283.1642 | -308.3229 | -328.0646 | -343.6417 | -345.1756 | -351.9717 | -355.1197
51004 | 28.2016 | 53.286 | 83.2347 | 118.0037 | 155.0082 | 197.3393 | 245.8154 | 353.048 | 442.9999 | 528.2716 | -306.7346 | -361.4204 | -420.3322 | -476.161 | -523.5947 | -564.2557 | -600.3255 | -630.5434 | -663.7413 | -690.6246
53001 | 53.8012 | 108.7759 | 171.5019 | 238.6647 | 304.8924 | 375.2152 | 451.4354 | 608.6186 | 742.4717 | 866.5912 | -546.0201 | -668.4488 | -798.8351 | -922.5205 | -1028.5786 | -1122.2313 | -1208.3348 | -1305.5269 | -1400.3216 | -1482.393
53002 | 0.064896 | 0.11941 | 0.18517 | 0.26422 | 0.35132 | 0.45465 | 0.57613 | 0.85426 | 1.0857 | 1.3076 | -0.54485 | -0.6562 | -0.77303 | -0.87848 | -0.9623 | -1.0269 | -1.0767 | -1.085 | -1.1068 | -1.1168
53003 | 100.8161 | 193.1542 | 300.5979 | 418.7146 | 537.9083 | 667.0179 | 808.9502 | 1106.3971 | 1359.5785 | 1595.8665 | -1015.5431 | -1225.5696 | -1453.2046 | -1673.2007 | -1865.3565 | -2037.7601 | -2198.804 | -2378.9166 | -2557.4051 | -2713.53
53004 | 34.0045 | 68.6935 | 108.2861 | 150.7009 | 192.5457 | 236.9997 | 285.1995 | 384.6461 | 469.3243 | 547.8564 | -344.9594 | -422.2206 | -504.5186 | -582.599 | -649.56 | -708.6907 | -763.0562 | -824.3682 | -884.1902 | -935.9867
53006 | 0.093654 | 0.17943 | 0.27924 | 0.38896 | 0.49967 | 0.6196 | 0.75143 | 1.0277 | 1.2629 | 1.4823 | -0.94324 | -1.1383 | -1.3498 | -1.5542 | -1.7327 | -1.8929 | -2.0425 | -2.2098 | -2.3756 | -2.5207
53007 | 0.14048 | 0.26914 | 0.41885 | 0.58343 | 0.74951 | 0.9294 | 1.1271 | 1.5416 | 1.8943 | 2.2235 | -1.4149 | -1.7075 | -2.0247 | -2.3313 | -2.599 | -2.8393 | -3.0637 | -3.3147 | -3.5635 | -3.7811
53008 | 82.0496 | 151.461 | 235.0099 | 334.9657 | 444.6277 | 574.2052 | 726.1427 | 1072.8716 | 1361.5852 | 1638.2684 | -701.8383 | -844.435 | -994.3011 | -1130.0938 | -1238.6641 | -1323.2942 | -1389.5253 | -1406.5734 | -1439.7654 | -1457.7045
53009 | 87.1494 | 172.6329 | 270.8659 | 377.0727 | 482.7088 | 595.7258 | 718.886 | 974.4536 | 1191.8845 | 1393.8405 | -881.8639 | -1073.7034 | -1279.334 | -1475.7537 | -1645.3546 | -1796.0286 | -1935.4059 | -2092.1802 | -2245.9062 | -2379.7595
53010 | 2.0604 | 3.9474 | 6.1432 | 8.557 | 10.9928 | 13.6311 | 16.5315 | 22.6095 | 27.7832 | 32.6115 | -20.7513 | -25.0436 | -29.6958 | -34.1919 | -38.1191 | -41.6427 | -44.9343 | -48.6159 | -52.2642 | -55.4555
54003 | 80.8599 | 159.8866 | 257.1825 | 376.5165 | 509.6782 | 668.6719 | 856.1669 | 1285.6342 | 1643.7071 | 1987.0836 | -664.8435 | -830.9907 | -1009.9143 | -1176.9819 | -1315.479 | -1428.5147 | -1522.713 | -1563.8403 | -1627.8497 | -1673.3788
54004 | 5.1568 | 10.876 | 17.6702 | 25.5202 | 33.8516 | 43.3738 | 54.2802 | 78.4254 | 98.7151 | 117.9862 | -62.6876 | -75.0648 | -88.3034 | -100.7252 | -111.1518 | -119.953 | -127.6158 | -133.6024 | -140.3234 | -145.6288
54005 | 88.1289 | 160.2501 | 244.7802 | 340.8161 | 441.3855 | 555.1491 | 684.5608 | 969.2427 | 1208.0792 | 1434.2801 | -793.3404 | -946.8434 | -1109.0262 | -1259.2562 | -1383.72 | -1487.5252 | -1576.7143 | -1646.7847 | -1723.748 | -1784.2007
54006 | 4.1605 | 8.7029 | 14.0983 | 20.3314 | 26.946 | 34.5055 | 43.1637 | 62.3313 | 78.4382 | 93.7363 | -49.8989 | -59.7269 | -70.2373 | -80.0972 | -88.3718 | -95.3547 | -101.4328 | -106.178 | -111.5057 | -115.7103
54007 | 37.5418 | 79.1772 | 128.6388 | 185.7871 | 246.4397 | 315.7614 | 395.1596 | 570.9371 | 718.646 | 858.9394 | -456.366 | -546.4718 | -642.8491 | -733.2792 | -809.1851 | -873.2577 | -929.0428 | -972.6258 | -1021.5547 | -1060.1777
55001 | 75.6986 | 104.39 | 139.2976 | 181.4667 | 228.0013 | 283.1141 | 347.7907 | 495.2424 | 618.3075 | 736.1542 | -330.2907 | -390.303 | -454.3752 | -513.7013 | -562.462 | -601.9624 | -634.5826 | -649.1814 | -671.6901 | -687.0256
55002 | 187.1135 | 217.5038 | 257.8027 | 313.8279 | 382.5186 | 471.1072 | 580.7589 | 845.9621 | 1064.8364 | 1278.304 | -429.7625 | -484.982 | -543.1135 | -592.9408 | -628.653 | -649.2981 | -657.0598 | -603.3245 | -571.1314 | -532.4133
55003 | 23.2417 | 31.0086 | 40.8221 | 53.4002 | 67.9396 | 85.8283 | 107.3448 | 157.7239 | 199.675 | 240.2437 | -83.5189 | -99.2423 | -116.1345 | -131.6305 | -144.1085 | -153.6951 | -161.0182 | -160.0235 | -162.4688 | -163.0902
56001 | 3.0425 | 6.2843 | 10.317 | 15.4147 | 21.2607 | 28.4297 | 37.0408 | 57.2227 | 73.9765 | 90.1663 | -27.8287 | -34.2559 | -41.0112 | -47.0215 | -51.6646 | -55.005 | -57.2902 | -55.7576 | -55.5027 | -54.5659
56002 | 1.8896 | 3.9029 | 6.4074 | 9.5733 | 13.204 | 17.6564 | 23.0043 | 35.5383 | 45.9433 | 55.998 | -17.2831 | -21.2747 | -25.4701 | -29.2028 | -32.0864 | -34.161 | -35.5802 | -34.6284 | -34.4701 | -33.8883
56003 | 17.4494 | 36.1803 | 59.5566 | 89.0997 | 122.9245 | 164.2851 | 213.8514 | 329.6149 | 425.796 | 518.6337 | -135.6884 | -173.4517 | -213.5697 | -249.8885 | -278.6474 | -300.2502 | -316.1685 | -311.9251 | -315.2371 | -314.1675
56004 | 53.7373 | 106.4093 | 174.2584 | 264.5873 | 372.0734 | 507.6145 | 673.1255 | 1067.925 | 1393.9554 | 1710.2482 | -426.8565 | -527.4909 | -633.7844 | -727.3112 | -797.7701 | -844.8232 | -872.398 | -816.5007 | -789.5301 | -751.2028
57003 | 24.6598 | 49.4408 | 79.5887 | 115.9301 | 155.9433 | 203.2192 | 258.6053 | 384.5858 | 489.8027 | 590.5253 | -216.1163 | -268.4341 | -324.4466 | -376.5142 | -419.5008 | -454.5454 | -483.7062 | -497.8861 | -518.1148 | -532.6502
57004 | 94.1464 | 188.7034 | 303.764 | 442.5147 | 595.3326 | 775.9393 | 987.5729 | 1469.0604 | 1871.197 | 2256.1967 | -824.5172 | -1024.1071 | -1237.7994 | -1436.438 | -1600.4195 | -1734.0769 | -1845.2643 | -1899.0609 | -1976.0488 | -2031.3247
57005 | 12.0565 | 24.1966 | 38.9807 | 56.8365 | 76.5291 | 99.8314 | 127.1593 | 189.3954 | 241.3612 | 291.1264 | -105.2044 | -130.7893 | -158.1729 | -183.603 | -204.5665 | -221.6101 | -235.7397 | -242.3061 | -251.9109 | -258.7247
57006 | 143.9197 | 294.0253 | 470.7652 | 670.6773 | 878.4505 | 1110.832 | 1372.7557 | 1940.5872 | 2419.9918 | 2872.0596 | -1598.2923 | -1930.618 | -2288.3242 | -2628.6677 | -2919.8294 | -3173.0176 | -3401.4009 | -3618.914 | -3846.2553 | -4037.3675
61021 | 99.2597 | 176.8157 | 266.3377 | 364.5187 | 463.6806 | 571.6217 | 690.8063 | 943.1134 | 1155.3846 | 1353.1755 | -879.0516 | -1049.0745 | -1230.213 | -1401.5286 | -1547.7151 | -1675.5431 | -1791.8087 | -1914.7485 | -2036.4213 | -2140.3129
61023 | 114.8176 | 210.8111 | 321.6007 | 443.6813 | 567.8151 | 704.1891 | 856.0241 | 1181.0626 | 1455.26 | 1712.6867 | -1047.4344 | -1255.29 | -1475.0891 | -1680.3786 | -1852.7777 | -2000.2802 | -2131.0978 | -2257.4704 | -2386.2011 | -2492.933
61024 | 13.8621 | 26.6285 | 41.5984 | 58.2315 | 75.153 | 93.5921 | 113.9485 | 157.5167 | 193.9552 | 227.6778 | -132.2379 | -161.4126 | -193.2493 | -224.2806 | -251.6375 | -276.4247 | -299.8236 | -326.4705 | -352.7485 | -375.7526
61025 | 68.7394 | 132.1667 | 206.585 | 289.3305 | 373.5593 | 465.3818 | 566.8622 | 783.994 | 965.5906 | 1133.6613 | -660.8712 | -805.8961 | -964.2502 | -1118.7126 | -1254.9947 | -1378.5785 | -1495.3432 | -1628.4614 | -1759.7353 | -1874.8009
61026 | 8.7478 | 16.8054 | 26.2542 | 36.7534 | 47.4352 | 59.0754 | 71.9271 | 99.4324 | 122.4367 | 143.7265 | -83.5033 | -101.9179 | -122.0137 | -141.6024 | -158.8727 | -174.5219 | -189.2956 | -206.1216 | -222.7145 | -237.2418
61027 | 93.2808 | 179.2568 | 280.0966 | 392.1731 | 506.2205 | 630.5184 | 767.803 | 1061.5928 | 1307.304 | 1534.7068 | -892.7411 | -1089.2622 | -1303.7688 | -1512.9134 | -1697.3549 | -1864.5295 | -2022.3983 | -2202.2629 | -2379.6363 | -2534.9939
61028 | 154.9692 | 278.3587 | 418.99 | 570.0036 | 719.5347 | 879.2531 | 1053.1917 | 1414.8871 | 1721.0349 | 2005.2505 | -1408.7214 | -1678.8645 | -1964.7424 | -2233.6233 | -2462.0103 | -2661.4666 | -2842.7344 | -3041.7889 | -3235.8349 | -3401.3014
61029 | 30.5675 | 61.8971 | 99.0792 | 141.0234 | 184.2517 | 231.8576 | 285.136 | 399.3977 | 495.3811 | 584.646 | -327.3007 | -399.5323 | -479.2618 | -557.9867 | -628.3529 | -692.9662 | -754.8194 | -825.8376 | -896.8376 | -960.2724
61037 | 36.4386 | 69.9971 | 109.3478 | 153.0704 | 197.5512 | 246.0212 | 299.5313 | 414.057 | 509.8412 | 598.4864 | -347.6079 | -424.2981 | -507.9856 | -589.5563 | -661.4681 | -726.6252 | -788.1328 | -858.1784 | -927.254 | -987.7239
61039 | 26.0623 | 50.0647 | 78.2098 | 109.482 | 141.2964 | 175.964 | 214.2365 | 296.1498 | 364.6584 | 428.0609 | -248.6228 | -303.4746 | -363.3312 | -421.6737 | -473.1079 | -519.7108 | -563.7035 | -613.8028 | -663.2084 | -706.4588
61040 | 46.5501 | 89.4246 | 139.7006 | 195.5643 | 252.3981 | 314.3303 | 382.7058 | 529.0455 | 651.4373 | 764.7074 | -444.2269 | -542.2091 | -649.1343 | -753.3585 | -845.2449 | -928.5035 | -1007.102 | -1096.6154 | -1184.8892 | -1262.17
61041 | 69.7759 | 134.3167 | 210.0979 | 294.4351 | 380.3471 | 474.0557 | 577.7626 | 799.577 | 985.0863 | 1156.7897 | -677.4903 | -825.1605 | -986.5282 | -1144.0773 | -1283.2246 | -1409.5394 | -1529.0172 | -1665.4157 | -1799.9234 | -1918.0119
61043 | 140.1291 | 258.3208 | 396.5352 | 551.3029 | 710.6109 | 887.1295 | 1084.5664 | 1509.2339 | 1865.4533 | 2199.0017 | -1273.4333 | -1533.6468 | -1812.7275 | -2077.9019 | -2304.8504 | -2503.0282 | -2682.8343 | -2863.2741 | -3046.2989 | -3201.4758
62004 | 41.8626 | 87.1544 | 141.2069 | 202.6029 | 266.244 | 336.6542 | 415.9171 | 586.0523 | 729.2365 | 862.6717 | -475.039 | -579.8892 | -696.2299 | -811.7738 | -915.6779 | -1011.6384 | -1104.0453 | -1210.507 | -1317.5408 | -1413.9541
62005 | 23.3328 | 48.5768 | 78.7038 | 112.9239 | 148.3952 | 187.6394 | 231.8178 | 326.6453 | 406.4512 | 480.8234 | -264.7703 | -323.2102 | -388.0545 | -452.4547 | -510.3672 | -563.8523 | -615.3567 | -674.6948 | -734.3517 | -788.0891
62006 | 38.1228 | 76.2433 | 121.3651 | 172.0981 | 224.2383 | 281.5289 | 345.4612 | 482.5128 | 597.5347 | 704.3961 | -397.4977 | -485.2152 | -581.7959 | -676.8926 | -761.6413 | -839.2411 | -913.3084 | -998.2057 | -1082.8419 | -1158.1466
62008 | 38.5638 | 80.2735 | 130.0496 | 186.586 | 245.1879 | 310.0212 | 383.0038 | 539.6576 | 671.4947 | 794.354 | -437.4593 | -534.0149 | -641.1488 | -747.5456 | -843.2208 | -931.5787 | -1016.6618 | -1114.684 | -1213.2299 | -1301.9937
62009 | 32.3059 | 63.6569 | 100.6429 | 142.0556 | 184.4665 | 230.9328 | 282.5941 | 393.2796 | 486.0634 | 572.1507 | -326.1407 | -398.1056 | -477.0931 | -554.5918 | -623.3983 | -686.1726 | -745.8629 | -814.1303 | -881.9378 | -941.9414
62010 | 55.6004 | 115.7487 | 187.5307 | 269.0639 | 353.5776 | 447.0796 | 552.3365 | 778.2665 | 968.4065 | 1145.5997 | -630.8562 | -770.0983 | -924.5983 | -1078.0383 | -1216.0194 | -1343.4502 | -1466.1606 | -1607.534 | -1749.6656 | -1877.6921
62011 | 2.9648 | 6.1724 | 10.0005 | 14.3486 | 18.8558 | 23.8424 | 29.4559 | 41.5051 | 51.6456 | 61.0957 | -33.643 | -41.0686 | -49.3081 | -57.4911 | -64.8497 | -71.6458 | -78.1902 | -85.73 | -93.3103 | -100.1384
62013 | 35.2374 | 72.8719 | 117.7277 | 168.5964 | 221.255 | 279.4526 | 344.8796 | 485.2887 | 603.4057 | 713.429 | -394.3624 | -481.403 | -577.8648 | -673.5373 | -759.4515 | -838.6926 | -914.8961 | -1002.6218 | -1090.7065 | -1169.9048
65060 | 7.8918 | 15.4526 | 24.4235 | 34.5337 | 44.9367 | 56.3804 | 69.2547 | 96.6822 | 119.6145 | 140.8824 | -87.6788 | -105.1422 | -124.4329 | -143.5105 | -160.5944 | -176.3219 | -191.4173 | -208.9589 | -226.2555 | -241.751
65061 | 34.4172 | 67.4171 | 106.5813 | 150.7317 | 196.1708 | 246.1757 | 302.4283 | 422.2826 | 522.4934 | 615.4792 | -383.5109 | -459.7487 | -543.9842 | -627.3132 | -701.9557 | -770.6932 | -836.688 | -913.4059 | -989.0519 | -1056.8493
65062 | 48.5587 | 95.058 | 150.2226 | 212.3826 | 276.3347 | 346.6678 | 425.7956 | 594.3598 | 735.2985 | 865.9667 | -538.5555 | -645.9437 | -764.5519 | -881.831 | -986.8345 | -1083.4847 | -1176.2331 | -1283.9883 | -1390.2384 | -1485.4022
65063 | 19.528 | 37.2552 | 58.0589 | 81.2352 | 104.8822 | 130.7375 | 159.3161 | 220.6564 | 271.9723 | 319.5329 | -185.6725 | -226.023 | -269.9982 | -312.7657 | -350.3681 | -384.3168 | -416.244 | -452.106 | -487.5784 | -518.5472
65064 | 40.4719 | 78.1523 | 122.4828 | 171.9371 | 222.4125 | 277.5481 | 338.7867 | 469.6415 | 579.0733 | 680.3788 | -403.339 | -489.7065 | -584.2801 | -676.8442 | -758.8169 | -833.4357 | -904.2213 | -985.3212 | -1065.2952 | -1135.7983
65065 | 36.1258 | 70.3348 | 110.9498 | 156.8144 | 204.1092 | 256.2106 | 314.9008 | 440.3473 | 545.1855 | 642.4112 | -399.7953 | -478.5683 | -565.5023 | -651.3385 | -728.0593 | -798.5154 | -865.971 | -943.6324 | -1020.3693 | -1089.0212
65066 | 74.5189 | 136.847 | 210.8724 | 297.0323 | 389.2143 | 495.5666 | 618.177 | 892.4497 | 1121.0472 | 1338.3235 | -881.841 | -1013.0696 | -1151.8443 | -1279.8282 | -1384.9711 | -1471.088 | -1543.3391 | -1589.2949 | -1643.9325 | -1682.2818
65067 | 43.1917 | 76.9364 | 118.7076 | 171.3125 | 231.4982 | 305.2221 | 393.6951 | 601.0875 | 772.56 | 938.0373 | -344.212 | -410.1911 | -479.0169 | -539.6705 | -585.9645 | -618.6534 | -640.2901 | -622.3836 | -616.956 | -604.4327
66101 | 27.1163 | 52.0786 | 81.3578 | 113.913 | 147.0572 | 183.2036 | 223.1062 | 308.6158 | 380.125 | 446.3276 | -258.4195 | -315.4267 | -377.6253 | -438.2286 | -491.6311 | -539.985 | -585.5981 | -637.39 | -688.5105 | -733.2342
66102 | 75.6641 | 145.3564 | 227.0807 | 317.8891 | 410.2758 | 510.9509 | 622.1025 | 859.9918 | 1058.9516 | 1243.0832 | -722.1743 | -881.4455 | -1055.256 | -1224.6783 | -1374.0472 | -1509.3933 | -1637.166 | -1782.6857 | -1926.1903 | -2051.8269
66103 | 63.7443 | 122.9131 | 192.461 | 269.9613 | 348.9913 | 435.2607 | 530.9208 | 735.4178 | 906.4393 | 1064.7482 | -627.6979 | -763.2074 | -911.451 | -1056.3798 | -1184.567 | -1301.1065 | -1411.5118 | -1537.7978 | -1662.3317 | -1771.9102
66105 | 51.841 | 99.5844 | 155.5682 | 217.7721 | 281.0546 | 350.0124 | 426.1408 | 589.0756 | 725.347 | 851.4617 | -494.539 | -603.6454 | -722.707 | -838.7569 | -941.0653 | -1033.7638 | -1121.2702 | -1220.9235 | -1319.1968 | -1405.2267
66106 | 60.1951 | 116.6591 | 183.238 | 257.7142 | 333.8942 | 417.2424 | 510.1895 | 708.5864 | 874.493 | 1028.1097 | -617.7202 | -747.4051 | -889.7434 | -1029.4459 | -1153.5366 | -1266.8429 | -1374.6755 | -1498.7075 | -1621.0145 | -1729.3256
66107 | 23.3467 | 44.848 | 70.0604 | 98.0741 | 126.5734 | 157.6287 | 191.9133 | 265.2913 | 326.6613 | 383.4574 | -222.7165 | -271.8528 | -325.4724 | -377.7357 | -423.8105 | -465.5574 | -504.9661 | -549.8451 | -594.1027 | -632.8464
66108 | 0.081065 | 0.15572 | 0.24327 | 0.34053 | 0.43949 | 0.54732 | 0.66637 | 0.92115 | 1.1342 | 1.3314 | -0.77332 | -0.94393 | -1.1301 | -1.3116 | -1.4716 | -1.6165 | -1.7534 | -1.9092 | -2.0629 | -2.1974
66109 | 25.7381 | 49.4418 | 77.2368 | 108.1198 | 139.5384 | 173.7747 | 211.5711 | 292.4652 | 360.1214 | 422.7351 | -245.5295 | -299.6989 | -358.8108 | -416.4274 | -467.2216 | -513.2447 | -556.69 | -606.1661 | -654.957 | -697.6692
67081 | 38.7556 | 74.3309 | 116.0618 | 162.4926 | 209.8019 | 261.4499 | 318.469 | 440.7811 | 543.0918 | 637.8625 | -372.2114 | -453.3284 | -541.7748 | -627.8661 | -703.6388 | -772.1459 | -836.6696 | -909.5622 | -981.5434 | -1044.487
67082 | 113.6825 | 194.767 | 290.5221 | 400.307 | 516.1037 | 647.8076 | 798.1697 | 1129.9941 | 1408.7234 | 1673.175 | -975.1135 | -1149.6589 | -1335.435 | -1508.873 | -1653.7199 | -1775.4455 | -1880.9126 | -1963.8156 | -2055.9838 | -2128.5182
67083 | 20.7321 | 39.3901 | 61.0989 | 85.1052 | 109.5101 | 136.2021 | 165.7763 | 228.5301 | 281.5508 | 331.098 | -211.7673 | -253.492 | -298.3651 | -341.2302 | -378.1591 | -410.7238 | -440.5819 | -472.1015 | -503.6538 | -530.6097
67084 | 21.0124 | 37.7343 | 57.6313 | 80.6974 | 105.2528 | 133.4006 | 165.7052 | 237.4098 | 297.5924 | 354.7993 | -193.323 | -229.4034 | -267.9759 | -304.1159 | -334.3879 | -359.849 | -381.9194 | -398.6332 | -417.6294 | -432.5776
67085 | 28.3322 | 54.4249 | 85.0213 | 119.0169 | 153.6021 | 191.289 | 232.8948 | 321.942 | 396.4171 | 465.3415 | -270.2758 | -329.9047 | -394.9744 | -458.398 | -514.3117 | -564.9733 | -612.7974 | -667.26 | -720.9684 | -767.9855
67086 | 80.619 | 154.8658 | 241.9275 | 338.662 | 437.0739 | 544.3117 | 662.7006 | 916.0839 | 1128.0024 | 1324.1262 | -769.0681 | -938.7418 | -1123.897 | -1304.3686 | -1463.4706 | -1607.628 | -1743.711 | -1898.684 | -2051.5109 | -2185.2978
67087 | 97.6321 | 188.0395 | 294.3409 | 414.3057 | 538.6885 | 677.451 | 833.5047 | 1171.0465 | 1455.287 | 1722.691 | -1054.9842 | -1255.0663 | -1470.3722 | -1675.365 | -1850.9741 | -2004.0971 | -2142.6957 | -2277.4371 | -2416.6516 | -2533.3177
67088 | 646.7543 | 695.2137 | 751.7877 | 814.5158 | 878.3246 | 948.0176 | 1025.0438 | 1188.0345 | 1324.8434 | 1451.8649 | -1199.9139 | -1309.3419 | -1427.7799 | -1541.947 | -1641.3556 | -1730.1996 | -1812.8556 | -1904.6815 | -1995.1642 | -2071.9607
67089 | 52.3679 | 100.5966 | 157.1495 | 219.9855 | 283.9112 | 353.57 | 430.4722 | 595.063 | 732.7195 | 860.1162 | -499.5656 | -609.781 | -730.0527 | -847.2822 | -950.6305 | -1044.2712 | -1132.667 | -1233.3332 | -1332.6054 | -1419.5097
67090 | 98.667 | 192.6272 | 304.3667 | 433.5841 | 570.7581 | 727.4885 | 906.889 | 1303.7893 | 1636.643 | 1952.419 | -948.5405 | -1152.2551 | -1370.5424 | -1575.9245 | -1748.9183 | -1895.6301 | -2024.1082 | -2127.1658 | -2241.5317 | -2334.4926
67091 | 51.1728 | 100.0617 | 158.0222 | 223.2801 | 290.3767 | 364.0827 | 447.0187 | 623.6404 | 771.3184 | 908.119 | -562.744 | -675.5823 | -800.1237 | -923.1693 | -1033.2405 | -1134.4674 | -1231.5211 | -1344.1581 | -1455.2226 | -1554.5795
80001 | 19.8223 | 41.2083 | 66.5622 | 95.0938 | 124.4417 | 156.705 | 192.518 | 269.4795 | 334.4548 | 395.0303 | -203.6131 | -253.0379 | -307.5958 | -361.458 | -409.5859 | -453.7572 | -496.0102 | -544.4228 | -593.2317 | -636.7925
80002 | 1.3748 | 2.858 | 4.6164 | 6.5952 | 8.6306 | 10.8682 | 13.3521 | 18.6897 | 23.1961 | 27.3973 | -14.1216 | -17.5494 | -21.3333 | -25.0689 | -28.4068 | -31.4703 | -34.4007 | -37.7584 | -41.1435 | -44.1646
80003 | 37.4706 | 77.897 | 125.824 | 179.758 | 235.2349 | 296.223 | 363.9211 | 509.4031 | 632.2275 | 746.7347 | -384.8944 | -478.3233 | -581.4552 | -683.2721 | -774.2494 | -857.7474 | -937.6193 | -1029.1347 | -1121.3992 | -1203.7433
80004 | 35.5843 | 73.9756 | 119.4898 | 170.7088 | 223.3929 | 281.3107 | 345.6008 | 483.7591 | 600.4003 | 709.1431 | -365.5183 | -454.2438 | -552.184 | -648.8753 | -735.2727 | -814.5673 | -890.4183 | -977.3267 | -1064.9465 | -1143.1453
80005 | 91.1905 | 189.5719 | 306.2061 | 437.4582 | 572.4641 | 720.8812 | 885.6268 | 1239.6597 | 1538.5557 | 1817.2117 | -936.7086 | -1164.0761 | -1415.0558 | -1662.8343 | -1884.2327 | -2087.4291 | -2281.8002 | -2504.5058 | -2729.0331 | -2929.4186
80006 | 27.5092 | 56.9207 | 91.7241 | 130.7906 | 170.889 | 214.8927 | 263.6784 | 368.2346 | 456.6139 | 538.9849 | -283.6591 | -351.5716 | -426.4225 | -500.1948 | -565.9981 | -626.2937 | -683.8735 | -749.8054 | -816.1305 | -875.2876
80007 | 51.8258 | 107.7398 | 174.0279 | 248.6244 | 325.3547 | 409.7077 | 503.3414 | 704.5584 | 874.4375 | 1032.8131 | -532.3496 | -661.5717 | -804.214 | -945.0377 | -1070.8688 | -1186.3555 | -1296.8267 | -1423.4022 | -1551.0137 | -1664.9043
80008 | 83.1579 | 172.8756 | 279.2391 | 398.934 | 522.0529 | 657.4027 | 807.644 | 1130.5098 | 1403.0918 | 1657.2159 | -854.1896 | -1061.5348 | -1290.4138 | -1516.3744 | -1718.2788 | -1903.5845 | -2080.8429 | -2283.9415 | -2488.7025 | -2671.4473
80009 | 51.1864 | 106.4105 | 171.8807 | 245.5568 | 321.3405 | 404.6527 | 497.1311 | 695.8655 | 863.6486 | 1020.0702 | -525.7815 | -653.4092 | -794.2916 | -933.3777 | -1057.6564 | -1171.7181 | -1280.8264 | -1405.8402 | -1531.8772 | -1644.3626
80010 | 6.8419 | 14.2235 | 22.9747 | 32.8227 | 42.9524 | 54.0885 | 66.4498 | 93.0139 | 115.4409 | 136.3492 | -70.2793 | -87.3389 | -106.1701 | -124.7613 | -141.3732 | -156.6194 | -171.2035 | -187.9137 | -204.7606 | -219.7961
80011 | 45.8207 | 95.5958 | 154.2124 | 219.8431 | 287.1702 | 361.196 | 443.4475 | 618.513 | 767.198 | 906.0183 | -498.2808 | -611.6929 | -735.5551 | -856.1548 | -962.2678 | -1058.0001 | -1147.9477 | -1247.0632 | -1346.7872 | -1434.796
81001 | 16.0944 | 33.4676 | 54.0535 | 77.2103 | 101.0246 | 127.205 | 156.268 | 218.6774 | 271.3914 | 320.5414 | -166.079 | -206.1855 | -250.4208 | -294.0457 | -332.981 | -368.6698 | -402.764 | -441.7198 | -480.989 | -516.0086
81002 | 32.2842 | 67.5549 | 108.8605 | 154.9127 | 202.0479 | 253.8789 | 311.5177 | 434.2572 | 537.9881 | 635.0687 | -367.3486 | -446.7631 | -532.7069 | -615.377 | -687.1147 | -750.8108 | -809.6354 | -871.9321 | -934.6986 | -989.0113
81003 | 97.2166 | 203.4276 | 327.8068 | 466.4746 | 608.4011 | 764.4662 | 938.0191 | 1307.5977 | 1619.9379 | 1912.2556 | -1106.4737 | -1345.5984 | -1604.3684 | -1853.2634 | -2069.2252 | -2260.9589 | -2438.0093 | -2625.4626 | -2814.3333 | -2977.7383
82001 | 18.0706 | 37.3695 | 60.201 | 85.8213 | 112.1113 | 140.9555 | 172.9293 | 241.4318 | 299.3443 | 353.3178 | -186.421 | -230.978 | -280.0781 | -328.4605 | -371.6074 | -411.1349 | -448.8741 | -492.084 | -535.5398 | -574.2962
82002 | 90.344 | 182.3146 | 290.0488 | 409.3165 | 530.2956 | 661.7443 | 806.4834 | 1111.8628 | 1371.8246 | 1613.7211 | -948.1242 | -1159.436 | -1390.3838 | -1615.8765 | -1815.0354 | -1995.8301 | -2166.7973 | -2361.7403 | -2555.3864 | -2727.4453
82003 | 106.3843 | 203.9898 | 318.1698 | 444.9242 | 574.0396 | 715.2163 | 871.5053 | 1202.1187 | 1482.0546 | 1743.7656 | -1003.1087 | -1224.41 | -1464.5724 | -1696.673 | -1899.2461 | -2080.5071 | -2249.3188 | -2433.6381 | -2618.348 | -2779.9024
82004 | 34.3094 | 69.2939 | 110.2755 | 155.6426 | 201.6577 | 251.6502 | 306.6929 | 422.8285 | 521.6876 | 613.673 | -360.672 | -441.0684 | -528.9447 | -614.7582 | -690.5631 | -759.3923 | -824.4941 | -898.7694 | -972.5419 | -1038.1042
82005 | 75.0839 | 151.6455 | 241.3313 | 340.6144 | 441.3157 | 550.7213 | 671.1788 | 925.3346 | 1141.6817 | 1342.986 | -789.3087 | -965.2514 | -1157.5634 | -1345.361 | -1511.2555 | -1661.8841 | -1804.3554 | -1966.9023 | -2128.3489 | -2271.828
82006 | 8.6467 | 17.4637 | 27.792 | 39.2255 | 50.8224 | 63.4217 | 77.2937 | 106.5626 | 131.4773 | 154.6598 | -90.8977 | -111.1594 | -133.3063 | -154.9333 | -174.0379 | -191.3844 | -207.7916 | -226.5107 | -245.103 | -261.6263
82007 | 20.4539 | 41.4598 | 66.105 | 93.4468 | 121.2312 | 151.4654 | 184.7909 | 255.2831 | 315.2204 | 371.0052 | -214.411 | -262.7193 | -315.5902 | -367.2946 | -413.0383 | -454.6329 | -494.0352 | -539.016 | -583.7845 | -623.5941
82008 | 75.3616 | 152.2062 | 242.2237 | 341.8739 | 442.9476 | 552.7578 | 673.6607 | 928.7564 | 1145.9034 | 1347.9522 | -792.2274 | -968.8207 | -1161.8439 | -1350.336 | -1516.8439 | -1668.0294 | -1811.0276 | -1974.1756 | -2136.2192 | -2280.2288
85001 | 111.2711 | 226.4402 | 363.0816 | 520.8271 | 688.177 | 879.4482 | 1098.5331 | 1583.7804 | 1991.1603 | 2378.0558 | -1197.679 | -1445.8616 | -1710.7403 | -1958.6118 | -2166.0634 | -2340.5806 | -2491.9427 | -2608.6404 | -2739.9531 | -2844.237
85002 | 86.8315 | 172.7914 | 276.0598 | 398.0219 | 530.0656 | 683.8573 | 862.359 | 1263.9959 | 1600.4793 | 1921.8209 | -874.3298 | -1057.2892 | -1252.5552 | -1434.1697 | -1584.572 | -1708.4504 | -1812.9786 | -1876.0157 | -1955.3757 | -2014.913
85003 | 56.2017 | 114.9942 | 184.9215 | 265.3908 | 350.3156 | 446.6354 | 556.2551 | 796.7486 | 998.9826 | 1190.2585 | -600.6334 | -729.9636 | -869.6442 | -1002.7751 | -1116.7795 | -1215.7105 | -1304.7506 | -1385.5522 | -1472.0081 | -1545.0886
85004 | 22.3108 | 46.6688 | 75.1746 | 106.9188 | 139.3751 | 175.0291 | 214.6506 | 298.944 | 370.2171 | 436.9136 | -252.2191 | -307.0727 | -366.4197 | -423.4955 | -473.0174 | -516.9907 | -557.6042 | -600.708 | -644.1092 | -681.6901
85005 | 0.040308 | 0.083895 | 0.13446 | 0.18989 | 0.24576 | 0.30627 | 0.37286 | 0.51258 | 0.63156 | 0.7427 | -0.41469 | -0.51318 | -0.61944 | -0.72148 | -0.80999 | -0.88875 | -0.9617 | -1.0416 | -1.1215 | -1.1913
85006 | 108.2712 | 214.967 | 343.558 | 496.3667 | 662.7109 | 857.4313 | 1084.2222 | 1596.6509 | 2025.5785 | 2435.7373 | -1081.9749 | -1307.9497 | -1548.958 | -1772.5201 | -1956.8968 | -2107.5975 | -2233.4728 | -2302.0066 | -2392.6283 | -2458.7455
85008 | 62.8395 | 131.4767 | 211.8505 | 301.4407 | 393.1184 | 493.9063 | 605.9689 | 844.5428 | 1046.1944 | 1234.9103 | -713.5967 | -868.1663 | -1035.4516 | -1196.3818 | -1336.0499 | -1460.0876 | -1574.6657 | -1696.1288 | -1818.4845 | -1924.4106
89001 | 0.13816 | 0.27431 | 0.4384 | 0.63339 | 0.84565 | 1.0941 | 1.3835 | 2.0374 | 2.5847 | 3.1081 | -1.3807 | -1.669 | -1.9766 | -2.2618 | -2.4971 | -2.6894 | -2.85 | -2.9375 | -3.0531 | -3.1375
89002 | 0.046053 | 0.091436 | 0.14613 | 0.21113 | 0.28188 | 0.36471 | 0.46117 | 0.67914 | 0.86158 | 1.036 | -0.46022 | -0.55634 | -0.65885 | -0.75394 | -0.83237 | -0.89647 | -0.95001 | -0.97916 | -1.0177 | -1.0458
90018 | 0.029838 | 0.05764 | 0.091241 | 0.13023 | 0.17141 | 0.21779 | 0.27081 | 0.3861 | 0.4825 | 0.57263 | -0.28263 | -0.34649 | -0.41769 | -0.48862 | -0.55257 | -0.61164 | -0.66856 | -0.73235 | -0.79783 | -0.85646
90019 | 0.14919 | 0.2882 | 0.4562 | 0.65113 | 0.85703 | 1.0889 | 1.3541 | 1.9305 | 2.4125 | 2.8632 | -1.4131 | -1.7325 | -2.0884 | -2.4431 | -2.7629 | -3.0582 | -3.3428 | -3.6617 | -3.9892 | -4.2823
90020 | 3.2822 | 6.3403 | 10.0365 | 14.3249 | 18.8546 | 23.9565 | 29.7896 | 42.4715 | 53.0753 | 62.9895 | -31.0888 | -38.1144 | -45.9459 | -53.7482 | -60.7829 | -67.2808 | -73.5421 | -80.5581 | -87.7614 | -94.2107
90021 | 5.9377 | 11.4703 | 18.1569 | 25.9151 | 34.1097 | 43.3394 | 53.8921 | 76.8349 | 96.018 | 113.9538 | -56.2425 | -68.9524 | -83.1203 | -97.2353 | -109.9618 | -121.717 | -133.0443 | -145.7369 | -158.7684 | -170.4357
90023 | 14.6802 | 28.3587 | 44.8904 | 64.0716 | 84.3314 | 107.1507 | 133.2407 | 189.9637 | 237.3912 | 281.7349 | -139.0519 | -170.4753 | -205.5033 | -240.4009 | -271.8654 | -300.9285 | -328.9336 | -360.3143 | -392.5329 | -421.3786
90024 | 4.9829 | 9.6258 | 15.2372 | 21.7479 | 28.6247 | 36.3703 | 45.226 | 64.4795 | 80.5779 | 95.6295 | -47.1985 | -57.8646 | -69.7542 | -81.5995 | -92.2795 | -102.1444 | -111.6502 | -122.3018 | -133.2378 | -143.0289
91001 | 32.9156 | 62.4228 | 99.8597 | 148.2611 | 204.5758 | 274.2484 | 358.3139 | 556.028 | 719.9033 | 878.3219 | -262.118 | -321.0698 | -384.1516 | -441.5119 | -487.087 | -521.223 | -546.2629 | -536.2081 | -539.2882 | -536.0158
91002 | 34.7006 | 65.6752 | 104.4684 | 153.6444 | 210.0331 | 279.0078 | 361.6535 | 554.5657 | 714.7267 | 869.2471 | -280.7379 | -343.4876 | -410.5053 | -471.6549 | -520.6003 | -558.0033 | -586.3386 | -582.4619 | -590.5471 | -591.9075
91003 | 32.5695 | 62.894 | 99.5743 | 142.22 | 187.3552 | 238.2842 | 296.5082 | 423.5058 | 529.6634 | 629.0053 | -307.5954 | -377.0994 | -454.5257 | -531.5617 | -600.9058 | -664.8117 | -726.247 | -794.3997 | -864.6114 | -927.3624
91004 | 32.1832 | 64.5816 | 103.1029 | 147.0418 | 192.9339 | 244.3229 | 302.2232 | 427.3958 | 533.1056 | 632.6114 | -317.3047 | -390.3873 | -470.2091 | -547.6248 | -615.3222 | -675.7143 | -731.7582 | -789.2412 | -848.879 | -900.9256
91005 | 53.0214 | 106.7915 | 170.4715 | 242.6018 | 317.4599 | 400.7767 | 494.242 | 695.1706 | 865.134 | 1024.897 | -527.7324 | -649.3646 | -782.0793 | -910.7737 | -1023.3445 | -1123.927 | -1217.4264 | -1315.0778 | -1415.5254 | -1503.3878
91006 | 77.7913 | 156.5859 | 249.988 | 355.8339 | 465.6854 | 587.89 | 724.9014 | 1019.1555 | 1268.037 | 1501.8057 | -774.8216 | -953.4989 | -1148.8186 | -1338.7231 | -1505.3532 | -1654.8019 | -1794.3039 | -1941.7493 | -2093.0768 | -2225.8718
91007 | 39.8633 | 77.0064 | 121.8974 | 173.983 | 228.9975 | 290.962 | 361.8082 | 515.8363 | 644.6231 | 765.0363 | -377.588 | -462.9168 | -558.0335 | -652.7959 | -738.2361 | -817.1555 | -893.2017 | -978.4144 | -1065.9025 | -1144.2315
91008 | 89.1553 | 172.227 | 272.6268 | 389.1177 | 512.1591 | 650.7445 | 809.1938 | 1153.6817 | 1441.717 | 1711.0244 | -844.4857 | -1035.3258 | -1248.0569 | -1459.9955 | -1651.0849 | -1827.5903 | -1997.6696 | -2188.2502 | -2383.9196 | -2559.1045
91009 | 79.9776 | 159.5138 | 254.1261 | 361.3622 | 472.4323 | 595.4126 | 732.6533 | 1029.2628 | 1279.1935 | 1512.5769 | -795.1736 | -977.9627 | -1179.6468 | -1378.4395 | -1555.6991 | -1717.8407 | -1872.4323 | -2046.2936 | -2222.4567 | -2379.4355
91010 | 47.5017 | 91.7622 | 145.255 | 207.3211 | 272.8773 | 346.7153 | 431.1367 | 614.6791 | 768.1438 | 911.6301 | -449.9402 | -551.6194 | -664.962 | -777.8825 | -879.6945 | -973.7362 | -1064.3541 | -1165.895 | -1270.1472 | -1363.4854
91011 | 64.0244 | 121.3527 | 188.5181 | 263.4286 | 340.1198 | 424.4598 | 518.2549 | 717.9661 | 886.7783 | 1044.7997 | -586.8755 | -716.0627 | -855.9562 | -990.6217 | -1107.5752 | -1211.5115 | -1307.5909 | -1409.5171 | -1512.5067 | -1601.8927
91012 | 46.0678 | 91.4325 | 146.1002 | 210.3587 | 279.4388 | 359.1035 | 450.8318 | 654.8404 | 826.1085 | 988.9057 | -433.2628 | -532.6287 | -640.3985 | -743.1776 | -831.0336 | -906.6816 | -974.1001 | -1029.4455 | -1091.8179 | -1143.8305
93001 | 8.0013 | 16.954 | 27.7701 | 40.4441 | 53.9975 | 69.5053 | 87.2413 | 126.3139 | 159.1052 | 190.1047 | -96.1463 | -116.1417 | -138.0879 | -159.4103 | -178.0594 | -194.6166 | -209.9022 | -224.5097 | -240.0702 | -253.5889
93002 | 24.9514 | 52.8697 | 86.5988 | 126.1217 | 168.3869 | 216.7468 | 272.0552 | 393.9001 | 496.1569 | 592.8264 | -299.8245 | -362.1787 | -430.6162 | -497.1086 | -555.2643 | -606.8966 | -654.5636 | -700.1159 | -748.6401 | -790.7969
93003 | 32.9264 | 69.7679 | 114.2775 | 166.4327 | 222.2068 | 286.0234 | 359.0095 | 519.7985 | 654.7387 | 782.3057 | -395.6545 | -477.9384 | -568.2498 | -655.9946 | -732.738 | -800.873 | -863.7753 | -923.8871 | -987.9206 | -1043.5517
93004 | 7.8171 | 16.5636 | 27.1306 | 39.5128 | 52.7541 | 67.9048 | 85.2325 | 123.4054 | 155.4416 | 185.7273 | -93.9324 | -113.4674 | -134.9082 | -155.7397 | -173.9594 | -190.1353 | -205.069 | -219.3401 | -234.5423 | -247.7497
93005 | 35.0847 | 74.341 | 121.7681 | 177.342 | 236.7719 | 304.7716 | 382.5417 | 553.87 | 697.6552 | 833.584 | -421.5887 | -509.2661 | -605.4972 | -698.9934 | -780.7672 | -853.3683 | -920.3937 | -984.4457 | -1052.6764 | -1111.9539
93006 | 0.02632 | 0.05577 | 0.091349 | 0.13304 | 0.17762 | 0.22864 | 0.28698 | 0.41551 | 0.52337 | 0.62534 | -0.31627 | -0.38205 | -0.45424 | -0.52438 | -0.58572 | -0.64019 | -0.69047 | -0.73852 | -0.7897 | -0.83417
94001 | 26.2349 | 53.6132 | 87.7093 | 130.0422 | 177.6449 | 234.7152 | 302.1297 | 456.6937 | 585.3122 | 708.4882 | -262.273 | -320.3499 | -383.7059 | -443.8855 | -494.8428 | -537.6058 | -574.5679 | -595.1457 | -623.4817 | -645.8129
94002 | 94.9821 | 184.2786 | 294.9444 | 432.4475 | 587.5814 | 774.6768 | 996.8142 | 1509.7265 | 1936.8319 | 2347.672 | -814.331 | -999.4972 | -1198.2193 | -1382.0339 | -1532.2697 | -1651.7777 | -1747.8812 | -1770.2281 | -1821.4449 | -1853.0881
95001 | 11.2277 | 21.1973 | 33.9977 | 50.9505 | 71.0536 | 96.3403 | 127.1787 | 200.6076 | 261.3553 | 320.3448 | -85.3329 | -104.4972 | -124.7457 | -142.597 | -156.0926 | -165.1892 | -170.6312 | -160.5995 | -155.9723 | -149.2776
96202 | 0.018738 | 0.038838 | 0.064843 | 0.098929 | 0.13875 | 0.18787 | 0.24683 | 0.38464 | 0.49784 | 0.60605 | -0.16123 | -0.20268 | -0.24863 | -0.29287 | -0.33085 | -0.36297 | -0.39111 | -0.40442 | -0.42529 | -0.44116
97001 | 0.02092 | 0.043124 | 0.072067 | 0.1106 | 0.15618 | 0.21304 | 0.28182 | 0.44402 | 0.57709 | 0.70493 | -0.16488 | -0.2095 | -0.25857 | -0.30493 | -0.34369 | -0.37506 | -0.40098 | -0.40447 | -0.41793 | -0.42591
97002 | 24.5422 | 49.0128 | 80.7507 | 122.9322 | 172.8701 | 235.3367 | 311.1011 | 490.3389 | 637.8055 | 779.9783 | -190.872 | -239.3378 | -291.9692 | -340.6554 | -380.2084 | -410.7298 | -434.2737 | -428.4979 | -434.894 | -435.3585
97013 | 0.33808 | 0.59326 | 1.0189 | 1.8044 | 2.9297 | 4.5646 | 6.7263 | 12.2885 | 16.8248 | 21.3355 | -0.7686 | -0.94784 | -1.0703 | -0.98539 | -0.6686 | -0.044228 | 0.30892 | 0.43093 | 0.53772 | 0.63947
97014 | 0.02092 | 0.043124 | 0.072067 | 0.1106 | 0.15618 | 0.21304 | 0.28182 | 0.44402 | 0.57709 | 0.70493 | -0.16488 | -0.2095 | -0.25857 | -0.30493 | -0.34369 | -0.37506 | -0.40098 | -0.40447 | -0.41793 | -0.42591
98001 | 15.4549 | 30.3484 | 51.1195 | 81.9398 | 121.2025 | 173.1289 | 238.2189 | 397.9263 | 528.1214 | 654.9227 | -112.8495 | -137.779 | -164.1367 | -186.1449 | -200.9978 | -207.6753 | -207.2435 | -168.1077 | -142.4607 | -113.5338
98002 | 15.571 | 32.2747 | 53.8844 | 82.2098 | 115.3013 | 156.117 | 205.1135 | 319.6396 | 413.7081 | 503.6292 | -133.9855 | -168.4251 | -206.6153 | -243.3755 | -274.9333 | -301.629 | -325.0113 | -336.0736 | -353.4157 | -366.6054
98003 | 12.1719 | 24.5349 | 41.0545 | 64.0462 | 92.1497 | 128.1808 | 172.5338 | 279.2122 | 366.6481 | 451.2658 | -90.7718 | -113.829 | -138.7459 | -161.2201 | -178.737 | -191.0298 | -199.1045 | -186.694 | -182.1483 | -174.7917
99981 | 61.0108 | 102.1027 | 176.8774 | 326.2831 | 547.7003 | 871.3094 | 1300.0607 | 2410.8315 | 3315.3937 | 4216.4649 | -59.8884 | -69.8691 | -64.7747 | -16.8319 | 21.2762 | 26.9599 | 33.4887 | 47.14 | 59.035 | 70.3875
99982 | 0.094419 | 0.15798 | 0.27371 | 0.50508 | 0.84804 | 1.3493 | 2.0136 | 3.7344 | 5.1358 | 6.5318 | -0.091318 | -0.10645 | -0.098186 | -0.023535 | 0.032727 | 0.041484 | 0.051548 | 0.0726 | 0.090941 | 0.10845
99983 | 0.18884 | 0.31595 | 0.54742 | 1.0102 | 1.6961 | 2.6987 | 4.0271 | 7.4689 | 10.2717 | 13.0636 | -0.18264 | -0.2129 | -0.19637 | -0.04707 | 0.065453 | 0.082968 | 0.1031 | 0.1452 | 0.18188 | 0.21689
| 115.0968 | 209.5155 | 321.987 | 451.5273 | 588.2257 | 743.1487 | 919.3627 | 1305.6352 | 1630.0944 | 1936.5227 | -960.2553 | -1168.9962 | -1395.4586 | -1613.1061 | -1801.2946 | -1966.8131 | -2118.1694 | -2263.7213 | -2417.9655 | -2549.5057
Column index | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21