## Disclaimer
TasNetworks - Annual Planning Report 2025 - Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2025.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Methodology
Fault level and sequence impedances
We calculate fault currents at transmission network substations in accordance with the recommendations of Australian Standard AS 3851-1991 – “The calculation of short-circuit currents in three-phase AC systems”. From this, the maximum fault currents calculated at 1.1 pu voltage and the minimum at 0.9 pu voltage. The Thevenin impedance is defined as the source impedance back to the generators, and large motors where considered. This method thus defines the extreme envelope for all fault currents and is appropriate to be used for future planning. We recognise that at particular network locations the actual envelope could be smaller but this would need confirmation with detailed local studies.
Figure B–1 illustrates the AC and DC components that make up fault currents. The size and rate of decay of the DC component is a function of the ratio between the reactance (X) and the resistance (R) of the impedance between the faulted point of the system and the generation feeding the fault. This ratio is defined as the X/R ratio of the system, with the DC component decaying with time constant X/2πfR.
The maximum current that a circuit breaker will be exposed to is defined as the Peak Make Current. During fault conditions, the current a circuit breaker is expected to break is known as the RMS Break Current. This is defined as the RMS of the symmetrical AC component of the fault current plus the offset by the DC component at that point.
Figure B–1: Components of AC fault current

## Maximum
Maximum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU (100 MVA Base)
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 3.8731 | 3.6404 | 0.053012 | 0.13935 | 2.6286 | 0.05496 | 0.14201 | 2.5838 | 0.031475 | 0.17363 | 5.5165
Arthurs Lake | 6.6 | 18.9397 | 0.0026907 | 0.052106 | 0.50539 | 9.6991 | 0.063191 | 0.55639 | 8.8048 | 0 | 0 | 0.00012399
Avoca | 110 | 1.8189 | 1.1983 | 0.15116 | 0.27931 | 1.8478 | 0.15119 | 0.28007 | 1.8525 | 0.22869 | 0.78753 | 3.4437
Avoca | 22 | 3.5661 | 1.5702 | 0.17566 | 0.79041 | 4.4996 | 0.17569 | 0.79117 | 4.5033 | 0 | 3.9308 | >50
Boyer | 110 | 10.7798 | 6.9648 | 0.0091073 | 0.05278 | 5.7953 | 0.0090932 | 0.053838 | 5.9207 | 0.028623 | 0.13764 | 4.8086
Boyer (A & B) | 6.6 | 25.318 | 8.4972 | 0.01766 | 0.37966 | 21.4986 | 0.017644 | 0.38062 | 21.5721 | 0 | 2.637 | >50
Boyer (D & E) | 6.6 | 35.4556 | 16.7824 | 0.010098 | 0.27121 | 26.8586 | 0.010091 | 0.27177 | 26.9323 | 0.0013249 | 1.177 | >50
Boyer (F) | 6.6 | 28.843 | 12.3944 | 0.0070115 | 0.33354 | 47.571 | 0.0070023 | 0.33381 | 47.6709 | 0.00076509 | 1.6617 | >50
Boyer (G) | 6.6 | 24.4985 | 11.7947 | 0.0093908 | 0.39267 | 41.8144 | 0.0093807 | 0.39303 | 41.8975 | 0.0060606 | 1.6618 | >50
Bridgewater | 110 | 8.3118 | 5.3922 | 0.010831 | 0.068615 | 6.3349 | 0.010895 | 0.06976 | 6.4032 | 0.044958 | 0.17587 | 3.912
Bridgewater | 11 | 14.211 | 6.2085 | 0.016414 | 0.40595 | 24.732 | 0.016477 | 0.40709 | 24.7064 | 0 | 1.9769 | >50
Bridgewater | 11 | 7.7999 | 3.1924 | 0.032931 | 0.73952 | 22.4564 | 0.032995 | 0.74066 | 22.448 | 0 | 3.9471 | >50
Burnie | 220 | 5.2428 | 4.2608 | 0.0083463 | 0.054432 | 6.5216 | 0.008132 | 0.052949 | 6.5112 | 0.013386 | 0.093704 | 7.0002
Burnie | 110 | 7.5179 | 5.2395 | 0.011304 | 0.075965 | 6.7199 | 0.011066 | 0.068812 | 6.2181 | 0.024588 | 0.18249 | 7.4218
Burnie | 22 | 11.3866 | 5.5558 | 0.017654 | 0.25291 | 14.3258 | 0.017416 | 0.24576 | 14.1109 | 0 | 1.0599 | >50
Butlers Gorge | 110 | 4.7167 | 4.2279 | 0.043773 | 0.11433 | 2.6118 | 0.045111 | 0.11748 | 2.6041 | 0.027757 | 0.16098 | 5.7996
Cattle Hill | 220 | 9.8736 | 9.9678 | 0.0029625 | 0.029088 | 9.8187 | 0.0030011 | 0.029801 | 9.9302 | 0.0042346 | 0.027395 | 6.4695
Chapel Street | 220 | 8.6424 | 8.1795 | 0.0036467 | 0.033204 | 9.1052 | 0.0037616 | 0.034846 | 9.2637 | 0.0031621 | 0.037304 | 11.7973
Chapel Street | 110 | 15.0585 | 16.0755 | 0.0040213 | 0.03813 | 9.4819 | 0.0041116 | 0.03938 | 9.5777 | 0.0020507 | 0.029754 | 14.5089
Chapel Street | 11 | 15.6775 | 8.8605 | 0.013371 | 0.36803 | 27.5238 | 0.013462 | 0.36928 | 27.432 | 0 | 1.2174 | >50
Chapel Street | 11 | 8.2625 | 4.5202 | 0.022721 | 0.69843 | 30.739 | 0.022812 | 0.69968 | 30.6721 | 0 | 2.4342 | >50
Comalco | 220 | 12.5203 | 13.0067 | 0.0018847 | 0.02298 | 12.1926 | 0.0019304 | 0.023238 | 12.0385 | 0.0022515 | 0.020089 | 8.9225
Creek Road | 110 | 14.4174 | 14.1976 | 0.0044505 | 0.039798 | 8.9423 | 0.0045319 | 0.041016 | 9.0506 | 0.0056553 | 0.040302 | 7.1265
Creek Road | 33 | 14.0417 | 5.8614 | 0.0068618 | 0.13689 | 19.9491 | 0.0069432 | 0.13811 | 19.8908 | 0 | 0.71003 | >50
Creek Road | 33 | 10.3707 | 4.0527 | 0.0081509 | 0.1854 | 22.7459 | 0.0082322 | 0.18662 | 22.6691 | 0 | 1.0529 | >50
Derby | 110 | 3.8418 | 2.0238 | 0.025962 | 0.14805 | 5.7027 | 0.026637 | 0.15168 | 5.6945 | 0.15743 | 0.53057 | 3.3701
Derby | 22 | 4.2837 | 1.273 | 0.045962 | 0.67245 | 14.6307 | 0.046637 | 0.67608 | 14.4967 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 3.2841 | 2.4902 | 0.072861 | 0.16003 | 2.1964 | 0.073892 | 0.16292 | 2.2048 | 0.083659 | 0.33363 | 3.988
Derwent Bridge | 22 | 4.1717 | 1.8353 | 0.088561 | 0.68643 | 7.7509 | 0.089592 | 0.68932 | 7.694 | 0 | 3.345 | >50
Devonport | 110 | 6.9998 | 4.7093 | 0.010636 | 0.081799 | 7.6905 | 0.011047 | 0.080746 | 7.309 | 0.03175 | 0.2014 | 6.3433
Devonport | 22 | 11.7093 | 5.3426 | 0.016065 | 0.24602 | 15.3138 | 0.016476 | 0.24497 | 14.8679 | 0 | 1.1299 | >50
Electrona | 110 | 6.2054 | 3.8335 | 0.026236 | 0.089272 | 3.4026 | 0.026327 | 0.090522 | 3.4384 | 0.053007 | 0.25962 | 4.8978
Electrona | 11 | 16.6953 | 6.7151 | 0.036414 | 0.3439 | 9.4442 | 0.036504 | 0.34515 | 9.4551 | 0 | 1.8895 | >50
Electrona | 11 | 9.344 | 3.7168 | 0.042136 | 0.61647 | 14.6304 | 0.042227 | 0.61772 | 14.6287 | 0 | 3.4264 | >50
Emu Bay | 110 | 7.0524 | 4.8314 | 0.013588 | 0.080736 | 5.9418 | 0.013422 | 0.074054 | 5.5173 | 0.031146 | 0.19901 | 6.3896
Emu Bay | 22 | 7.3993 | 3.106 | 0.02041 | 0.38963 | 19.0901 | 0.020245 | 0.38295 | 18.9161 | 0 | 2.0166 | >50
Emu Bay | 22 | 4.1452 | 1.6007 | 0.027188 | 0.69604 | 25.6011 | 0.027022 | 0.68935 | 25.5106 | 0 | 4.0331 | >50
Farrell | 220 | 9.4925 | 9.9552 | 0.0023905 | 0.030318 | 12.6827 | 0.002587 | 0.031475 | 12.1663 | 0.0032915 | 0.024808 | 7.537
Farrell | 110 | 8.1634 | 10.0199 | 0.0027401 | 0.070675 | 25.7932 | 0.0029036 | 0.071626 | 24.6682 | 0.0013904 | 0.030424 | 21.881
George Town | 220 | 12.8095 | 13.5955 | 0.0018012 | 0.022464 | 12.4718 | 0.0018468 | 0.022723 | 12.3038 | 0.0016637 | 0.018292 | 10.9943
George Town | 110 | 14.5835 | 15.6021 | 0.0016426 | 0.039556 | 24.0816 | 0.0016935 | 0.040312 | 23.8043 | 0.0014436 | 0.031045 | 21.5055
George Town | 22 | 10.0806 | 5.6431 | 0.0058598 | 0.28632 | 48.8615 | 0.0059106 | 0.28707 | 48.5688 | 0 | 0.96143 | >50
Gordon | 220 | 7.8678 | 8.3719 | 0.0021796 | 0.036628 | 16.8051 | 0.0026393 | 0.041219 | 15.6173 | 0.00063094 | 0.025459 | 40.3511
Gordon | 22 | 2.1002 | 0.09 | 0.07028 | 1.3739 | 19.5495 | 0.070739 | 1.3785 | 19.4873 | 0 | 0 | >50
Hadspen | 220 | 12.5095 | 11.4406 | 0.0022928 | 0.022963 | 10.0151 | 0.0023442 | 0.023351 | 9.9613 | 0.0043298 | 0.028853 | 6.6637
Hadspen | 110 | 14.649 | 14.3884 | 0.0033908 | 0.039267 | 11.5806 | 0.0035113 | 0.040425 | 11.5129 | 0.0036747 | 0.040223 | 10.9458
Hadspen | 22 | 10.0215 | 5.3425 | 0.00766 | 0.28797 | 37.5936 | 0.0077805 | 0.28912 | 37.1601 | 0 | 1.0441 | >50
Hampshire | 110 | 3.3961 | 2.1058 | 0.043694 | 0.16433 | 3.761 | 0.043456 | 0.15718 | 3.617 | 0.10768 | 0.47813 | 4.4403
Huon River | 110 | 2.6272 | 1.6522 | 0.087454 | 0.20168 | 2.3062 | 0.087544 | 0.20293 | 2.3181 | 0.16852 | 0.58684 | 3.4823
Huon River | 11 | 7.9068 | 3.57 | 0.10335 | 0.72288 | 6.9942 | 0.10344 | 0.72413 | 7.0002 | 0 | 3.4017 | >50
Kermandie | 110 | 3.2487 | 1.9706 | 0.066444 | 0.16487 | 2.4814 | 0.066534 | 0.16612 | 2.4968 | 0.13261 | 0.50748 | 3.8268
Kermandie | 11 | 13.2391 | 3.7169 | 0.076345 | 0.42937 | 5.6241 | 0.076435 | 0.43062 | 5.6338 | 0.89773 | 3.681 | 4.1003
Kingston | 110 | 8.4128 | 5.059 | 0.014939 | 0.066985 | 4.4838 | 0.01503 | 0.068236 | 4.5401 | 0.03562 | 0.20085 | 5.6388
Kingston | 33 | 7.2286 | 2.0954 | 0.01919 | 0.26556 | 13.8388 | 0.01928 | 0.26681 | 13.8388 | 0 | 2.2251 | >50
Kingston | 11 | 14.4812 | 6.0359 | 0.025939 | 0.39785 | 15.3378 | 0.02603 | 0.3991 | 15.3326 | 0 | 2.0725 | >50
Kingston | 11 | 7.9516 | 3.0916 | 0.036839 | 0.72519 | 19.685 | 0.03693 | 0.72644 | 19.6708 | 0 | 4.1526 | >50
Knights Rd | 110 | 5.6746 | 3.5248 | 0.027544 | 0.097952 | 3.5562 | 0.027634 | 0.099203 | 3.5899 | 0.058842 | 0.28094 | 4.7745
Knights Rd | 11 | 10.3446 | 3.5682 | 0.033644 | 0.55712 | 16.5595 | 0.033734 | 0.55837 | 16.5522 | 0 | 3.7397 | >50
Liapootah | 220 | 9.7542 | 9.888 | 0.0028739 | 0.029456 | 10.2496 | 0.0029468 | 0.030518 | 10.3563 | 0.0027974 | 0.027187 | 9.7186
Lindisfarne | 220 | 6.1243 | 6.3824 | 0.0045419 | 0.046921 | 10.3307 | 0.0046003 | 0.047821 | 10.3951 | 0.0050441 | 0.040216 | 7.9728
Lindisfarne | 110 | 13.0528 | 11.5349 | 0.0050362 | 0.043945 | 8.7258 | 0.0050995 | 0.04509 | 8.842 | 0.0093775 | 0.059853 | 6.3826
Lindisfarne | 33 | 7.9634 | 2.5061 | 0.0095363 | 0.24149 | 25.3237 | 0.0095996 | 0.24264 | 25.276 | 0 | 1.8211 | >50
Meadowbank | 110 | 8.88 | 7.1753 | 0.013211 | 0.063663 | 4.819 | 0.013174 | 0.06483 | 4.9212 | 0.012758 | 0.10972 | 8.6
Meadowbank | 22 | 5.0082 | 3.9366 | 0.037611 | 0.57526 | 15.2951 | 0.037574 | 0.57643 | 15.3413 | 0 | 1.0475 | >50
Mornington | 110 | 10.6627 | 7.4915 | 0.0070003 | 0.053694 | 7.6702 | 0.0070636 | 0.054839 | 7.7635 | 0.022168 | 0.11983 | 5.4055
Mornington | 33 | 7.8468 | 2.1301 | 0.011225 | 0.24502 | 21.8273 | 0.011289 | 0.24616 | 21.8063 | 0 | 2.2216 | >50
Mowbray | 110 | 11.5778 | 11.2702 | 0.004956 | 0.049621 | 10.0123 | 0.00515 | 0.051038 | 9.9103 | 0.0062588 | 0.052155 | 8.333
Mowbray | 22 | 9.7179 | 4.3413 | 0.0097606 | 0.29691 | 30.4189 | 0.0099546 | 0.29832 | 29.9685 | 0 | 1.3999 | >50
New Norfolk | 110 | 11.9369 | 7.8162 | 0.0082044 | 0.047667 | 5.8099 | 0.0081928 | 0.048739 | 5.949 | 0.021513 | 0.12194 | 5.668
New Norfolk | 22 | 7.8216 | 3.7517 | 0.016704 | 0.36872 | 22.073 | 0.016693 | 0.36979 | 22.1526 | 0 | 1.5703 | >50
Newton | 110 | 4.3557 | 3.5762 | 0.01355 | 0.13188 | 9.7329 | 0.013714 | 0.13283 | 9.6862 | 0.049585 | 0.2136 | 4.3077
Newton | 11 | 7.5471 | 0.21917 | 0.04225 | 0.76388 | 18.08 | 0.042414 | 0.76483 | 18.0327 | 78.7191 | 4.6116 | 0.058583
Newton | 22 | 3.7484 | 1.4651 | 0.04225 | 0.76918 | 18.2054 | 0.042414 | 0.77013 | 18.1577 | 0 | 4.3822 | >50
North Hobart | 110 | 13.5432 | 13.0752 | 0.0064114 | 0.042146 | 6.5737 | 0.0064927 | 0.043364 | 6.6789 | 0.010635 | 0.044852 | 4.2173
North Hobart | 11 | 11.4488 | 6.1166 | 0.009725 | 0.50421 | 51.8469 | 0.0098063 | 0.50543 | 51.5411 | 0 | 1.8223 | >50
Norwood | 110 | 12.083 | 10.7325 | 0.0048588 | 0.047536 | 9.7833 | 0.0050059 | 0.04881 | 9.7506 | 0.0099295 | 0.063825 | 6.4278
Norwood | 22 | 9.1629 | 5.5552 | 0.012078 | 0.31483 | 26.0663 | 0.012225 | 0.31611 | 25.857 | 0 | 0.92802 | >50
Palmerston | 220 | 14.0161 | 14.3415 | 0.0016718 | 0.020528 | 12.2792 | 0.0017024 | 0.020914 | 12.2852 | 0.0020652 | 0.018699 | 9.0546
Palmerston | 110 | 13.7649 | 14.167 | 0.0042844 | 0.041725 | 9.7388 | 0.0043064 | 0.04248 | 9.8644 | 0.00285 | 0.037519 | 13.1646
Palmerston | 22 | 9.5726 | 3.3472 | 0.015359 | 0.30118 | 19.6099 | 0.015381 | 0.30194 | 19.631 | 0 | 1.9849 | >50
Paloona | 110 | 8.9737 | 8.9945 | 0.0082479 | 0.06381 | 7.7365 | 0.0086839 | 0.062278 | 7.1717 | 0.0079598 | 0.064872 | 8.15
Pieman | 220 | 7.511 | 8.478 | 0.0035887 | 0.038268 | 10.6635 | 0.0038499 | 0.039711 | 10.315 | 0.0019033 | 0.023748 | 12.4772
Port Latta | 110 | 3.5386 | 2.3723 | 0.053368 | 0.15422 | 2.8897 | 0.037124 | 0.12131 | 3.2678 | 0.12109 | 0.42362 | 3.4983
Port Latta | 22 | 6.885 | 2.0567 | 0.063267 | 0.41451 | 6.5517 | 0.047023 | 0.38161 | 8.1152 | 0 | 3.4171 | >50
Port Latta | 22 | 4.235 | 1.068 | 0.073368 | 0.67782 | 9.2386 | 0.057124 | 0.64491 | 11.2897 | 0 | 6.8136 | >50
Que | 110 | 4.041 | 3.3092 | 0.02793 | 0.14015 | 5.0177 | 0.028094 | 0.1411 | 5.0224 | 0.06657 | 0.22774 | 3.4211
Que | 22 | 3.8568 | 1.7081 | 0.04623 | 0.74725 | 16.1636 | 0.046394 | 0.7482 | 16.1272 | 0 | 3.5806 | >50
Queenstown | 110 | 3.0037 | 2.3052 | 0.021408 | 0.19109 | 8.9263 | 0.021571 | 0.19204 | 8.9027 | 0.075474 | 0.35932 | 4.7609
Queenstown | 22 | 6.3589 | 2.8975 | 0.030186 | 0.45301 | 15.0072 | 0.030349 | 0.45396 | 14.9577 | 0 | 2.0827 | >50
Queenstown | 11 | 12.8321 | 7.3792 | 0.028703 | 0.44902 | 15.6437 | 0.028866 | 0.44997 | 15.588 | 0 | 1.4477 | >50
Railton | 110 | 8.8022 | 6.5227 | 0.0064749 | 0.065274 | 10.0811 | 0.0068859 | 0.064221 | 9.3265 | 0.031214 | 0.1323 | 4.2384
Railton | 22 | 8.426 | 3.7828 | 0.0136 | 0.34235 | 25.1729 | 0.014011 | 0.3413 | 24.3593 | 0 | 1.6062 | >50
Risdon | 110 | 13.6164 | 12.2889 | 0.0049175 | 0.042116 | 8.5645 | 0.0049862 | 0.043291 | 8.6823 | 0.0089292 | 0.054277 | 6.0786
Risdon | 33 | 11.0582 | 4.5355 | 0.0080563 | 0.17385 | 21.5795 | 0.0081251 | 0.17503 | 21.5417 | 0 | 0.92423 | >50
Risdon | 11 | 20.451 | 3.2408 | 0.009217 | 0.27225 | 29.5379 | 0.0092857 | 0.27343 | 29.4459 | 4.8476 | 1.1622 | 0.23975
Rokeby | 110 | 8.2694 | 5.375 | 0.010071 | 0.069091 | 6.8604 | 0.010134 | 0.070235 | 6.9305 | 0.034118 | 0.17834 | 5.2272
Rokeby | 11 | 14.4942 | 6.0499 | 0.019551 | 0.39786 | 20.3498 | 0.019614 | 0.399 | 20.3424 | 0 | 2.0661 | >50
Rokeby | 11 | 7.8124 | 3.0885 | 0.032037 | 0.73837 | 23.0473 | 0.0321 | 0.73951 | 23.0375 | 0 | 4.1322 | >50
Rosebery | 110 | 7.2978 | 7.5797 | 0.00587 | 0.0789 | 13.4413 | 0.0060335 | 0.079851 | 13.2347 | 0.015282 | 0.068151 | 4.4596
Rosebery | 44 | 5.6872 | 2.8133 | 0.012398 | 0.25352 | 20.4488 | 0.012561 | 0.25447 | 20.2583 | 0.0617 | 1.0295 | 16.6854
Rosebery | 22 | 2.8504 | 2.2805 | 0.073698 | 1.0105 | 13.7117 | 0.073861 | 1.0115 | 13.6942 | 0 | 1.7755 | >50
Savage River | 110 | 1.8467 | 1.2065 | 0.08708 | 0.30053 | 3.4511 | 0.087244 | 0.30148 | 3.4556 | 0.18431 | 0.79105 | 4.292
Savage River | 22 | 5.5521 | 3.0848 | 0.10058 | 0.51018 | 5.0723 | 0.10074 | 0.51113 | 5.0735 | 0 | 1.78 | >50
Scottsdale | 110 | 5.1857 | 3.2857 | 0.022431 | 0.10907 | 4.8623 | 0.022736 | 0.11097 | 4.8807 | 0.079419 | 0.29233 | 3.6809
Scottsdale | 22 | 12.0324 | 6.6312 | 0.028131 | 0.23827 | 8.4699 | 0.028436 | 0.24017 | 8.4459 | 0 | 0.82645 | >50
Sheffield | 220 | 12.9238 | 13.2062 | 0.001778 | 0.022266 | 12.5234 | 0.0018521 | 0.022255 | 12.016 | 0.0027025 | 0.020751 | 7.6787
Sheffield | 110 | 12.1322 | 13.3635 | 0.0028076 | 0.047507 | 16.9205 | 0.0032187 | 0.046454 | 14.4327 | 0.0026517 | 0.035362 | 13.3355
Sheffield | 22 | 5.0941 | 1.2405 | 0.022908 | 0.56631 | 24.7213 | 0.023319 | 0.56525 | 24.2404 | 0 | 5.8676 | >50
Smithton | 110 | 2.9821 | 1.9859 | 0.065896 | 0.1821 | 2.7634 | 0.038651 | 0.1337 | 3.4591 | 0.15513 | 0.51745 | 3.3355
Smithton | 22 | 6.7717 | 7.6978 | 0.072596 | 0.4201 | 5.7868 | 0.045351 | 0.3717 | 8.196 | 0 | 0.3271 | >50
Sorell | 110 | 4.9406 | 3.0473 | 0.029582 | 0.11307 | 3.8222 | 0.029645 | 0.11421 | 3.8526 | 0.065348 | 0.32747 | 5.0113
Sorell | 22 | 8.4582 | 2.8825 | 0.022286 | 0.34058 | 15.2822 | 0.02235 | 0.34173 | 15.2901 | 0 | 2.3232 | >50
St Leonards | 110 | 11.2576 | 10.5246 | 0.0050901 | 0.051034 | 10.0262 | 0.0052558 | 0.052364 | 9.9632 | 0.0087272 | 0.06007 | 6.883
St Leonards | 22 | 9.3118 | 2.5224 | 0.0084901 | 0.30991 | 36.5024 | 0.0086558 | 0.31124 | 35.9573 | 6.2256e-14 | 2.8144 | >50
St Marys | 110 | 1.1225 | 0.71717 | 0.25382 | 0.44823 | 1.7659 | 0.25385 | 0.44899 | 1.7687 | 0.43408 | 1.3383 | 3.0831
St Marys | 22 | 3.0279 | 4.1723 | 0.28685 | 0.90948 | 3.1706 | 0.28687 | 0.91024 | 3.173 | 0 | 0.1754 | >50
Starwood | 110 | 10.1896 | 8.9461 | 0.0096426 | 0.055836 | 5.7906 | 0.0096935 | 0.056592 | 5.8381 | 0.019054 | 0.077345 | 4.0593
Tarraleah | 110 | 10.6577 | 11.902 | 0.0083615 | 0.053524 | 6.4012 | 0.0088192 | 0.055823 | 6.3297 | 0.0017958 | 0.034939 | 19.4566
Temco | 110 | 12.9111 | 11.7257 | 0.0033726 | 0.044591 | 13.2216 | 0.0034235 | 0.045347 | 13.2458 | 0.0080786 | 0.05703 | 7.0594
Trevallyn | 110 | 12.7923 | 12.6817 | 0.0043886 | 0.04492 | 10.2355 | 0.0046038 | 0.046395 | 10.0774 | 0.0033618 | 0.044707 | 13.2986
Trevallyn | 22 | 13.9924 | 5.8436 | 0.007222 | 0.20619 | 28.5499 | 0.0074371 | 0.20766 | 27.9222 | 0 | 1.0683 | >50
Trevallyn | 22 | 10.0605 | 3.9812 | 0.0086387 | 0.28682 | 33.2019 | 0.0088538 | 0.28829 | 32.5616 | 0 | 1.6007 | >50
Triabunna | 110 | 1.6321 | 1.1326 | 0.23948 | 0.26056 | 1.088 | 0.23954 | 0.2617 | 1.0925 | 0.31903 | 0.7847 | 2.4597
Triabunna | 22 | 4.9935 | 2.7764 | 0.24948 | 0.52156 | 2.0906 | 0.24954 | 0.5227 | 2.0946 | 0 | 2.0362 | >50
Tungatinah | 110 | 10.8474 | 12.1951 | 0.0078862 | 0.052639 | 6.6748 | 0.0083478 | 0.054942 | 6.5816 | 0.0013202 | 0.033362 | 25.2711
Tungatinah | 22 | 4.9428 | 1.4397 | 0.028286 | 0.58344 | 20.6262 | 0.028748 | 0.58574 | 20.3752 | 0 | 4.8574 | >50
Ulverstone | 110 | 6.2677 | 4.721 | 0.01933 | 0.090071 | 4.6596 | 0.019611 | 0.086802 | 4.4263 | 0.038434 | 0.18181 | 4.7305
Ulverstone | 22 | 8.8777 | 4.4952 | 0.02688 | 0.32407 | 12.0561 | 0.027161 | 0.3208 | 11.8113 | 0 | 1.2813 | >50
Waddamana | 220 | 10.9376 | 10.9893 | 0.0023956 | 0.026285 | 10.9719 | 0.0024354 | 0.027003 | 11.0877 | 0.0034875 | 0.025081 | 7.1917
Waddamana | 110 | 7.2913 | 5.1176 | 0.016146 | 0.077524 | 4.8015 | 0.01668 | 0.079938 | 4.7925 | 0.030505 | 0.17505 | 5.7385
Waddamana | 22 | 1.8074 | 2.2675 | 0.15415 | 1.5915 | 10.3248 | 0.15468 | 1.5939 | 10.3048 | 0 | 0.624 | >50
Waratah Tee | 110 | 2.5052 | 1.7593 | 0.05779 | 0.22321 | 3.8623 | 0.057954 | 0.22416 | 3.8679 | 0.12569 | 0.50801 | 4.0418
Wesley Vale | 110 | 6.472 | 3.7296 | 0.01362 | 0.088169 | 6.4734 | 0.014031 | 0.087116 | 6.2088 | 0.049957 | 0.2827 | 5.6588
Wesley Vale | 22 | 7.1263 | 2.8888 | 0.028061 | 0.40414 | 14.4021 | 0.028472 | 0.40309 | 14.1572 | 0 | 2.1915 | >50
Notes on above maximum fault levels 1. Results are provided for substations that can operate in different configurations due to the presence of bus couplers, with both open and closed positions considered. The only exception is Boyer 6.6 kV F & G. 2. Boyer 6.6 kV F & G buses, Chapel Street 11 kV, Electrona 11 kV, and Kingston 11 kV buses are kept open due to exceedance of 13 kA fault level. 3. Bridgewater 11 kV and Rokeby 11 kV buses are kept normally open due to protection reasons. 4. Mowbray 22 kV and Trevallyn 22 kV buses are closed but the 22 kV Trevallyn–Mowbray super feeders are normally kept open to keep fault levels below 13 kA. The results above only contain the Trevallyn-Mowbray superfeeders in the open position. 5. At Creek Road and Trevallyn substations the supply transformer incoming circuit breaker is operated open due to exceedance of 13 kA fault level. It is only opened when fault level exceeds 13 kA. These results reflect scenarios where the third supply transformers at Creek Rd and Trevallyn are both in service and out of service. 6. Smithton 22 kV bus coupler operated open due to distribution earthing issue. 8. The Boyer D & E fault level is the full fault level not taking into consideration the operation of the fault current limiter (FCL). The FCL operates at 10 kA, and as such the maximum sustained fault current that can be supplied through the incomer circuits will be 20 kA. The fault contribution from Boyer is expected to be 8.6 kA. As such the maximum sustained bus fault current will be 28.6 kA.

## Minimum
Minimum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU (100 MVA Base)
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 2.2478 | 2.3674 | 0.063734 | 0.20037 | 3.1438 | 0.063689 | 0.20343 | 3.1942 | 0.031475 | 0.17363 | 5.5165
Arthurs Lake | 6.6 | 10.9605 | 0.09 | 0.082534 | 0.71357 | 8.6458 | 0.082489 | 0.71663 | 8.6876 | 1.0899 | 0 | >50
Avoca | 110 | 1.2818 | 0.91327 | 0.15637 | 0.33422 | 2.1373 | 0.15633 | 0.33728 | 2.1575 | 0.22869 | 0.78753 | 3.4437
Avoca | 22 | 2.7333 | 1.2601 | 0.18087 | 0.84532 | 4.6735 | 0.18083 | 0.84838 | 4.6916 | 0 | 3.9308 | >50
Boyer | 110 | 3.5987 | 3.5151 | 0.021401 | 0.12954 | 6.0531 | 0.021639 | 0.12967 | 5.9922 | 0.028623 | 0.13764 | 4.8086
Boyer (A & B) | 6.6 | 8.9929 | 3.102 | 0.04512 | 0.87434 | 19.3782 | 0.045358 | 0.87447 | 19.2791 | 0 | 5.8678 | >50
Boyer (D & E) | 6.6 | 10.2808 | 6.079 | 0.038073 | 0.76487 | 20.0894 | 0.038312 | 0.765 | 19.9677 | 0.0053 | 2.355 | >50
Boyer (F) | 6.6 | 10.5027 | 7.4726 | 0.039777 | 0.74858 | 18.8196 | 0.040015 | 0.74871 | 18.7105 | 0.00076558 | 1.6626 | >50
Boyer (G) | 6.6 | 10.4246 | 7.4457 | 0.039366 | 0.75423 | 19.1594 | 0.039605 | 0.75435 | 19.0472 | 0.0060656 | 1.6626 | >50
Bridgewater | 110 | 2.9826 | 2.6745 | 0.024004 | 0.15661 | 6.5241 | 0.024249 | 0.15671 | 6.4624 | 0.050893 | 0.20744 | 4.076
Bridgewater | 11 | 5.8771 | 2.5534 | 0.040309 | 0.80284 | 19.9169 | 0.040554 | 0.80294 | 19.7992 | 0 | 3.9471 | >50
Burnie | 220 | 0.83914 | 0.97113 | 0.038856 | 0.28014 | 7.2097 | 0.038909 | 0.28373 | 7.2921 | 0.015969 | 0.16239 | 10.1691
Burnie | 110 | 2.3438 | 1.7263 | 0.037756 | 0.19809 | 5.2466 | 0.037809 | 0.20168 | 5.3341 | 0.08347 | 0.40648 | 4.8698
Burnie | 22 | 4.8026 | 2.2831 | 0.029597 | 0.49098 | 16.589 | 0.029651 | 0.49458 | 16.6801 | 0 | 2.1198 | >50
Butlers Gorge | 110 | 2.0102 | 2.2422 | 0.075912 | 0.22255 | 2.9316 | 0.076143 | 0.22275 | 2.9254 | 0.027757 | 0.16098 | 5.7996
Cattle Hill | 220 | 3.1392 | 3.9743 | 0.0077878 | 0.074861 | 9.6126 | 0.0080416 | 0.074939 | 9.3189 | 0.0042346 | 0.027395 | 6.4695
Chapel Street | 220 | 2.0604 | 2.6437 | 0.01461 | 0.11379 | 7.7885 | 0.014856 | 0.1139 | 7.6669 | 0.0031447 | 0.038476 | 12.2355
Chapel Street | 110 | 4.4016 | 5.6351 | 0.012573 | 0.1066 | 8.4786 | 0.012816 | 0.10671 | 8.3262 | 0.0025822 | 0.036646 | 14.1918
Chapel Street | 11 | 6.169 | 3.5751 | 0.031238 | 0.76517 | 24.4947 | 0.031482 | 0.76527 | 24.3085 | 0 | 2.4342 | >50
Comalco | 220 | 2.9617 | 3.8597 | 0.007734 | 0.079404 | 10.2669 | 0.0077445 | 0.082796 | 10.691 | 0.0023457 | 0.020556 | 8.7629
Creek Road | 110 | 4.2654 | 5.3504 | 0.013856 | 0.1099 | 7.9312 | 0.014099 | 0.11001 | 7.8023 | 0.0059016 | 0.042819 | 7.2556
Creek Road | 33 | 6.237 | 2.9636 | 0.016298 | 0.25196 | 15.4594 | 0.016541 | 0.25206 | 15.2382 | 0 | 1.0903 | >50
Derby | 110 | 1.7967 | 1.3125 | 0.049372 | 0.25849 | 5.2357 | 0.049359 | 0.26169 | 5.3017 | 0.15743 | 0.53057 | 3.3701
Derby | 22 | 3.0063 | 1.0103 | 0.069372 | 0.78289 | 11.2855 | 0.069359 | 0.78609 | 11.3336 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 1.6522 | 1.5506 | 0.1033 | 0.26687 | 2.5834 | 0.10353 | 0.26707 | 2.5795 | 0.083659 | 0.33363 | 3.988
Derwent Bridge | 22 | 2.9456 | 1.4377 | 0.119 | 0.79327 | 6.666 | 0.11923 | 0.79347 | 6.6548 | 0 | 3.345 | >50
Devonport | 110 | 2.0815 | 1.8544 | 0.041652 | 0.22325 | 5.3599 | 0.041706 | 0.22684 | 5.4391 | 0.057482 | 0.30172 | 5.249
Devonport | 22 | 6.0388 | 2.9579 | 0.023577 | 0.39045 | 16.5604 | 0.023631 | 0.39404 | 16.6748 | 0 | 1.6116 | >50
Electrona | 110 | 1.7204 | 1.2793 | 0.073938 | 0.26471 | 3.5801 | 0.074182 | 0.26481 | 3.5698 | 0.1367 | 0.54292 | 3.9716
Electrona | 11 | 6.8957 | 2.9574 | 0.050653 | 0.68321 | 13.488 | 0.050897 | 0.68331 | 13.4255 | 0 | 3.4264 | >50
Emu Bay | 110 | 1.6411 | 1.49 | 0.071426 | 0.27915 | 3.9083 | 0.071479 | 0.28274 | 3.9556 | 0.099529 | 0.35907 | 3.6077
Emu Bay | 22 | 3.1173 | 1.2794 | 0.032597 | 0.75728 | 23.2315 | 0.032651 | 0.76087 | 23.3033 | 0 | 4.0331 | >50
Farrell | 220 | 1.6675 | 2.285 | 0.016913 | 0.14081 | 8.3252 | 0.016839 | 0.14163 | 8.4107 | 0.0031583 | 0.025654 | 8.1228
Farrell | 110 | 2.2647 | 3.0296 | 0.014233 | 0.20825 | 14.6309 | 0.014159 | 0.20907 | 14.7657 | 0.0023328 | 0.049626 | 21.2727
George Town | 220 | 2.7996 | 3.7104 | 0.008455 | 0.08398 | 9.9326 | 0.0084824 | 0.087437 | 10.308 | 0.0016322 | 0.018698 | 11.4557
George Town | 110 | 3.915 | 5.0842 | 0.0081332 | 0.12041 | 14.8053 | 0.0081438 | 0.12381 | 15.2027 | 0.0013032 | 0.033998 | 26.0874
George Town | 22 | 3.9044 | 2.1437 | 0.016943 | 0.60485 | 35.6991 | 0.016954 | 0.60824 | 35.8769 | 0 | 2.095 | >50
Gordon | 220 | 1.2154 | 1.7079 | 0.026672 | 0.19294 | 7.2338 | 0.02692 | 0.19304 | 7.1708 | 0.00050127 | 0.025851 | >50
Gordon | 22 | 1.5902 | 0.09 | 0.087852 | 1.4849 | 16.9021 | 0.0881 | 1.485 | 16.8556 | 0 | 0 | >50
Hadspen | 220 | 3.0596 | 3.7414 | 0.0076901 | 0.076842 | 9.9923 | 0.0076771 | 0.080145 | 10.4395 | 0.004593 | 0.031392 | 6.8347
Hadspen | 110 | 4.1799 | 5.0268 | 0.011251 | 0.11247 | 9.997 | 0.011237 | 0.11562 | 10.2886 | 0.004833 | 0.052539 | 10.871
Hadspen | 22 | 3.9672 | 2.1362 | 0.017754 | 0.59523 | 33.5261 | 0.017742 | 0.59842 | 33.7298 | 0 | 2.126 | >50
Hampshire | 110 | 2.0487 | 1.4858 | 0.049087 | 0.22545 | 4.593 | 0.049141 | 0.22905 | 4.661 | 0.10768 | 0.47813 | 4.4403
Huon River | 110 | 1.6586 | 1.2029 | 0.095971 | 0.26842 | 2.7969 | 0.096214 | 0.26852 | 2.7909 | 0.16852 | 0.58684 | 3.4823
Huon River | 11 | 5.9238 | 2.8435 | 0.11187 | 0.78962 | 7.0583 | 0.11211 | 0.78972 | 7.0439 | 0 | 3.4017 | >50
Kermandie | 110 | 1.9418 | 1.4034 | 0.074961 | 0.23161 | 3.0898 | 0.075204 | 0.23171 | 3.0811 | 0.13261 | 0.50748 | 3.8268
Kermandie | 11 | 6.1461 | 1.5558 | 0.094561 | 0.76281 | 8.0669 | 0.094804 | 0.76291 | 8.0473 | 1.7934 | 7.376 | 4.1129
Kingston | 110 | 2.8389 | 2.4564 | 0.034588 | 0.16283 | 4.7076 | 0.034832 | 0.16293 | 4.6777 | 0.046691 | 0.23964 | 5.1326
Kingston | 33 | 2.9584 | 0.86179 | 0.031856 | 0.53152 | 16.6851 | 0.0321 | 0.53163 | 16.5618 | 0 | 4.4475 | >50
Kingston | 11 | 5.9558 | 2.4717 | 0.045356 | 0.79192 | 17.4601 | 0.0456 | 0.79203 | 17.3691 | 0 | 4.1526 | >50
Knights Rd | 110 | 1.8553 | 1.4192 | 0.071948 | 0.24445 | 3.3975 | 0.072192 | 0.24455 | 3.3875 | 0.12713 | 0.4734 | 3.7238
Knights Rd | 11 | 4.3447 | 1.4708 | 0.048361 | 1.0864 | 22.4644 | 0.048604 | 1.0865 | 22.3539 | 0 | 7.4793 | >50
Liapootah | 220 | 2.4739 | 3.2161 | 0.011484 | 0.094835 | 8.258 | 0.011735 | 0.094923 | 8.0886 | 0.0025472 | 0.029125 | 11.4343
Lindisfarne | 220 | 2.0078 | 2.5485 | 0.013107 | 0.11701 | 8.9271 | 0.013355 | 0.1171 | 8.7685 | 0.0047697 | 0.042319 | 8.8724
Lindisfarne | 110 | 4.1164 | 4.7658 | 0.013554 | 0.11397 | 8.4091 | 0.013796 | 0.11408 | 8.2688 | 0.011365 | 0.066815 | 5.8788
Lindisfarne | 33 | 3.1259 | 1.0199 | 0.021414 | 0.50347 | 23.5106 | 0.021659 | 0.50357 | 23.2499 | 0 | 3.6421 | >50
Meadowbank | 110 | 2.553 | 2.9105 | 0.039131 | 0.18093 | 4.6237 | 0.039363 | 0.18108 | 4.6003 | 0.014034 | 0.1162 | 8.2802
Meadowbank | 22 | 3.5611 | 2.9877 | 0.053045 | 0.66131 | 12.4669 | 0.053278 | 0.66146 | 12.4152 | 0 | 1.0475 | >50
Mornington | 110 | 3.6965 | 3.6326 | 0.016348 | 0.12677 | 7.7549 | 0.016592 | 0.12688 | 7.6467 | 0.024168 | 0.13236 | 5.4769
Mornington | 33 | 3.1489 | 0.8721 | 0.022779 | 0.49972 | 21.938 | 0.023023 | 0.49982 | 21.7094 | 0 | 4.4456 | >50
Mowbray | 110 | 3.4782 | 3.2889 | 0.014424 | 0.13508 | 9.3649 | 0.014412 | 0.13827 | 9.5946 | 0.031385 | 0.15343 | 4.8886
Mowbray | 22 | 3.9051 | 1.1901 | 0.021719 | 0.60459 | 27.8364 | 0.021707 | 0.60778 | 27.9996 | 0 | 4.7583 | >50
New Norfolk | 110 | 3.7122 | 3.7279 | 0.020627 | 0.1256 | 6.089 | 0.020867 | 0.12572 | 6.0247 | 0.021667 | 0.12363 | 5.7061
New Norfolk | 22 | 3.0815 | 1.5189 | 0.037252 | 0.76588 | 20.5591 | 0.037491 | 0.76601 | 20.4317 | 0 | 3.1405 | >50
Newton | 110 | 2.1454 | 2.1495 | 0.024294 | 0.219 | 9.0149 | 0.024219 | 0.21983 | 9.0765 | 0.049585 | 0.2136 | 4.3077
Newton | 11 | 5.5408 | 0.17927 | 0.052994 | 0.851 | 16.0587 | 0.052919 | 0.85183 | 16.0967 | 78.7191 | 4.6116 | 0.058583
Newton | 22 | 2.7543 | 1.1656 | 0.052994 | 0.8563 | 16.1587 | 0.052919 | 0.85713 | 16.1969 | 0 | 4.3822 | >50
North Hobart | 110 | 4.3102 | 5.3425 | 0.014818 | 0.10861 | 7.3294 | 0.015061 | 0.10871 | 7.218 | 0.010635 | 0.044852 | 4.2173
North Hobart | 11 | 4.5427 | 3.0408 | 0.023214 | 1.0398 | 44.7932 | 0.023457 | 1.0399 | 44.3328 | 0 | 2.5824 | >50
Norwood | 110 | 4.1429 | 4.7521 | 0.011914 | 0.11342 | 9.5201 | 0.011901 | 0.11661 | 9.7984 | 0.010643 | 0.066223 | 6.2224
Norwood | 22 | 3.3041 | 1.4162 | 0.029306 | 0.71448 | 24.3799 | 0.029294 | 0.71767 | 24.4994 | 0 | 3.5806 | >50
Palmerston | 220 | 3.269 | 4.288 | 0.007318 | 0.071904 | 9.8257 | 0.0075837 | 0.072286 | 9.5317 | 0.0021383 | 0.020206 | 9.4495
Palmerston | 110 | 4.6138 | 5.7634 | 0.010175 | 0.10189 | 10.0142 | 0.010128 | 0.10493 | 10.3607 | 0.0028411 | 0.037997 | 13.3738
Palmerston | 22 | 3.7637 | 1.3482 | 0.029494 | 0.62703 | 21.2598 | 0.029449 | 0.63009 | 21.3958 | 0 | 4.0097 | >50
Paloona | 110 | 1.51 | 1.9134 | 0.077479 | 0.30349 | 3.917 | 0.077532 | 0.30708 | 3.9606 | 0.015955 | 0.11068 | 6.9367
Pieman | 220 | 1.7127 | 2.2978 | 0.016422 | 0.13709 | 8.3476 | 0.016348 | 0.13791 | 8.4358 | 0.0029097 | 0.031503 | 10.8269
Port Latta | 110 | 1.4038 | 1.0321 | 0.12034 | 0.31469 | 2.6151 | 0.12039 | 0.31828 | 2.6437 | 0.2176 | 0.66475 | 3.055
Port Latta | 22 | 3.1307 | 0.85645 | 0.088517 | 0.74949 | 8.4672 | 0.08857 | 0.75308 | 8.5026 | 0 | 6.8136 | >50
Que | 110 | 2.0506 | 2.0315 | 0.038673 | 0.22727 | 5.8766 | 0.038599 | 0.22809 | 5.9092 | 0.06657 | 0.22774 | 3.4211
Que | 22 | 2.8255 | 1.3522 | 0.056973 | 0.83437 | 14.6449 | 0.056899 | 0.83519 | 14.6784 | 0 | 3.5806 | >50
Queenstown | 110 | 0.59712 | 0.09 | 0.048219 | 0.79809 | 16.5513 | 0.048145 | 0.79891 | 16.5939 | 0 | 0 | >50
Queenstown | 22 | 2.9349 | 1.0089 | 0.052151 | 0.80341 | 15.4055 | 0.052077 | 0.80423 | 15.4433 | 0 | 5.4421 | >50
Queenstown | 11 | 5.8827 | 2.8064 | 0.04749 | 0.80168 | 16.8809 | 0.047416 | 0.8025 | 16.9247 | 0 | 3.4471 | >50
Railton | 110 | 3.2369 | 3.1453 | 0.015634 | 0.14514 | 9.2836 | 0.015688 | 0.14873 | 9.4807 | 0.040902 | 0.151 | 3.6918
Railton | 22 | 3.4635 | 1.5499 | 0.02613 | 0.68166 | 26.0877 | 0.026183 | 0.68525 | 26.1714 | 0 | 3.2121 | >50
Risdon | 110 | 4.2276 | 4.9307 | 0.013016 | 0.111 | 8.5274 | 0.013262 | 0.1111 | 8.3774 | 0.010164 | 0.063039 | 6.2025
Risdon | 33 | 5.145 | 2.366 | 0.016887 | 0.30562 | 18.0984 | 0.017131 | 0.30572 | 17.8465 | 0 | 1.3863 | >50
Risdon | 11 | 10.1155 | 2.5359 | 0.019227 | 0.45021 | 23.4158 | 0.019471 | 0.45031 | 23.1275 | 4.8518 | 1.3714 | 0.28265
Rokeby | 110 | 3.5331 | 3.1572 | 0.017515 | 0.13259 | 7.5698 | 0.01776 | 0.13269 | 7.4713 | 0.034118 | 0.17834 | 5.2272
Rokeby | 11 | 5.8858 | 2.4721 | 0.039415 | 0.80169 | 20.3396 | 0.03966 | 0.80179 | 20.2167 | 0 | 4.1322 | >50
Rosebery | 110 | 2.6933 | 3.2801 | 0.019783 | 0.17436 | 8.8133 | 0.019709 | 0.17518 | 8.8882 | 0.01848 | 0.078734 | 4.2604
Rosebery | 44 | 2.7467 | 1.3735 | 0.027663 | 0.42927 | 15.5178 | 0.027589 | 0.43009 | 15.5893 | 0 | 1.725 | >50
Rosebery | 22 | 2.1471 | 1.7846 | 0.084441 | 1.0976 | 12.9989 | 0.084367 | 1.0985 | 13.0201 | 0 | 1.7755 | >50
Savage River | 110 | 1.184 | 0.88213 | 0.097823 | 0.38765 | 3.9627 | 0.097749 | 0.38847 | 3.9741 | 0.18431 | 0.79105 | 4.292
Savage River | 22 | 2.8937 | 1.3705 | 0.12482 | 0.80695 | 6.4647 | 0.12475 | 0.80777 | 6.4751 | 0 | 3.5599 | >50
Scottsdale | 110 | 1.7735 | 1.3155 | 0.057656 | 0.2603 | 4.5147 | 0.057644 | 0.26349 | 4.5711 | 0.15021 | 0.52206 | 3.4756
Scottsdale | 22 | 5.3166 | 2.7892 | 0.045556 | 0.44196 | 9.7015 | 0.045543 | 0.44515 | 9.7742 | 0 | 1.6529 | >50
Sheffield | 220 | 2.3099 | 3.1052 | 0.013426 | 0.10143 | 7.5545 | 0.013352 | 0.10224 | 7.6573 | 0.0028733 | 0.022666 | 7.8884
Sheffield | 110 | 3.5015 | 4.4339 | 0.010716 | 0.13452 | 12.5536 | 0.010769 | 0.13811 | 12.8245 | 0.0039882 | 0.046027 | 11.5407
Sheffield | 22 | 3.7558 | 0.99806 | 0.028362 | 0.62839 | 22.1559 | 0.028416 | 0.63198 | 22.2404 | 0 | 5.8676 | >50
Smithton | 110 | 1.133 | 0.81943 | 0.16598 | 0.38326 | 2.3091 | 0.16603 | 0.38685 | 2.33 | 0.28146 | 0.8535 | 3.0324
Smithton | 22 | 3.1778 | 3.3114 | 0.10096 | 0.73661 | 7.2957 | 0.10102 | 0.7402 | 7.3274 | 0 | 0.6541 | >50
Sorell | 110 | 2.5567 | 2.0152 | 0.040144 | 0.18044 | 4.4947 | 0.040389 | 0.18054 | 4.47 | 0.065348 | 0.32747 | 5.0113
Sorell | 22 | 3.3527 | 1.1896 | 0.046944 | 0.70314 | 14.9781 | 0.047189 | 0.70324 | 14.9026 | 0 | 4.5662 | >50
St Leonards | 110 | 3.5778 | 4.1108 | 0.014469 | 0.13127 | 9.0726 | 0.014457 | 0.13446 | 9.3013 | 0.013926 | 0.076395 | 5.4858
St Leonards | 22 | 3.7518 | 1.0344 | 0.017959 | 0.62945 | 35.0483 | 0.017947 | 0.63264 | 35.2506 | 2.0299e-13 | 5.6136 | >50
St Marys | 110 | 0.83709 | 0.5635 | 0.25903 | 0.50314 | 1.9424 | 0.25899 | 0.5062 | 1.9545 | 0.43408 | 1.3383 | 3.0831
St Marys | 22 | 1.6167 | 2.1675 | 0.32463 | 1.4261 | 4.3931 | 0.32459 | 1.4292 | 4.4031 | 0 | 0.3508 | >50
Starwood | 110 | 3.8269 | 4.3008 | 0.015943 | 0.12243 | 7.6793 | 0.015954 | 0.12582 | 7.8868 | 0.019054 | 0.077345 | 4.0593
Tarraleah | 110 | 2.9296 | 3.9662 | 0.035632 | 0.15732 | 4.4151 | 0.035863 | 0.15752 | 4.3922 | 0.0017958 | 0.034939 | 19.4566
Temco | 110 | 4.046 | 4.6587 | 0.011403 | 0.11622 | 10.1921 | 0.011414 | 0.11961 | 10.4799 | 0.010964 | 0.066525 | 6.0678
Trevallyn | 110 | 4.1213 | 5.0534 | 0.011261 | 0.11409 | 10.131 | 0.011249 | 0.11728 | 10.4261 | 0.0031771 | 0.047921 | 15.0833
Trevallyn | 22 | 6.7948 | 3.0838 | 0.015049 | 0.3473 | 23.0787 | 0.015036 | 0.3505 | 23.3102 | 0 | 1.6007 | >50
Triabunna | 110 | 1.1612 | 0.86246 | 0.24686 | 0.32388 | 1.312 | 0.2471 | 0.32398 | 1.3111 | 0.31903 | 0.7847 | 2.4597
Triabunna | 22 | 2.6638 | 1.2269 | 0.26686 | 0.84588 | 3.1698 | 0.2671 | 0.84598 | 3.1672 | 0 | 4.0723 | >50
Tungatinah | 110 | 2.6911 | 3.6878 | 0.040876 | 0.17078 | 4.178 | 0.041105 | 0.171 | 4.1601 | 0.0013799 | 0.033433 | 24.2292
Tungatinah | 22 | 3.4274 | 1.1403 | 0.055452 | 0.6871 | 12.3909 | 0.055683 | 0.6873 | 12.343 | 0 | 4.8574 | >50
Ulverstone | 110 | 1.8823 | 1.7449 | 0.054299 | 0.24523 | 4.5162 | 0.054352 | 0.24882 | 4.5779 | 0.075563 | 0.29778 | 3.9408
Ulverstone | 22 | 3.7965 | 1.6071 | 0.040416 | 0.62096 | 15.3643 | 0.04047 | 0.62456 | 15.4326 | 0 | 3.1694 | >50
Waddamana | 220 | 2.7382 | 3.5409 | 0.009077 | 0.085818 | 9.4544 | 0.0093195 | 0.085904 | 9.2176 | 0.003351 | 0.02726 | 8.135
Waddamana | 110 | 2.7232 | 2.5691 | 0.034994 | 0.16997 | 4.8572 | 0.03521 | 0.17024 | 4.8349 | 0.035125 | 0.20152 | 5.7372
Waddamana | 22 | 1.407 | 1.7802 | 0.17082 | 1.673 | 9.7941 | 0.17104 | 1.6732 | 9.7829 | 0 | 0.624 | >50
Warratah Tee | 110 | 1.4884 | 1.2245 | 0.068533 | 0.31033 | 4.5281 | 0.068459 | 0.31115 | 4.545 | 0.12569 | 0.50801 | 4.0418
Wesley Vale | 110 | 2.4419 | 1.9425 | 0.029952 | 0.19122 | 6.3842 | 0.030006 | 0.19481 | 6.4925 | 0.060762 | 0.33407 | 5.4981
Wesley Vale | 22 | 2.992 | 1.1912 | 0.048245 | 0.78825 | 16.3387 | 0.048298 | 0.79185 | 16.3949 | 0 | 4.384 | >50
Notes on above minimum fault levels 1. Boyer 6.6 kV, Arthur's Lake — Fault level calculation excludes current contribution from synchronous motors. 2. Boyer 6.6 kV F & G buses, Chapel Street 11 kV, Electrona 11 kV, Kingston 11 kV, Bridgewater 11 kV and Rokeby 11 kV buses are kept open. 3. Mowbray 22 kV and Trevallyn 22 kV buses are closed but the 22 kV Trevallyn–Mowbray super feeders are kept open. 4. At Creek Road and Trevallyn substations the supply transformer incoming circuit breaker is operated open due to exceedance of 13 kA fault level. It is only opened when fault level exceeds 13 kA. These results reflect scenarios where the third supply transformers at Creek Rd and Trevallyn are both in service and out of service. 5. Smithton 22 kV buses are kept open.