## Disclaimer
TasNetworks – Annual Planning Report 2025 – Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2025.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Assumptions + methodology
Tx-Dx connection points | Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Appendix A.3.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix C of this APR.
Distribution line max. demand |  | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Appendix A.3.2 of this APR.
Updated 27 October 2025

## Tx-Dx connection points
|  |  |  | Planning area |  |  |  | Kingston-South
| Transmission-distribution connection point: |  |  | Supplying |  |  |  | Distribution lines
| Huon River |  |  | Voltage |  |  |  | 110/11 kV
|  |  |  | Number of transformers |  |  |  | 1
|  |  |  | Peaking season |  |  |  | Summer
Forecast | Parameter |  | 2023 (Actuals) | 2024 (Actuals) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Firm delivery | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum demand forecast | Maximum demand (MW) | Maximum demand (peak season) (MW) | 0.57438 | 0.6402 | 0.65832 | 0.6563 | 0.64524 | 0.6374 | 0.63783 | 0.63659 | 0.65109 | 0.69032 | 0.7251 | 0.74385
| Reactive power (coincident) (MVAr) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.77374 | 0.86241 | 0.88683 | 0.8841 | 0.86921 | 0.85864 | 0.85922 | 0.85756 | 0.87709 | 0.92993 | 0.97679 | 1.002
(Summer peak) | Maximum demand (MVA) | Maximum demand (peak season) (MVA) | 0.96363 | 1.0741 | 1.1045 | 1.1011 | 1.0825 | 1.0694 | 1.0701 | 1.068 | 1.0923 | 1.1582 | 1.2165 | 1.248
| Power factor (coincident) | Maximum demand (peak season) Power factor (coincident) | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605
|  | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Maximum demand forecast | Maximum demand (MW) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.057749 | 0.47673 | 0.49022 | 0.48871 | 0.48048 | 0.47464 | 0.47496 | 0.47404 | 0.48484 | 0.51405 | 0.53995 | 0.55391
(Winter) | Reactive power (coincident) (MVAr) | Maximum demand (non-peak season) (MVA) | 0.069797 | 0.57618 | 0.59249 | 0.59067 | 0.58072 | 0.57366 | 0.57405 | 0.57294 | 0.58598 | 0.62129 | 0.6526 | 0.66947
Hours exceeding | 95% of maximum demand | Hours exceeding 95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Regional diversity factor | Summer | Regional Diversity Factor (Summer) | 0.90316
| Winter | Regional Diversity Factor (Winter) | 0.83073
Load transfer capacity (MVA) |  | Load transfer capacity (MVA)1
Load transfer capacity (MVA)2
Load transfer capacity (MVA)3
Load transfer capacity (MVA)4
Load transfer capacity (MVA)5
Embedded generation capacity | Units less than 100 kVA | Embedded generation capacity (MVA) Units less than 100 kVA | 0.012
| Units greater than 100 kVA | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
| DER generation contribution (MW) | Embedded generation forecast capacity (MVA) | 0 | 0 | 0 | 0.00053448 | 0.0013896 | 0.0034741 | 0.005612 | 0.0075896 | 0.0093533 | 0.010903 | 0.0124 | 0.013843
Notes
[13 empty] | 2033 | 2034
[13 empty] | 0 | 0
[13 empty] | 0 | 0
[13 empty] | 1.2165 | 1.248
xxc

## Zone subs & sub-trans lines
|  |  |  | Planning area |  |  |  | Kingston-South
| Zone substation: |  |  | Supplying |  |  |  | Distribution lines
| Zs-Summerleas |  |  | Voltage |  |  |  | 33/11 kV
|  |  |  | Number of transformers |  |  |  | 1
|  |  |  | Peaking season |  |  |  | Winter
|  |  |  | Subtransmission lines |  |  |  | 32374,32377,32379
|  |  |  | Source Substation |  |  |  | Kingston 33kV
Forecast | Parameter |  | 2023 (Actuals) | 2024 (Actuals) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Firm delivery | Substation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Short-term firm delivery | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sub-transmission line capacity (MVA) | Total (winter) | Sub-transmission lines capacityTotal (winter) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
| Firm delivery (winter) | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total (summer) | Sub-transmission lines capacityTotal (summer) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
| Firm delivery (summer) | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub-transmission line capacity (MVA) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(peak season)Maximum demand (MVA) | 12.274 | 10.7118 | 10.3423 | 10.4252 | 10.2553 | 10.2488 | 10.2639 | 10.3098 | 10.4463 | 10.8776 | 11.2299 | 11.4641
(Winter) | Power factor (coincident) | Maximum demand forecast(peak season)Power factor (coincident) | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 12.2802 | 10.7172 | 10.3475 | 10.4305 | 10.2605 | 10.2539 | 10.2691 | 10.315 | 10.4516 | 10.8831 | 11.2355 | 11.4699
(Summer) | Power factor (coincident) | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Hours exceeding | 95% of maximum demand | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Load transfer capacity (MVA) | Kingston | Load transfer capacity (MVA)1 | 4.9
Load transfer capacity (MVA)2
Load transfer capacity (MVA)3
Load transfer capacity (MVA)4
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA)Units less than 100 kVA | 7.197
| Units greater than 100 kVA | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
DER Capacity (MW) | Embedded Generation |  | 1.8562 | 2.119 | 2.4327 | 2.6908 | 2.8564 | 3.2632 | 3.682 | 4.0679 | 4.4076 | 4.6991 | 4.9708 | 5.221
Notes

## Distribution feeder max. demand
|  |  | Summer | [11 empty] | Winter | [11 empty] | Feeder DER forecast | [11 empty] | Embedded Generation (MVA)
Substation |  | Feeder | 2023 (Actual) | 2024 (Actual) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2023 (Actual) | 2024 (Actual) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Substation | <100kVA | >100kVA
Arthurs Lake (DL) |  | 49101 | 35 | 39.9716 | 41.1032 | 40.9768 | 40.2866 | 39.7969 | 39.8235 | 39.7465 | 40.6517 | 43.1009 | 45.2728 | 46.4432 | 35 | 32.6333 | 31.5077 | 31.7602 | 31.2426 | 31.2228 | 31.2688 | 31.4086 | 31.8246 | 33.1386 | 34.2116 | 34.9253 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752 | Arthurs Lake (DL) | 0.012 | 0
Avoca |  | 56001 | 10.0837 | 8.5067 | 8.7475 | 8.7206 | 8.5737 | 147.473 | 147.5716 | 147.2861 | 150.6404 | 159.7165 | 167.7645 | 172.1018 | 8 | 0.44444 | 0.42911 | 0.43255 | 0.4255 | 0.42523 | 0.42586 | 0.42776 | 0.43343 | 0.45133 | 0.46594 | 0.47566 | 8.6 | 8.6 | 8.6 | 11.7142 | 16.6279 | 28.4426 | 40.4017 | 51.326 | 60.9545 | 69.3228 | 77.3194 | 84.9573 | Avoca | 3.267 | 0
Avoca |  | 56002 | 0 | 0 | 0 | 0 | 0 | 139.0036 | 139.0965 | 138.8274 | 141.989 | 150.5439 | 158.1296 | 162.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.8666 | 4.3972 | 9.025 | 21.9627 | 37.1594 | 53.1527 | 69.1683 | 84.637 | 100.581 | 112.5889 | Bridgewater | 21.781 | 0.012
Avoca |  | 56003 | 54.065 | 42.1291 | 43.3217 | 43.1885 | 42.4611 | 180.9485 | 181.0694 | 180.7191 | 184.8349 | 195.9712 | 205.846 | 211.1678 | 55.1 | 44.3485 | 42.8187 | 43.162 | 42.4585 | 42.4316 | 42.4941 | 42.6841 | 43.2494 | 45.0352 | 46.4934 | 47.4632 | 60.6007 | 64.1868 | 66.4644 | 87.6891 | 111.8686 | 170.1053 | 228.8581 | 282.0503 | 328.299 | 367.8568 | 405.1008 | 440.3642 | Burnie | 32.961 | 0.003
Avoca |  | 56004 | 225.7164 | 184.2983 | 189.5155 | 188.933 | 185.7506 | 183.4928 | 183.6154 | 183.2602 | 187.4338 | 198.7267 | 208.7403 | 214.137 | 135 | 130.0992 | 125.6114 | 126.6184 | 124.5547 | 124.4756 | 124.6592 | 125.2164 | 126.875 | 132.1135 | 136.3913 | 139.2364 | 217.2836 | 233.1907 | 258.0153 | 325.8749 | 428.5504 | 686.3504 | 958.2859 | 1216.4902 | 1452.6481 | 1665.6054 | 1876.9879 | 2087.1187 | Chapel Street | 20.875 | 0
Bridgewater |  | 48180 | 124.3 | 117.2939 | 120.6142 | 120.2435 | 118.2182 | 116.7812 | 116.8592 | 116.6332 | 119.2894 | 126.4766 | 132.8496 | 136.2842 | 208.2274 | 206.533 | 199.4087 | 201.0073 | 197.7312 | 197.6056 | 197.8971 | 198.7816 | 201.4146 | 209.7308 | 216.5219 | 221.0384 | 660.4669 | 747.5639 | 847.6685 | 903.4352 | 962.5945 | 1105.8939 | 1251.5968 | 1385.0979 | 1503.3169 | 1607.1916 | 1708.7088 | 1809.6217 | Creek Road | 0 | 0
Bridgewater |  | 48181 | 163.6949 | 99.7293 | 102.5525 | 102.2373 | 100.5152 | 99.2934 | 99.3598 | 99.1676 | 101.426 | 107.537 | 112.9556 | 115.8759 | 184.4887 | 149.5241 | 144.3663 | 145.5236 | 143.1518 | 143.0609 | 143.2719 | 143.9123 | 145.8185 | 151.8391 | 156.7557 | 160.0256 | 0 | 0 | 0 | 5.884 | 15.7816 | 41.3761 | 69.3631 | 96.9498 | 123.0133 | 147.0251 | 171.0089 | 194.5868 | Derby | 2.841 | 0.012
Bridgewater |  | 48182 | 202.5772 | 153.6159 | 157.9645 | 157.479 | 154.8264 | 152.9444 | 153.0467 | 152.7506 | 156.2294 | 165.6422 | 173.9887 | 178.4869 | 288.3237 | 259.0954 | 250.158 | 252.1634 | 248.0535 | 247.896 | 248.2617 | 249.3713 | 252.6743 | 263.107 | 271.6264 | 277.2924 | 331.5008 | 381.5806 | 437.1033 | 468.4699 | 500.7511 | 578.0154 | 655.7406 | 726.3027 | 789.4496 | 845.8678 | 902.0635 | 958.7247 | Derwent Bridge | 0.055 | 0
Bridgewater |  | 48183 | 185.9309 | 141.071 | 145.0644 | 144.6186 | 142.1826 | 140.4544 | 140.5483 | 140.2763 | 143.471 | 152.1152 | 159.7801 | 163.9109 | 210.2484 | 169.8464 | 163.9876 | 165.3022 | 162.608 | 162.5048 | 162.7445 | 163.4719 | 165.6371 | 172.4761 | 178.0609 | 181.7752 | 234.026 | 259.0423 | 285.6377 | 324.8051 | 377.0488 | 506.4273 | 641.1517 | 767.1954 | 880.2958 | 979.6949 | 1075.0379 | 1165.743 | Devonport | 24.972 | 0.013
Bridgewater |  | 48184 | 145.7 | 146.7094 | 150.8625 | 150.3988 | 147.8655 | 146.0681 | 146.1658 | 145.883 | 149.2054 | 158.195 | 166.1663 | 170.4622 | 237.8522 | 227.6337 | 219.7815 | 221.5435 | 217.9326 | 217.7943 | 218.1155 | 219.0904 | 221.9923 | 231.1582 | 238.6431 | 243.6211 | 201.0393 | 224.8634 | 246.5488 | 292.1757 | 362.95 | 540.8383 | 728.6096 | 906.7501 | 1068.9497 | 1213.6493 | 1354.5103 | 1490.5038 | Electrona | 20.258 | 0
Bridgewater |  | 48185 | 148.3 | 126.6714 | 130.2573 | 129.8569 | 127.6696 | 126.1178 | 126.2021 | 125.9579 | 128.8265 | 136.5883 | 143.4709 | 147.1801 | 202.3419 | 199.0112 | 192.1464 | 193.6868 | 190.53 | 190.409 | 190.6898 | 191.5421 | 194.0792 | 202.0925 | 208.6363 | 212.9884 | 244.0292 | 251.9176 | 278.5244 | 299.03 | 324.6697 | 391.0937 | 464.647 | 538.8557 | 611.1812 | 680.1165 | 751.1359 | 819.4664 | Emu Bay (RT) | 0 | 0
Bridgewater |  | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | George Town | 18.704 | 0.012
Bridgewater |  | 48188 | 72.9 | 116.4254 | 119.7212 | 119.3533 | 117.3429 | 115.9166 | 115.994 | 115.7696 | 118.4062 | 125.5402 | 131.866 | 135.2752 | 114.2934 | 109.2999 | 105.5297 | 106.3757 | 104.6419 | 104.5755 | 104.7297 | 105.1978 | 106.5912 | 110.9922 | 114.5862 | 116.9764 | 0 | 0 | 0 | 0.99282 | 2.5383 | 6.2037 | 9.864 | 13.1636 | 16.0348 | 18.4998 | 20.8278 | 23.0269 | Hadspen | 32.642 | 0.043
Bridgewater |  | 48189 | 64.7 | 64.5506 | 66.3779 | 152.0487 | 149.4876 | 147.6705 | 147.7693 | 147.4834 | 150.8422 | 159.9304 | 167.9892 | 172.3322 | 110.5112 | 113.965 | 110.0338 | 110.9159 | 109.1082 | 109.0389 | 109.1997 | 109.6878 | 111.1407 | 115.7295 | 119.4769 | 121.9691 | 174.3028 | 198.9489 | 254.9992 | 280.4968 | 310.5765 | 383.7308 | 458.0147 | 525.4487 | 583.9413 | 633.4964 | 679.2279 | 721.0647 | Huon River | 0.012 | 0
Bridgewater |  | 48190 | 184.3 | 169.3194 | 174.1125 | 259.4522 | 255.082 | 251.9814 | 252.1499 | 251.6621 | 257.3935 | 272.9014 | 286.6526 | 294.0636 | 204.3616 | 183.1977 | 176.8783 | 178.2963 | 175.3904 | 175.279 | 175.5375 | 176.3221 | 178.6576 | 186.0342 | 192.058 | 196.0642 | 464.4354 | 506.4946 | 558.6045 | 630.4422 | 719.7431 | 939.5299 | 1168.0468 | 1383.1976 | 1579.3522 | 1756.0055 | 1931.8234 | 2103.3264 | Kermandie | 8.18 | 0
Bridgewater |  | 48191 | 53.4 | 47.8837 | 49.2392 | 134.9627 | 132.6894 | 131.0765 | 131.1642 | 130.9104 | 133.8918 | 141.9588 | 149.1119 | 152.967 | 74.3083 | 68.5655 | 66.2003 | 66.7311 | 65.6434 | 65.6018 | 65.6985 | 65.9922 | 66.8663 | 69.6271 | 71.8816 | 73.3811 | 43.2908 | 49.4918 | 49.4918 | 76.9777 | 105.2535 | 176.2571 | 250.8717 | 321.001 | 383.8956 | 438.8281 | 490.8853 | 539.5768 | Kingston 11kV | 22.799 | 0.005
Bridgewater |  | 48192 | 140.8 | 141.1749 | 145.1713 | 230.6 | 226.7157 | 223.96 | 224.1097 | 223.6761 | 228.7701 | 242.5535 | 254.7756 | 261.3624 | 241.7905 | 225.0046 | 217.2431 | 218.9847 | 215.4156 | 215.2788 | 215.5963 | 216.5599 | 219.4284 | 228.4883 | 235.8868 | 240.8073 | 1085.804 | 1241.522 | 1381.3855 | 1496.9536 | 1571.1659 | 1750.2166 | 1930.9832 | 2095.5767 | 2239.6558 | 2363.7132 | 2480.9133 | 2591.3317 | Kingston 33kV | 0 | 0
Bridgewater |  | 48193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.5899 | 433.7158 | 507.872 | 547.4143 | 609.7618 | 758.5757 | 906.9783 | 1039.4505 | 1152.6227 | 1247.2114 | 1333.4592 | 1411.5212 | Knights Road | 16.562 | 0.024
Burnie |  | 91001 | 163.4182 | 145.0754 | 149.1822 | 148.7237 | 146.2186 | 144.4413 | 144.5378 | 144.2582 | 147.5435 | 156.433 | 164.3155 | 168.5637 | 150 | 162.2796 | 156.6818 | 157.9379 | 155.3637 | 155.2651 | 155.4941 | 156.1891 | 158.2579 | 164.7922 | 170.1282 | 173.677 | 173.5106 | 187.7696 | 211.5764 | 243.9034 | 286.8892 | 391.9037 | 500.1816 | 601.119 | 691.9964 | 772.6548 | 851.2056 | 925.136 | Lindisfarne | 0 | 0
Burnie |  | 91002 | 79 | 78.15 | 80.3623 | 80.1153 | 78.7658 | 77.8084 | 77.8604 | 77.7098 | 79.4796 | 84.2682 | 88.5144 | 90.8028 | 81.0636 | 57.0314 | 55.0641 | 55.5056 | 54.6009 | 54.5662 | 54.6467 | 54.891 | 55.618 | 57.9144 | 59.7897 | 61.0369 | 112.13 | 121.766 | 124.5908 | 151.3286 | 191.6097 | 292.0459 | 397.9253 | 499.0121 | 592.386 | 677.553 | 762.8945 | 848.0334 | Meadowbank | 1.743 | 0.012
Burnie |  | 91003 | 154.5534 | 158.7124 | 163.2053 | 162.7037 | 159.9631 | 158.0187 | 158.1243 | 157.8184 | 161.4126 | 171.1377 | 179.7612 | 184.4086 | 235.0999 | 211.4367 | 204.1433 | 205.7798 | 202.4259 | 202.2974 | 202.5958 | 203.5013 | 206.1967 | 214.7104 | 221.6628 | 226.2866 | 270.3893 | 350.4648 | 412.7949 | 453.7536 | 512.5792 | 658.4237 | 811.4178 | 957.1756 | 1092.0951 | 1215.9708 | 1341.373 | 1468.1429 | Mornington | 0 | 0
Burnie |  | 91004 | 152.6667 | 166.2 | 170.9048 | 170.3795 | 167.5097 | 165.4736 | 165.5842 | 165.2638 | 169.0276 | 179.2115 | 188.2418 | 193.1084 | 162 | 159.8944 | 154.3789 | 155.6165 | 153.0802 | 152.983 | 153.2087 | 153.8934 | 155.9318 | 162.3701 | 167.6277 | 171.1243 | 271.3375 | 279.219 | 302.8929 | 333.1866 | 372.0808 | 467.3226 | 566.0821 | 659.2428 | 744.9622 | 823.8039 | 904.754 | 987.2062 | Mowbray | 12.604 | 0.012
Burnie |  | 91005 | 98.1754 | 50.6611 | 52.0952 | 51.9351 | 51.0603 | 50.4397 | 50.4734 | 50.3757 | 51.523 | 54.6273 | 57.3799 | 58.8633 | 108.5406 | 151.5625 | 146.3343 | 147.5075 | 145.1033 | 145.0112 | 145.2251 | 145.8742 | 147.8063 | 153.9091 | 158.8927 | 162.2071 | 559.8906 | 659.1229 | 736.9646 | 808.7196 | 882.4541 | 1058.8673 | 1236.5609 | 1398.1654 | 1539.9981 | 1662.5536 | 1778.4385 | 1885.293 | New Norfolk | 5.83 | 0.012
Burnie |  | 91006 | 166.911 | 150.6125 | 154.8761 | 154.4 | 151.7993 | 149.9542 | 150.0544 | 149.7641 | 153.1749 | 162.4036 | 170.587 | 174.9972 | 249.9722 | 248.0385 | 239.4825 | 241.4023 | 237.4678 | 237.3171 | 237.6671 | 238.7294 | 241.8914 | 251.8789 | 260.0348 | 265.459 | 664.9257 | 769.9682 | 836.7409 | 967.3153 | 1087.5055 | 1376.636 | 1668.5406 | 1933.8902 | 2166.4857 | 2367.838 | 2560.1703 | 2744.8695 | Newton | 0 | 0
Burnie |  | 91007 | 57.8539 | 87.8869 | 90.3748 | 90.097 | 88.5794 | 87.5027 | 87.5612 | 87.3918 | 89.3821 | 94.7674 | 99.5426 | 102.1161 | 109.2243 | 219.5818 | 212.0074 | 213.707 | 210.2239 | 210.0904 | 210.4003 | 211.3407 | 214.14 | 222.9816 | 230.2018 | 235.0037 | 748.9674 | 871.9782 | 1018.0627 | 1163.9173 | 1304.9536 | 1653.8602 | 2016.9242 | 2356.6455 | 2661.4096 | 2928.611 | 3183.3204 | 3423.1054 | North Hobart | 14.614 | 0.06
Burnie |  | 91008 | 130.6683 | 70.5944 | 72.5928 | 72.3697 | 71.1507 | 70.2859 | 70.3329 | 70.1968 | 71.7955 | 76.1211 | 79.9568 | 82.024 | 245.7037 | 238.9476 | 230.7051 | 232.5546 | 228.7643 | 228.6191 | 228.9563 | 229.9796 | 233.0258 | 242.6472 | 250.5041 | 255.7296 | 669.3927 | 810.1297 | 936.3237 | 1047.7339 | 1163.8933 | 1445.197 | 1730.6166 | 1990.6002 | 2218.0414 | 2413.6637 | 2598.5694 | 2773.8732 | Norwood | 17.898 | 0.035
Burnie |  | 91009 | 96.3747 | 115.8833 | 119.1638 | 118.7975 | 116.7965 | 115.3768 | 115.4539 | 115.2306 | 117.8549 | 124.9556 | 131.252 | 134.6453 | 183.3222 | 178.0739 | 171.9313 | 173.3096 | 170.4849 | 170.3767 | 170.6279 | 171.3906 | 173.6607 | 180.831 | 186.6863 | 190.5805 | 674.1934 | 788.7008 | 926.9005 | 1040.1925 | 1161.8077 | 1457.1231 | 1758.9725 | 2037.7036 | 2286.8434 | 2507.6861 | 2724.5092 | 2938.999 | Palmerston | 2.801 | 0.024
Burnie |  | 91010 | 126.753 | 78.9202 | 81.1543 | 80.9049 | 79.5421 | 78.5753 | 78.6278 | 78.4757 | 80.2629 | 85.0988 | 89.3868 | 91.6977 | 217.3396 | 219.1958 | 211.6347 | 213.3313 | 209.8544 | 209.7211 | 210.0304 | 210.9692 | 213.7636 | 222.5896 | 229.7971 | 234.5906 | 422.9673 | 480.8486 | 550.9575 | 624.5841 | 666.9142 | 769.1208 | 872.8447 | 967.8251 | 1051.9278 | 1125.722 | 1197.4192 | 1267.6616 | Port Latta (RT) | 0 | 0
Burnie |  | 91011 | 96 | 189.4598 | 194.8231 | 194.2243 | 190.9528 | 188.6317 | 188.7578 | 188.3926 | 192.6831 | 204.2922 | 214.5863 | 220.1341 | 81 | 107.9083 | 104.186 | 105.0212 | 103.3095 | 103.2439 | 103.3962 | 103.8584 | 105.234 | 109.579 | 113.1272 | 115.487 | 381.8218 | 455.329 | 518.9976 | 569.5743 | 638.2226 | 805.6658 | 977.6394 | 1137.1017 | 1279.8603 | 1405.8859 | 1527.9483 | 1643.0381 | Queenstown | 2.329 | 0
Burnie |  | 91012 | 97.6667 | 82.1444 | 84.4698 | 84.2102 | 82.7918 | 81.7854 | 81.8401 | 81.6817 | 83.542 | 88.5754 | 93.0386 | 95.444 | 69.0022 | 74.7028 | 72.1259 | 72.7042 | 71.5192 | 71.4738 | 71.5792 | 71.8991 | 72.8515 | 75.8594 | 78.3158 | 79.9494 | 147.1906 | 147.1906 | 155.8426 | 203.6749 | 261.1367 | 402.9261 | 550.5325 | 689.1565 | 814.5524 | 926.1195 | 1034.99 | 1138.5939 | Railton | 21.624 | 0.042
Chapel Street |  | 20534 | 37.9309 | 30.0084 | 30.8579 | 30.7631 | 30.2449 | 29.8773 | 29.8972 | 29.8394 | 30.519 | 32.3577 | 33.9882 | 34.8669 | 67.9438 | 59.0865 | 57.0483 | 57.5057 | 56.5684 | 56.5325 | 56.6159 | 56.8689 | 57.6222 | 60.0014 | 61.9442 | 63.2363 | 56.544 | 66.805 | 80.6605 | 95.587 | 112.7661 | 154.2047 | 196.108 | 234.2336 | 267.7037 | 296.8239 | 325.0241 | 352.9433 | Risdon 33kV | 0 | 0
Chapel Street |  | 20535 | 85.5568 | 69.3381 | 71.301 | 71.0818 | 69.8845 | 69.0351 | 69.0812 | 68.9476 | 70.5178 | 74.7665 | 78.5339 | 80.5643 | 314.4447 | 157.4343 | 152.0036 | 153.2222 | 150.7249 | 150.6292 | 150.8514 | 151.5256 | 153.5326 | 159.8718 | 165.0485 | 168.4913 | 282.2252 | 330.2581 | 371.8596 | 434.1297 | 490.6644 | 626.3771 | 762.5615 | 884.935 | 990.1905 | 1078.7473 | 1159.9938 | 1233.9343 | Rokeby | 20.966 | 0.012
Chapel Street |  | 20536 | 89.5253 | 71.9158 | 73.9516 | 73.7243 | 72.4825 | 71.6015 | 71.6494 | 71.5107 | 73.1393 | 77.546 | 81.4535 | 83.5593 | 165.8201 | 151.9914 | 146.7485 | 147.925 | 145.514 | 145.4216 | 145.6361 | 146.287 | 148.2247 | 154.3447 | 159.3424 | 162.6663 | 320.6956 | 375.9192 | 443.64 | 494.0698 | 546.6423 | 673.1191 | 800.3144 | 914.8553 | 1013.5756 | 1096.794 | 1173.2803 | 1243.0056 | Rosebery 22kV | 1.195 | 0.012
Chapel Street |  | 20537 | 72.8609 | 56.6174 | 58.2202 | 58.0412 | 57.0636 | 56.37 | 56.4077 | 56.2985 | 57.5807 | 61.0499 | 64.1262 | 65.784 | 126.8334 | 124.655 | 120.3551 | 121.3199 | 119.3426 | 119.2668 | 119.4427 | 119.9766 | 121.5657 | 126.585 | 130.6839 | 133.4099 | 221.3492 | 248.6398 | 291.6668 | 330.7103 | 372.3801 | 472.8851 | 574.231 | 665.7481 | 744.8531 | 811.7388 | 873.4109 | 929.8228 | Rosebery 44kV | 0 | 0
Chapel Street |  | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Savage River DL | 0 | 0
Chapel Street |  | 20539 | 26.2926 | 22.7017 | 23.3443 | 23.2726 | 22.8806 | 22.6024 | 22.6175 | 22.5738 | 23.0879 | 24.4789 | 25.7124 | 26.3772 | 39.1628 | 34.0141 | 32.8408 | 33.104 | 32.5645 | 32.5438 | 32.5918 | 32.7375 | 33.1711 | 34.5407 | 35.6592 | 36.403 | 41.9247 | 48.6327 | 50.0916 | 57.5951 | 69.9395 | 100.3778 | 131.3692 | 159.2867 | 183.1127 | 202.8547 | 220.6152 | 236.4372 | Scottsdale | 9.851 | 0.012
Chapel Street |  | 20540 | 115.3074 | 114.4294 | 117.6687 | 117.3071 | 115.3312 | 113.9293 | 114.0054 | 113.7849 | 116.3762 | 123.3879 | 129.6053 | 132.956 | 119.7486 | 125.5257 | 121.1957 | 122.1673 | 120.1761 | 120.0998 | 120.277 | 120.8146 | 122.4148 | 127.4692 | 131.5967 | 134.3417 | 7.05 | 7.05 | 7.05 | 12.5131 | 20.9057 | 40.4668 | 59.6238 | 76.5594 | 91.0235 | 103.2109 | 114.4831 | 124.8608 | Sheffield | 0 | 0
Chapel Street |  | 20541 | 142.5702 | 129.8861 | 133.563 | 133.1524 | 130.9096 | 129.3184 | 129.4048 | 129.1545 | 132.0959 | 140.0546 | 147.1119 | 150.9152 | 239.9805 | 227.1048 | 219.2709 | 221.0287 | 217.4263 | 217.2882 | 217.6087 | 218.5813 | 221.4765 | 230.6211 | 238.0886 | 243.055 | 465.8514 | 490.1162 | 549.3372 | 600.67 | 637.9651 | 727.8248 | 818.981 | 902.7048 | 977.4676 | 1044.1097 | 1110.4598 | 1177.6758 | Smithton | 6.168 | 0.024
Chapel Street |  | 20544 | 103.6098 | 77.8168 | 80.0197 | 79.7737 | 78.43 | 77.4767 | 77.5285 | 77.3785 | 79.1407 | 83.909 | 88.137 | 90.4157 | 144.9676 | 138.1782 | 133.4118 | 134.4813 | 132.2895 | 132.2055 | 132.4005 | 132.9923 | 134.7538 | 140.3177 | 144.8612 | 147.8829 | 229.0522 | 275.0173 | 305.6281 | 338.396 | 381.8963 | 486.2887 | 590.9318 | 684.7837 | 765.2968 | 832.8305 | 894.5963 | 950.6435 | Sorell | 32.257 | 0.022
Chapel Street |  | 20545 | 33.5161 | 27.6167 | 28.3984 | 28.3112 | 27.8343 | 27.496 | 27.5143 | 27.4611 | 28.0865 | 29.7787 | 31.2792 | 32.0879 | 64.0616 | 54.8358 | 52.9442 | 53.3687 | 52.4988 | 52.4655 | 52.5429 | 52.7777 | 53.4768 | 55.6848 | 57.4879 | 58.6871 | 69.8978 | 95.2289 | 102.6556 | 116.8601 | 139.4224 | 193.6959 | 248.2641 | 297.3904 | 339.7232 | 375.4073 | 408.2098 | 438.1235 | St Leonards | 15.206 | 0.012
Chapel Street |  | 20547 | 170.0343 | 137.9889 | 141.8951 | 141.459 | 139.0763 | 137.3858 | 137.4776 | 137.2116 | 140.3365 | 148.7918 | 156.2892 | 160.3298 | 151.527 | 303.6461 | 293.1719 | 295.5222 | 290.7056 | 290.5211 | 290.9496 | 292.25 | 296.121 | 308.3475 | 318.3318 | 324.9721 | 682.963 | 814.6864 | 934.7226 | 1025.3999 | 1128.8809 | 1379.3452 | 1633.3054 | 1864.4923 | 2066.5165 | 2239.6914 | 2401.9372 | 2552.9315 | St Marys | 15.463 | 0
Chapel Street |  | 20548 | 108.656 | 88.1341 | 90.629 | 90.3504 | 88.8286 | 87.7488 | 87.8075 | 87.6376 | 89.6335 | 95.0339 | 99.8226 | 102.4033 | 320.3896 | 156.2793 | 170.4847 | 171.8515 | 169.0505 | 168.9432 | 169.1924 | 169.9486 | 172.1997 | 179.3096 | 185.1157 | 188.9771 | 345.4435 | 418.9402 | 489.3717 | 558.912 | 605.654 | 718.7634 | 834.0391 | 940.3909 | 1035.7519 | 1121.1197 | 1206.6616 | 1294.4486 | Trevallyn | 46.227 | 0.06
Chapel Street |  | 20549 | 101.8624 | 82.56 | 84.8971 | 84.6362 | 83.2106 | 82.1991 | 82.2541 | 82.095 | 83.9646 | 89.0235 | 93.5093 | 95.9268 | 178.6856 | 235.2142 | 246.6968 | 248.6745 | 244.6215 | 244.4662 | 244.8267 | 245.921 | 249.1783 | 259.4666 | 267.8682 | 273.4558 | 435.9942 | 524.2975 | 580.0835 | 625.8345 | 677.2957 | 800.7522 | 924.5593 | 1035.7425 | 1131.319 | 1211.6921 | 1285.3993 | 1352.455 | Triabunna (RT) | 0 | 0
Chapel Street |  | 20551 | 40.5655 | 55.1576 | 56.719 | 56.5447 | 55.5923 | 54.9165 | 54.9532 | 54.8469 | 56.096 | 59.4758 | 62.4727 | 64.0879 | 40.5 | 43.705 | 61.7936 | 62.289 | 61.2738 | 61.2349 | 61.3252 | 61.5993 | 62.4152 | 64.9923 | 67.0967 | 68.4964 | 61.1169 | 72.5118 | 99.3037 | 110.5026 | 124.5779 | 161.4434 | 201.8362 | 241.278 | 277.8056 | 310.5077 | 342.0349 | 371.8193 | Tungatinah | 0.228 | 0
Chapel Street |  | 20552 | 90.0807 | 80.8678 | 83.157 | 82.9014 | 81.505 | 80.5143 | 80.5681 | 80.4123 | 82.2436 | 87.1988 | 91.5926 | 93.9606 | 188.7202 | 165.5414 | 179.4273 | 180.8657 | 177.9179 | 177.8049 | 178.0672 | 178.8631 | 181.2322 | 188.7151 | 194.8257 | 198.8897 | 499.5989 | 576.2719 | 644.7789 | 691.8162 | 745.2409 | 873.3209 | 1001.7204 | 1117.0175 | 1216.139 | 1299.5099 | 1375.9872 | 1445.5861 | Ulverstone | 23.656 | 0.024
Chapel Street |  | 20553 | 98.0885 | 83.1956 | 85.5507 | 85.2877 | 83.8511 | 82.8319 | 82.8873 | 82.7269 | 84.611 | 89.7088 | 94.2291 | 96.6653 | 174.4404 | 150.036 | 144.8605 | 146.0219 | 143.6419 | 143.5507 | 143.7624 | 144.405 | 146.3177 | 152.359 | 157.2924 | 160.5735 | 369.9958 | 434.7211 | 505.6074 | 587.6613 | 640.8216 | 773.6528 | 913.9908 | 1048.3145 | 1172.7382 | 1286.5228 | 1400.7268 | 1511.1612 | Waddamana | 0.791 | 0
Chapel Street |  | 20554 | 91.4512 | 82.4294 | 84.7629 | 84.5024 | 83.079 | 82.0692 | 82.124 | 81.9651 | 83.8318 | 88.8827 | 93.3614 | 95.7751 | 150.8271 | 136.1962 | 131.4981 | 132.5523 | 130.3919 | 130.3091 | 130.5013 | 131.0846 | 132.8209 | 138.3049 | 142.7832 | 145.7616 | 115.8202 | 141.1866 | 160.4485 | 178.1953 | 203.1064 | 264.0228 | 326.5967 | 384.3571 | 435.4517 | 479.5981 | 521.0442 | 559.4499 | Wesley Vale | 10.335 | 0.019
Creek Road |  | 10001 | 144.6955 | 103.9944 | 106.9383 | 106.6097 | 104.8139 | 103.5399 | 103.6091 | 103.4087 | 105.7637 | 112.136 | 117.7864 | 120.8316 | 221.4583 | 226.8577 | 219.0323 | 220.7882 | 217.1897 | 217.0518 | 217.3719 | 218.3435 | 221.2355 | 230.3701 | 237.8296 | 242.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Bellerive | 6.108 | 0.014
Creek Road |  | 10002 | 144.0649 | 118.4944 | 121.8488 | 121.4743 | 119.4282 | 117.9765 | 118.0554 | 117.827 | 120.5104 | 127.7711 | 134.2094 | 137.6792 | 218.11 | 225.0107 | 217.249 | 218.9907 | 215.4214 | 215.2847 | 215.6022 | 216.5658 | 219.4343 | 228.4946 | 235.8932 | 240.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Cambridge | 7.805 | 0.024
Creek Road |  | 10003 | 148.1841 | 109.6102 | 112.7131 | 112.3666 | 110.4739 | 109.1311 | 109.2041 | 108.9928 | 111.475 | 118.1914 | 124.1469 | 127.3565 | 223.4236 | 227.5156 | 219.6675 | 221.4285 | 217.8195 | 217.6812 | 218.0023 | 218.9767 | 221.8771 | 231.0382 | 238.5193 | 243.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Claremont | 11.167 | 0
Creek Road |  | 10007 | 127.3392 | 174.5833 | 179.5255 | 178.9737 | 175.9591 | 173.8202 | 173.9364 | 173.5999 | 177.5535 | 188.2511 | 197.7369 | 202.8491 | 208.8296 | 196.9122 | 190.1197 | 191.6439 | 188.5203 | 188.4007 | 188.6785 | 189.5218 | 192.0321 | 199.961 | 206.4357 | 210.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Derwent Park | 3.878 | 0.024
Creek Road |  | 10008 | 111.9256 | 113.3778 | 116.5873 | 116.229 | 114.2712 | 112.8822 | 112.9577 | 112.7391 | 115.3067 | 122.2539 | 128.4142 | 131.7341 | 233.0331 | 200.6655 | 193.7436 | 195.2968 | 192.1137 | 191.9918 | 192.275 | 193.1343 | 195.6925 | 203.7724 | 210.3706 | 214.7589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-East Hobart | 0.491 | 0.027
Creek Road |  | 10022 | 171.1878 | 111.4444 | 114.5992 | 114.247 | 112.3226 | 110.9573 | 111.0315 | 110.8167 | 113.3405 | 120.1692 | 126.2244 | 129.4877 | 223.0988 | 197.4835 | 190.6714 | 192.1999 | 189.0674 | 188.9473 | 189.226 | 190.0718 | 192.5893 | 200.5412 | 207.0347 | 211.3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Geilston Bay | 10.85 | 0
Creek Road |  | 10024 | 173.6397 | 113.2667 | 116.473 | 116.1151 | 114.1592 | 112.7716 | 112.847 | 112.6287 | 115.1937 | 122.1341 | 128.2883 | 131.605 | 230.0957 | 200.4735 | 193.5582 | 195.11 | 191.9299 | 191.8081 | 192.091 | 192.9496 | 195.5053 | 203.5775 | 210.1693 | 214.5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Howrah | 13.516 | 0.024
Creek Road |  | 10026 | 121.315 | 122.35 | 125.8135 | 125.4268 | 123.3141 | 121.8152 | 121.8966 | 121.6608 | 124.4315 | 131.9285 | 138.5763 | 142.159 | 197.2417 | 186.0457 | 179.6281 | 181.0682 | 178.117 | 178.0039 | 178.2665 | 179.0632 | 181.435 | 188.9263 | 195.0437 | 199.1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-New Town | 8.702 | 0.032
Derby |  | 55001 | 108.3333 | 116.1998 | 119.4892 | 119.122 | 117.1155 | 115.6919 | 115.7692 | 115.5453 | 118.1767 | 125.2969 | 131.6104 | 135.013 | 78.466 | 36.9167 | 35.6432 | 35.929 | 35.3434 | 35.3209 | 35.373 | 35.5311 | 36.0018 | 37.4882 | 38.7021 | 39.5094 | 165.1315 | 170.2661 | 193.3871 | 226.5938 | 266.7801 | 363.6872 | 462.2642 | 553.1267 | 634.5439 | 707.3198 | 779.8892 | 853.2474 | Zs-Rosny Park | 7.466 | 0
Derby |  | 55002 | 119.3333 | 45.6461 | 46.9383 | 46.794 | 46.0058 | 45.4466 | 45.477 | 45.389 | 46.4227 | 49.2196 | 51.6998 | 53.0364 | 115.7967 | 33.0036 | 31.8651 | 32.1206 | 31.5971 | 31.577 | 31.6236 | 31.7649 | 32.1857 | 33.5146 | 34.5998 | 35.3215 | 53.712 | 56.5905 | 60.5432 | 89.2591 | 138.806 | 270.2839 | 417.7924 | 567.1237 | 712.5697 | 851.6468 | 997.0016 | 1145.8566 | Zs-Sandy Bay | 18.762 | 0.011
Derby |  | 55003 | 32.3333 | 36.245 | 37.271 | 37.1564 | 36.5306 | 36.0865 | 36.1107 | 36.0408 | 36.8616 | 39.0825 | 41.0519 | 42.1132 | 17.2372 | 16.1297 | 15.5733 | 15.6981 | 15.4423 | 15.4325 | 15.4552 | 15.5243 | 15.7299 | 16.3794 | 16.9098 | 17.2625 | 18.28 | 18.28 | 24.3036 | 36.7481 | 51.0155 | 87.0125 | 125.3427 | 162.2241 | 196.5125 | 228.0302 | 260.0134 | 292.5852 | Zs-Summerleas | 7.197 | 0
Derwent Bridge |  | 49621 | 0.34614 | 0.26068 | 0.26806 | 0.26724 | 0.26274 | 0.25954 | 0.25972 | 0.25922 | 0.26512 | 0.28109 | 0.29526 | 0.30289 | 0.41245 | 0.34369 | 0.33184 | 0.3345 | 0.32904 | 0.32884 | 0.32932 | 0.33079 | 0.33517 | 0.34901 | 0.36031 | 0.36783 | 0 | 0 | 0 | 1.4503 | 3.6786 | 8.8833 | 13.9968 | 18.535 | 22.4307 | 25.7396 | 28.842 | 31.7607 | Zs-Trial Harbour | 0.809 | 0
Devonport |  | 80001 | 83.0228 | 61.0933 | 62.8228 | 62.6297 | 61.5748 | 60.8263 | 60.867 | 60.7492 | 62.1327 | 65.8762 | 69.1957 | 70.9846 | 91.2981 | 211.6362 | 204.3358 | 205.9739 | 202.6169 | 202.4882 | 202.7869 | 203.6932 | 206.3912 | 214.9129 | 221.8718 | 226.5 | 207.9282 | 250.6716 | 274.1389 | 305.529 | 334.6124 | 402.8637 | 469.8306 | 528.7161 | 578.3407 | 619.3116 | 656.2619 | 689.3767 | Zs-West Hobart | 13.843 | 0.024
Devonport |  | 80002 | 153.1936 | 155.9333 | 160.3475 | 159.8547 | 157.1621 | 155.2518 | 155.3555 | 155.055 | 158.5862 | 168.1411 | 176.6135 | 181.1796 | 131.2303 | 119.2733 | 115.159 | 116.0822 | 114.1903 | 114.1178 | 114.2861 | 114.7969 | 116.3174 | 121.12 | 125.0419 | 127.6503 | 35.222 | 35.222 | 35.222 | 37.0574 | 39.754 | 45.7244 | 51.2375 | 55.7995 | 59.4259 | 62.2627 | 64.702 | 66.8014
Devonport |  | 80003 | 169.6102 | 150.7133 | 154.9798 | 154.5034 | 151.901 | 150.0546 | 150.1549 | 149.8644 | 153.2774 | 162.5124 | 170.7012 | 175.1144 | 181.5924 | 174.0794 | 168.0746 | 169.422 | 166.6606 | 166.5548 | 166.8005 | 167.546 | 169.7652 | 176.7747 | 182.4987 | 186.3055 | 395.7012 | 445.9094 | 492.0873 | 536.6681 | 602.4663 | 758.3133 | 913.0945 | 1051.2121 | 1169.6473 | 1269.4765 | 1361.821 | 1445.7538
Devonport |  | 80004 | 56.4746 | 92.1867 | 94.7963 | 94.5049 | 92.9131 | 91.7837 | 91.8451 | 91.6674 | 93.755 | 99.4038 | 104.4126 | 107.1121 | 99.6264 | 98.8582 | 95.4481 | 96.2133 | 94.6452 | 94.5851 | 94.7246 | 95.148 | 96.4082 | 100.3888 | 103.6394 | 105.8013 | 281.108 | 377.564 | 434.0157 | 503.5542 | 568.8113 | 724.1288 | 879.0116 | 1018.0173 | 1138.395 | 1241.4305 | 1338.6989 | 1430.7183
Devonport |  | 80005 | 103.2 | 67.52 | 69.4314 | 69.218 | 68.0521 | 67.2249 | 67.2698 | 67.1397 | 68.6687 | 72.806 | 76.4746 | 78.4518 | 250.1773 | 206.8292 | 199.6946 | 201.2956 | 198.0147 | 197.889 | 198.1809 | 199.0667 | 201.7034 | 210.0315 | 216.8324 | 221.3554 | 366.0303 | 442.6047 | 534.7376 | 611.0216 | 697.8631 | 905.6487 | 1114.0948 | 1302.0461 | 1464.9763 | 1603.7947 | 1733.359 | 1853.7373
Devonport |  | 80006 | 205.8314 | 115.16 | 118.42 | 118.056 | 116.0675 | 114.6566 | 114.7333 | 114.5113 | 117.1192 | 124.1757 | 130.4327 | 133.8049 | 116.3897 | 280.6336 | 270.9532 | 273.1254 | 268.6738 | 268.5032 | 268.8993 | 270.1011 | 273.6787 | 284.9786 | 294.2063 | 300.3433 | 455.9051 | 497.3813 | 536.8039 | 602.8291 | 646.4836 | 754.3963 | 868.1273 | 976.2733 | 1075.0388 | 1163.2439 | 1248.9181 | 1326.9691
Devonport |  | 80007 | 91.308 | 103.7467 | 106.6836 | 106.3557 | 104.5642 | 103.2932 | 103.3622 | 103.1623 | 105.5117 | 111.8688 | 117.5058 | 120.5437 | 160.9115 | 142.7917 | 137.8661 | 138.9713 | 136.7063 | 136.6195 | 136.821 | 137.4325 | 139.2529 | 145.0025 | 149.6977 | 152.8203 | 541.4932 | 646.8871 | 731.6314 | 801.3698 | 885.6233 | 1089.3965 | 1296.8384 | 1487.7705 | 1658.1835 | 1809.4258 | 1958.5638 | 2107.18
Devonport |  | 80008 | 163.4687 | 72.4533 | 74.5044 | 74.2754 | 73.0243 | 72.1366 | 72.1849 | 72.0452 | 73.686 | 78.1256 | 82.0622 | 84.1838 | 236.5933 | 144.2572 | 139.2811 | 140.3977 | 138.1094 | 138.0217 | 138.2253 | 138.8431 | 140.6821 | 146.4908 | 151.2342 | 154.3888 | 309.8018 | 371.8489 | 428.3748 | 505.8315 | 612.7733 | 871.9628 | 1135.8532 | 1377.8803 | 1591.8717 | 1778.4978 | 1957.613 | 2129.642
Devonport |  | 80009 | 83.6755 | 77.6867 | 79.8858 | 79.6403 | 78.2988 | 77.3471 | 77.3988 | 77.2491 | 79.0084 | 83.7686 | 87.9896 | 90.2645 | 146.7103 | 170.6146 | 164.7293 | 166.0499 | 163.3435 | 163.2398 | 163.4806 | 164.2113 | 166.3863 | 173.2563 | 178.8663 | 182.5974 | 327.4908 | 371.8049 | 415.7636 | 472.6998 | 558.0039 | 763.7161 | 971.4839 | 1159.7998 | 1323.6024 | 1463.4626 | 1594.3572 | 1716.7956
Devonport |  | 80010 | 105.5043 | 73.4667 | 75.5464 | 75.3142 | 74.0456 | 73.1456 | 73.1944 | 73.0528 | 74.7166 | 79.2182 | 83.21 | 85.3612 | 182 | 186.0459 | 179.6283 | 181.0683 | 178.1172 | 178.0041 | 178.2666 | 179.0634 | 181.4352 | 188.9264 | 195.0439 | 199.1124 | 981.8264 | 1233.0835 | 1397.2928 | 1507.5121 | 1613.9174 | 1869.9873 | 2128.8631 | 2364.6604 | 2571.8871 | 2751.9347 | 2924.8782 | 3092.3382
Devonport |  | 80011 | 92.0007 | 88.5067 | 91.0121 | 90.7324 | 89.2041 | 88.1198 | 88.1787 | 88.0081 | 90.0124 | 95.4357 | 100.2446 | 102.8363 | 156 | 156.3725 | 150.9785 | 152.1889 | 149.7084 | 149.6133 | 149.834 | 150.5037 | 152.4972 | 158.7936 | 163.9354 | 167.355 | 529.7704 | 632.2386 | 743.3366 | 799.9007 | 870.7665 | 1043.0132 | 1220.9477 | 1387.469 | 1538.3103 | 1673.2718 | 1805.9051 | 1935.6675
Electrona |  | 33271 | 109.9648 | 95.0502 | 97.7409 | 97.4404 | 95.7992 | 94.6347 | 94.698 | 94.5148 | 96.6672 | 102.4914 | 107.6559 | 110.4392 | 183.6586 | 158.62 | 153.1484 | 154.3762 | 151.8601 | 151.7637 | 151.9875 | 152.6668 | 154.689 | 161.0759 | 166.2916 | 169.7604 | 345.5719 | 437.6339 | 502.8521 | 543.0185 | 571.9285 | 640.0803 | 707.4329 | 768.0472 | 820.5023 | 864.9966 | 906.1444 | 942.6347
Electrona |  | 33272 | 154.9824 | 115.9582 | 119.2407 | 118.8742 | 116.8719 | 115.4513 | 115.5285 | 115.305 | 117.931 | 125.0363 | 131.3368 | 134.7323 | 250.445 | 251.7421 | 243.0583 | 245.0069 | 241.0136 | 240.8606 | 241.2159 | 242.294 | 245.5033 | 255.6398 | 263.9175 | 269.4227 | 517.2529 | 553.2057 | 607.5954 | 669.4964 | 736.9579 | 903.842 | 1078.3459 | 1243.1478 | 1392.9817 | 1526.6192 | 1656.748 | 1777.4722
Electrona |  | 33273 | 18.085 | 1.0682 | 1.0984 | 1.0951 | 1.0766 | 1.0635 | 1.0642 | 1.0622 | 1.0864 | 1.1518 | 1.2099 | 1.2411 | 16.6384 | 0.92103 | 0.88926 | 0.89638 | 0.88177 | 0.88122 | 0.88251 | 0.88646 | 0.8982 | 0.93529 | 0.96557 | 0.98571 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Electrona |  | 33274 | 180.0703 | 144.4984 | 148.5889 | 148.1322 | 145.6371 | 143.8668 | 143.963 | 143.6845 | 146.9568 | 155.8109 | 163.6621 | 167.8933 | 263.5225 | 238.6318 | 230.4003 | 232.2473 | 228.462 | 228.317 | 228.6537 | 229.6757 | 232.7179 | 242.3265 | 250.1731 | 255.3916 | 533.3492 | 609.89 | 749.091 | 809.5414 | 853.225 | 957.2376 | 1060.868 | 1153.4338 | 1232.6764 | 1299.12 | 1359.9535 | 1415.2764
Electrona |  | 33275 | 8.0821 | 24.6159 | 25.3128 | 25.235 | 24.8099 | 24.5083 | 24.5247 | 24.4773 | 25.0347 | 26.5431 | 27.8805 | 28.6013 | 12.1884 | 8.5077 | 8.2142 | 8.2801 | 8.1451 | 8.1399 | 8.1519 | 8.1884 | 8.2968 | 8.6394 | 8.9192 | 9.1052 | 527.6849 | 563.6107 | 611.2893 | 683.5439 | 779.7429 | 1020.5676 | 1274.3335 | 1515.0413 | 1734.5883 | 1931.4174 | 2124.9436 | 2306.8102
Electrona |  | 33276 | 165.0645 | 130.2142 | 133.9003 | 133.4887 | 131.2403 | 129.645 | 129.7317 | 129.4807 | 132.4295 | 140.4084 | 147.4834 | 151.2963 | 240.265 | 243.2399 | 234.8494 | 236.7321 | 232.8737 | 232.7259 | 233.0691 | 234.1109 | 237.2118 | 247.006 | 255.0041 | 260.3234 | 735.242 | 771.9507 | 824.9006 | 919.5807 | 1005.7303 | 1217.2121 | 1436.1822 | 1642.456 | 1830.7112 | 2000.1994 | 2167.5063 | 2328.7077
Electrona |  | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay |  | 90019 | 408.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401.7503 | 0.24 | 0.23172 | 0.23358 | 0.22977 | 0.22963 | 0.22996 | 0.23099 | 0.23405 | 0.24372 | 0.25161 | 0.25686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay |  | 90020 | 98.4862 | 71.4733 | 73.4966 | 73.2707 | 72.0366 | 71.1609 | 71.2085 | 71.0707 | 72.6893 | 77.0688 | 80.9523 | 83.0452 | 122.6979 | 96.671 | 93.3364 | 94.0846 | 92.5512 | 92.4924 | 92.6288 | 93.0429 | 94.2752 | 98.1678 | 101.3465 | 103.4605 | 0 | 0 | 0 | 7.589 | 20.3774 | 52.4734 | 85.5273 | 115.4897 | 141.1293 | 162.3806 | 181.4741 | 198.4286
Emu Bay |  | 90021 | 67.5481 | 0.575 | 0.59128 | 0.58946 | 0.57953 | 0.57249 | 0.57287 | 0.57176 | 0.58478 | 0.62002 | 0.65126 | 0.66809 | 88.3617 | 78.8733 | 76.1526 | 76.7631 | 75.512 | 75.464 | 75.5753 | 75.9131 | 76.9186 | 80.0945 | 82.688 | 84.4128 | 0 | 0 | 0 | 9.7672 | 25.2575 | 62.653 | 100.5257 | 134.8877 | 164.6231 | 189.6177 | 212.3386 | 232.6535
Emu Bay |  | 90023 | 86.3185 | 65.725 | 67.5856 | 67.3778 | 66.2429 | 65.4377 | 65.4815 | 65.3548 | 66.8432 | 70.8705 | 74.4416 | 76.3661 | 136.561 | 121.3834 | 117.1963 | 118.1359 | 116.2104 | 116.1366 | 116.3079 | 116.8278 | 118.3752 | 123.2628 | 127.2541 | 129.9085 | 57.9803 | 73.1866 | 80.7496 | 125.0509 | 175.5161 | 297.8757 | 422.5925 | 537.1233 | 638.4699 | 726.854 | 811.6541 | 893.1108
Emu Bay |  | 90024 | 78.9189 | 44.135 | 45.3844 | 45.2449 | 44.4828 | 43.9421 | 43.9715 | 43.8864 | 44.8859 | 47.5902 | 49.9883 | 51.2806 | 122.879 | 121.0229 | 116.8482 | 117.785 | 115.8652 | 115.7917 | 115.9624 | 116.4807 | 118.0236 | 122.8967 | 126.8761 | 129.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53001 | 90.8942 | 78.6392 | 80.8653 | 80.6168 | 79.2589 | 78.2954 | 78.3478 | 78.1962 | 79.9771 | 84.7957 | 89.0684 | 91.3712 | 119.2912 | 113.8746 | 109.9465 | 110.828 | 109.0216 | 108.9524 | 109.1131 | 109.6008 | 111.0525 | 115.6378 | 119.3821 | 121.8724 | 685.8533 | 801.0168 | 889.6631 | 955.2478 | 1005.5041 | 1125.2545 | 1245.1293 | 1353.3073 | 1447.5306 | 1527.5113 | 1603.0203 | 1674.2908
George Town |  | 53002 | 144.5577 | 8.6803 | 8.9261 | 8.8986 | 8.7487 | 8.6424 | 8.6482 | 8.6314 | 8.828 | 9.3599 | 9.8315 | 10.0857 | 166.7577 | 7.2056 | 6.957 | 7.0128 | 6.8985 | 6.8941 | 6.9043 | 6.9351 | 7.027 | 7.3171 | 7.554 | 7.7116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53003 | 88.8974 | 117.3986 | 120.722 | 120.3509 | 118.3237 | 116.8855 | 116.9636 | 116.7373 | 119.3959 | 126.5895 | 132.9682 | 136.4059 | 149.7026 | 143.9946 | 139.0275 | 140.1421 | 137.858 | 137.7705 | 137.9737 | 138.5903 | 140.426 | 146.2241 | 150.9588 | 154.1078 | 813.2555 | 923.2165 | 1006.0339 | 1116.7109 | 1235.6663 | 1523.4507 | 1816.6048 | 2086.2851 | 2325.8958 | 2535.9426 | 2738.1865 | 2930.2147
George Town |  | 53004 | 43.0165 | 37.6633 | 38.7295 | 38.6105 | 37.9601 | 37.4987 | 37.5238 | 37.4512 | 38.3041 | 40.6119 | 42.6583 | 43.7612 | 56.8138 | 55.2125 | 53.308 | 53.7353 | 52.8595 | 52.826 | 52.9039 | 53.1403 | 53.8442 | 56.0674 | 57.8829 | 59.0903 | 238.3686 | 255.231 | 283.9252 | 309.4693 | 338.4944 | 407.5582 | 476.4565 | 539.1723 | 594.3885 | 642.5034 | 688.7678 | 733.3094
George Town |  | 53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53006 | 0 | 0 | 0 | 31.6878 | 31.1541 | 30.7754 | 30.796 | 30.7364 | 31.4364 | 33.3304 | 35.0099 | 35.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
George Town |  | 53007 | 0 | 0 | 0 | 31.6878 | 31.1541 | 30.7754 | 30.796 | 30.7364 | 31.4364 | 33.3304 | 35.0099 | 35.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15929 | 0.41415 | 1.0354 | 1.6725 | 2.2619 | 2.7875 | 3.2495 | 3.6955 | 4.1256
George Town |  | 53008 | 64 | 49.7031 | 51.1101 | 82.6408 | 81.2488 | 80.2612 | 80.3148 | 80.1595 | 81.985 | 86.9246 | 91.3047 | 93.6652 | 68.7223 | 68.4755 | 66.1134 | 66.6434 | 65.5572 | 65.5156 | 65.6123 | 65.9055 | 66.7785 | 69.5357 | 71.7872 | 73.2847 | 312.781 | 358.0599 | 380.3059 | 437.3446 | 505.28 | 669.4479 | 836.3361 | 989.2455 | 1124.3827 | 1242.2721 | 1355.5782 | 1463.3362
George Town |  | 53009 | 79 | 52.5744 | 54.0627 | 85.5844 | 84.1428 | 83.12 | 83.1756 | 83.0147 | 84.9053 | 90.0208 | 94.5569 | 97.0015 | 102.3811 | 122.8423 | 118.6049 | 119.5558 | 117.6072 | 117.5325 | 117.7058 | 118.2319 | 119.798 | 124.7443 | 128.7836 | 131.4699 | 911.5911 | 1047.3615 | 1149.7639 | 1252.6087 | 1338.5152 | 1542.4023 | 1746.1847 | 1931.1784 | 2093.2918 | 2233.5088 | 2366.9907 | 2492.3317
George Town |  | 53010 | 187.6723 | 24.7711 | 25.4723 | 25.394 | 24.9663 | 24.6628 | 24.6793 | 24.6316 | 25.1925 | 26.7104 | 28.0563 | 28.7816 | 242.744 | 34.3062 | 33.1228 | 33.3884 | 32.8442 | 32.8233 | 32.8717 | 33.0187 | 33.456 | 34.8374 | 35.9654 | 36.7156 | 0 | 0 | 0 | 2.0707 | 5.3839 | 13.4599 | 21.7429 | 29.4046 | 36.2381 | 42.2433 | 48.0414 | 53.6324
Gordon |  | 49801 | 11.7503 | 5.7404 | 5.9029 | 5.8848 | 5.7856 | 5.7153 | 5.7191 | 5.7081 | 5.8381 | 6.1898 | 6.5017 | 6.6698 | 15.5568 | 8.5152 | 8.2215 | 8.2874 | 8.1523 | 8.1471 | 8.1591 | 8.1956 | 8.3042 | 8.647 | 8.927 | 9.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna |  | 37002 | 57.0015 | 56.1201 | 57.7088 | 57.5314 | 56.5623 | 194.8784 | 195.0086 | 194.6314 | 199.0639 | 211.0575 | 221.6925 | 227.424 | 21.5428 | 22.3845 | 21.6124 | 21.7857 | 21.4306 | 21.417 | 21.4486 | 21.5444 | 21.8298 | 22.7311 | 23.4672 | 23.9567 | 6.24 | 6.24 | 6.24 | 10.5555 | 17.5417 | 34.7973 | 52.7749 | 69.7653 | 85.4336 | 99.9531 | 115.1216 | 131.3733
Hadspen |  | 67081 | 96.3604 | 71.5175 | 73.542 | 73.316 | 72.0811 | 71.2049 | 71.2525 | 71.1147 | 72.7342 | 77.1165 | 81.0023 | 83.0965 | 132.3497 | 136.9945 | 132.2689 | 133.3292 | 131.1562 | 131.0729 | 131.2662 | 131.8529 | 133.5994 | 139.1156 | 143.6201 | 146.616 | 402.812 | 477.3123 | 570.8251 | 617.1603 | 666.3465 | 785.7307 | 906.6136 | 1016.0712 | 1111.0079 | 1191.9092 | 1267.8342 | 1339.7244
Hadspen |  | 67082 | 131 | 119.7542 | 123.1442 | 122.7657 | 120.6979 | 119.2308 | 119.3105 | 119.0797 | 121.7916 | 129.1295 | 135.6362 | 139.1429 | 131.3579 | 144.0218 | 139.0538 | 140.1685 | 137.884 | 137.7964 | 137.9997 | 138.6165 | 140.4525 | 146.2517 | 150.9873 | 154.1368 | 628.1141 | 687.4882 | 749.6442 | 830.3352 | 933.3362 | 1182.3314 | 1435.8509 | 1668.81 | 1875.3965 | 2056.008 | 2229.339 | 2392.4502
Hadspen |  | 67083 | 138.3715 | 112.9247 | 116.1214 | 115.7645 | 113.8146 | 112.4311 | 112.5063 | 112.2886 | 114.8459 | 121.7654 | 127.901 | 131.2077 | 141.0807 | 237.4912 | 229.299 | 231.1373 | 227.3701 | 227.2257 | 227.5608 | 228.5779 | 231.6056 | 241.1683 | 248.9774 | 254.1709 | 79.2853 | 83.1514 | 91.7471 | 107.3929 | 133.0579 | 197.7709 | 267.1686 | 335.0506 | 399.7055 | 460.7314 | 523.9715 | 588.9442
Hadspen |  | 67084 | 172.0287 | 172.2769 | 177.1538 | 176.6093 | 173.6345 | 171.5239 | 171.6386 | 171.3065 | 175.2079 | 185.7642 | 195.1246 | 200.1693 | 172.7152 | 138.5577 | 133.7782 | 134.8506 | 132.6528 | 132.5685 | 132.7641 | 133.3575 | 135.1238 | 140.703 | 145.2589 | 148.289 | 76.2533 | 76.4234 | 83.1836 | 97.2982 | 120.0422 | 176.4572 | 236.298 | 294.8228 | 351.4549 | 406.7897 | 467.1871 | 531.663
Hadspen |  | 67085 | 70.2029 | 65.2019 | 67.0477 | 66.8416 | 65.7157 | 64.917 | 64.9603 | 64.8347 | 66.3112 | 70.3065 | 73.8492 | 75.7584 | 115.3128 | 114.3402 | 110.3961 | 111.2811 | 109.4674 | 109.3979 | 109.5592 | 110.0489 | 111.5066 | 116.1106 | 119.8702 | 122.3707 | 528.9254 | 616.5762 | 670.0171 | 706.2884 | 740.2393 | 819.1745 | 896.0166 | 963.1159 | 1019.294 | 1065.3816 | 1106.6876 | 1143.4824
Hadspen |  | 67086 | 96.4917 | 91.2825 | 93.8665 | 93.578 | 92.0018 | 90.8835 | 90.9443 | 90.7683 | 92.8355 | 98.4288 | 103.3886 | 106.0615 | 175.7695 | 182.4601 | 176.1661 | 177.5784 | 174.6841 | 174.5732 | 174.8307 | 175.6121 | 177.9382 | 185.2851 | 191.2846 | 195.2748 | 1122.6154 | 1310.593 | 1508.478 | 1613.7955 | 1723.7863 | 1990.5811 | 2261.5445 | 2508.3398 | 2723.7711 | 2907.8997 | 3079.6149 | 3238.4808
Hadspen |  | 67087 | 182 | 80.2208 | 82.4917 | 82.2382 | 80.853 | 79.8702 | 79.9236 | 79.769 | 81.5856 | 86.5012 | 90.8599 | 93.2089 | 211.3447 | 230.2388 | 222.2967 | 224.0789 | 220.4267 | 220.2867 | 220.6117 | 221.5977 | 224.5328 | 233.8036 | 241.3742 | 246.4091 | 864.4763 | 970.3083 | 1179.8776 | 1260.3277 | 1352.188 | 1570.787 | 1788.7459 | 1983.7921 | 2151.1499 | 2291.7411 | 2420.5427 | 2535.9197
Hadspen |  | 67088 | 47.4435 | 42.5008 | 43.704 | 43.5696 | 42.8357 | 42.3151 | 42.3434 | 42.2614 | 43.2239 | 45.8281 | 48.1374 | 49.3819 | 99.5241 | 205.3757 | 198.2913 | 199.881 | 196.6232 | 196.4984 | 196.7882 | 197.6678 | 200.286 | 208.5556 | 215.3086 | 219.7999 | 614.2081 | 700.1056 | 784.943 | 851.427 | 912.0891 | 1058.4545 | 1206.74 | 1342.0849 | 1461.3232 | 1565.2194 | 1665.2253 | 1761.9086
Hadspen |  | 67089 | 55.3855 | 50.4819 | 51.911 | 51.7514 | 50.8797 | 50.2613 | 50.2949 | 50.1976 | 51.3408 | 54.4341 | 57.177 | 58.6552 | 109.3138 | 109.9003 | 106.1093 | 106.96 | 105.2167 | 105.1499 | 105.305 | 105.7756 | 107.1767 | 111.6019 | 115.2156 | 117.6189 | 591.2843 | 680.4192 | 782.2485 | 848.2993 | 913.5348 | 1071.1329 | 1230.9216 | 1376.6043 | 1504.3045 | 1614.3339 | 1718.2684 | 1816.1956
Hadspen |  | 67090 | 167.4959 | 141.4987 | 145.5043 | 145.0571 | 142.6138 | 140.8803 | 140.9744 | 140.7017 | 143.9061 | 152.5764 | 160.2646 | 164.408 | 264.604 | 248.2771 | 239.7128 | 241.6346 | 237.6963 | 237.5453 | 237.8957 | 238.959 | 242.1241 | 252.1212 | 260.2849 | 265.7143 | 989.2083 | 1128.6993 | 1266.6831 | 1370.1299 | 1483.9945 | 1754.3568 | 2024.8542 | 2268.8569 | 2481.5801 | 2665.353 | 2841.3107 | 3011.4902
Hadspen |  | 67091 | 79.6207 | 59.0483 | 60.7199 | 60.5332 | 59.5136 | 58.7902 | 58.8295 | 58.7157 | 60.0529 | 63.6711 | 66.8794 | 68.6085 | 133.9512 | 139.9172 | 135.0907 | 136.1737 | 133.9543 | 133.8693 | 134.0667 | 134.6659 | 136.4496 | 142.0835 | 146.6842 | 149.744 | 323.7766 | 379.3443 | 418.9872 | 489.6783 | 569.5833 | 769.5122 | 980.1811 | 1180.547 | 1364.5084 | 1531.1683 | 1697.1574 | 1862.222
Huon River |  | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Huon River |  | 38423 | 110.4 | 10.1166 | 10.403 | 10.371 | 10.1963 | 10.0724 | 10.0791 | 10.0596 | 10.2887 | 10.9086 | 11.4583 | 11.7545 | 105.234 | 36.1624 | 34.915 | 35.1949 | 34.6213 | 34.5993 | 34.6504 | 34.8052 | 35.2662 | 36.7223 | 37.9114 | 38.7022 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
Kermandie |  | 31002 | 111.9187 | 123.6303 | 127.1301 | 126.7393 | 124.6045 | 123.09 | 123.1722 | 122.9339 | 125.7337 | 133.3091 | 140.0264 | 143.6466 | 120.7585 | 119.6174 | 115.4912 | 116.4171 | 114.5197 | 114.447 | 114.6158 | 115.128 | 116.653 | 121.4694 | 125.4026 | 128.0185 | 77.4966 | 85.7988 | 93.3555 | 107.2899 | 129.6152 | 184.0717 | 239.885 | 291.4008 | 337.2308 | 377.4804 | 416.5226 | 454.7138
Kermandie |  | 31007 | 92.6143 | 87.5585 | 90.0371 | 89.7604 | 88.2484 | 87.1758 | 87.234 | 87.0653 | 89.0481 | 94.4133 | 99.1706 | 101.7345 | 135.5033 | 126.5291 | 122.1645 | 123.1439 | 121.1368 | 121.0599 | 121.2384 | 121.7803 | 123.3934 | 128.4881 | 132.6486 | 135.4156 | 231.2838 | 251.9903 | 263.6379 | 302.9809 | 362.7188 | 511.7613 | 669.8754 | 822.623 | 965.9773 | 1099.0913 | 1234.8881 | 1361.8237
Kermandie |  | 31008 | 123.897 | 118.6505 | 122.0093 | 121.6343 | 119.5855 | 118.1319 | 118.2109 | 117.9822 | 120.6691 | 127.9394 | 134.3862 | 137.8605 | 157.8333 | 148.8228 | 143.6892 | 144.8411 | 142.4804 | 142.3899 | 142.6 | 143.2373 | 145.1346 | 151.127 | 156.0205 | 159.2751 | 251.3387 | 273.438 | 296.6033 | 343.9314 | 401.9323 | 546.8027 | 700.4237 | 848.6671 | 987.7197 | 1117.0292 | 1249.5994 | 1381.8831
Kermandie |  | 31010 | 64.322 | 55.0896 | 56.6491 | 56.475 | 55.5237 | 54.8488 | 54.8855 | 54.7793 | 56.0269 | 59.4025 | 62.3957 | 64.0089 | 81.2664 | 72.0579 | 69.5723 | 70.13 | 68.987 | 68.9432 | 69.0449 | 69.3535 | 70.2721 | 73.1736 | 75.5429 | 77.1187 | 99.6484 | 105.7714 | 113.1114 | 129.329 | 155.4166 | 219.6473 | 286.5096 | 349.5868 | 407.235 | 459.3325 | 511.0767 | 560.5976
Kingston 11kV |  | 34251 | 99.1984 | 64.6253 | 66.4547 | 66.2504 | 65.1345 | 64.3428 | 64.3858 | 64.2612 | 65.7247 | 69.6846 | 73.196 | 75.0883 | 141.1249 | 121.4755 | 117.2852 | 118.2255 | 116.2986 | 116.2247 | 116.3962 | 116.9164 | 118.465 | 123.3563 | 127.3506 | 130.0071 | 659.3548 | 727.3215 | 828.2056 | 910.2527 | 946.0472 | 1032.42 | 1120.4104 | 1201.6321 | 1274.3069 | 1338.6653 | 1401.3816 | 1462.3012
Kingston 11kV |  | 34252 | 184.5964 | 141.4125 | 145.4156 | 144.9687 | 142.5268 | 140.7944 | 140.8885 | 140.6159 | 143.8183 | 152.4834 | 160.1669 | 164.3077 | 309.9776 | 254.0096 | 245.2476 | 247.2137 | 243.1845 | 243.0301 | 243.3885 | 244.4764 | 247.7145 | 257.9424 | 266.2946 | 271.8494 | 1196.662 | 1328.1139 | 1472.5164 | 1618.1629 | 1714.4475 | 1944.5369 | 2174.4061 | 2380.1107 | 2556.3866 | 2704.2257 | 2839.5104 | 2962.3832
Kingston 11kV |  | 34253 | 88.5234 | 52.3083 | 53.789 | 53.6237 | 52.7205 | 52.0796 | 52.1145 | 52.0136 | 53.1982 | 56.4034 | 59.2455 | 60.7772 | 149.7311 | 136.9163 | 132.1934 | 133.2532 | 131.0814 | 130.9981 | 131.1914 | 131.7777 | 133.5232 | 139.0362 | 143.5382 | 146.5324 | 463.9158 | 528.8996 | 628.9652 | 681.2175 | 719.6539 | 811.7986 | 904.1341 | 986.9946 | 1058.182 | 1118.022 | 1172.8902 | 1222.8106
Kingston 11kV |  | 34254 | 14.0706 | 6.7783 | 6.9702 | 6.9487 | 6.8317 | 6.7487 | 6.7532 | 6.7401 | 6.8936 | 7.3089 | 7.6772 | 7.8757 | 19.5 | 14.1217 | 13.6346 | 37.5226 | 36.9111 | 36.8876 | 36.942 | 37.1072 | 37.5987 | 39.1511 | 40.4188 | 41.2619 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
Kingston 11kV |  | 34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7787 | 23.3912 | 23.3763 | 23.4108 | 23.5154 | 23.8269 | 24.8107 | 25.6141 | 26.1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34256 | 99.9951 | 78.0646 | 80.2744 | 80.0277 | 78.6797 | 77.7233 | 77.7753 | 77.6248 | 79.3927 | 84.1761 | 88.4176 | 90.7035 | 174.4023 | 145.727 | 140.7001 | 165.6068 | 162.9077 | 162.8043 | 163.0444 | 163.7731 | 165.9424 | 172.794 | 178.3891 | 182.1102 | 480.5132 | 557.988 | 672.5486 | 723.1808 | 771.0623 | 885.7898 | 1000.7145 | 1103.8129 | 1192.3484 | 1266.7229 | 1334.8548 | 1396.768
Kingston 11kV |  | 34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.4115 | 232.1186 | 257.7582 | 253.5571 | 253.3961 | 253.7698 | 254.9041 | 258.2804 | 268.9445 | 277.653 | 283.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4376 | 75.7319 | 76.339 | 75.0948 | 75.0471 | 75.1578 | 75.4937 | 76.4937 | 79.652 | 82.2312 | 83.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34259 | 164.3435 | 106.5485 | 109.5647 | 109.2279 | 107.3881 | 106.0828 | 106.1537 | 105.9483 | 108.3612 | 114.89 | 120.6792 | 123.7991 | 294.5235 | 221.3235 | 213.689 | 215.4021 | 211.8914 | 211.7569 | 212.0692 | 213.017 | 215.8385 | 224.7503 | 232.0277 | 236.8677 | 996.9094 | 1138.8981 | 1296.2601 | 1407.4419 | 1478.7793 | 1650.2556 | 1822.5613 | 1977.5972 | 2111.1113 | 2223.571 | 2326.8522 | 2420.9306
Kingston 11kV |  | 34260 | 74.97 | 43.8161 | 45.0564 | 44.918 | 44.1614 | 43.6246 | 43.6537 | 43.5693 | 44.5615 | 47.2464 | 49.6271 | 50.9101 | 109.9378 | 134.6064 | 129.9632 | 131.0051 | 128.8699 | 128.7881 | 128.978 | 129.5545 | 131.2705 | 136.6905 | 141.1166 | 144.0602 | 99.7487 | 127.5088 | 148.1355 | 169.5062 | 192.4337 | 247.0714 | 301.4996 | 350.0771 | 391.6164 | 426.4066 | 458.2269 | 487.1403
Kingston 11kV |  | 34261 | 76.9418 | 82.8719 | 85.2178 | 84.9559 | 83.5249 | 82.5096 | 82.5648 | 82.4051 | 84.2818 | 89.3597 | 93.8625 | 96.2892 | 98.6893 | 125.7349 | 121.3977 | 122.371 | 120.3765 | 120.3001 | 120.4775 | 121.016 | 122.6189 | 127.6817 | 131.816 | 134.5657 | 0 | 0 | 0 | 20.7423 | 54.1093 | 135.3173 | 217.7596 | 292.4987 | 357.1674 | 411.7646 | 461.9375 | 507.6229
Kingston 11kV |  | 34262 | 104.0471 | 80.4834 | 82.7618 | 82.5074 | 81.1177 | 80.1317 | 80.1852 | 80.0301 | 81.8527 | 86.7843 | 91.1573 | 93.514 | 142.2183 | 170.8265 | 164.9339 | 166.2561 | 163.5464 | 163.4425 | 163.6836 | 164.4152 | 166.5929 | 173.4714 | 179.0884 | 182.8241 | 36.9928 | 38.3424 | 38.3424 | 46.7312 | 60.4001 | 94.5122 | 130.6207 | 165.4502 | 198.2105 | 228.8623 | 260.5087 | 293.0764
Kingston 11kV |  | 34263 | 90.6633 | 70.689 | 72.6901 | 72.4667 | 71.2461 | 70.3801 | 70.4271 | 70.2909 | 71.8917 | 76.2232 | 80.064 | 82.1339 | 154.1723 | 186.3883 | 179.9589 | 181.4016 | 178.445 | 178.3317 | 178.5947 | 179.393 | 181.7691 | 189.2742 | 195.4029 | 199.4789 | 363.9402 | 409.3921 | 466.1888 | 526.0266 | 571.3465 | 682.2842 | 797.6352 | 907.6155 | 1011.2576 | 1110.5879 | 1218.7753 | 1340.049
Kingston 11kV |  | 34264 | 162.9071 | 112.5586 | 115.7449 | 115.3891 | 113.4455 | 112.0666 | 112.1415 | 111.9245 | 114.4735 | 121.3706 | 127.4863 | 130.7822 | 201.1108 | 168.2277 | 162.4247 | 163.7268 | 161.0583 | 160.9561 | 161.1935 | 161.9139 | 164.0585 | 170.8323 | 176.3639 | 180.0428 | 232.9853 | 248.6839 | 261.0295 | 291.9213 | 334.0519 | 436.7308 | 542.4518 | 640.7562 | 728.9937 | 807.1235 | 883.216 | 955.447
Kingston 33kV |  | 36240 | 124.4027 | -3.4968 | -3.5958 | -3.5847 | -3.5243 | -3.4815 | -3.4838 | -3.4771 | -3.5563 | -3.7705 | -3.9605 | -4.0629 | 216.7573 | 182.8778 | 176.5695 | 177.985 | 175.0841 | 174.973 | 175.231 | 176.0142 | 178.3456 | 185.7093 | 191.7226 | 195.7219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Knights Road |  | 30603 | 175.1 | 185.03 | 190.2679 | 189.6831 | 186.4881 | 184.2213 | 184.3444 | 183.9878 | 188.1779 | 199.5156 | 209.569 | 214.9871 | 251.8704 | 263.52 | 254.4299 | 256.4696 | 252.2895 | 252.1294 | 252.5012 | 253.6298 | 256.9892 | 267.6001 | 276.265 | 282.0278 | 278.4738 | 323.9695 | 336.7861 | 394.0063 | 454.7155 | 602.997 | 756.0797 | 899.3455 | 1029.3511 | 1146.2562 | 1262.3289 | 1373.6653
Knights Road |  | 30604 | 254.8598 | 49.98 | 51.3948 | 51.2369 | 50.3738 | 49.7615 | 49.7948 | 49.6985 | 50.8303 | 53.8928 | 56.6084 | 58.072 | 253.5363 | 265.5515 | 256.3914 | 258.4468 | 254.2345 | 254.0731 | 254.4478 | 255.5851 | 258.9704 | 269.6631 | 278.3948 | 284.202 | 289.8047 | 322.4866 | 352.5112 | 392.0443 | 446.7498 | 578.7189 | 713.3273 | 837.8457 | 949.5204 | 1048.6674 | 1145.6964 | 1238.87
Knights Road |  | 30605 | 129.5265 | 214.52 | 220.5927 | 219.9147 | 216.2104 | 213.5824 | 213.7251 | 213.3117 | 218.1696 | 231.3144 | 242.9701 | 249.2517 | 186.5098 | 220.94 | 213.3187 | 215.0289 | 211.5242 | 211.3899 | 211.7017 | 212.6479 | 215.4645 | 224.3608 | 231.6257 | 236.4573 | 131.0558 | 152.6553 | 165.5713 | 192.8054 | 221.873 | 292.4711 | 364.9318 | 432.4052 | 493.4428 | 548.3085 | 602.9004 | 656.0658
Knights Road |  | 30606 | 151.5887 | 162.31 | 166.9047 | 166.3917 | 163.589 | 161.6006 | 161.7086 | 161.3957 | 165.0714 | 175.0169 | 183.8359 | 188.5886 | 174.4706 | 276.6206 | 267.0786 | 269.2197 | 264.8318 | 264.6637 | 265.054 | 266.2387 | 269.7652 | 280.9035 | 289.9992 | 296.0485 | 253.4635 | 303.9118 | 326.4497 | 375.8313 | 436.1876 | 584.3656 | 737.8171 | 881.4389 | 1011.2952 | 1127.2187 | 1241.182 | 1353.4402
Knights Road |  | 30607 | 104 | 86.0167 | 88.4516 | 88.1798 | 86.6945 | 85.6407 | 85.6979 | 85.5322 | 87.4801 | 92.7507 | 97.4244 | 99.9431 | 172.3114 | 162.237 | 156.6407 | 157.8965 | 155.323 | 155.2244 | 155.4533 | 156.1481 | 158.2164 | 164.749 | 170.0836 | 173.6314 | 480.6929 | 522.8974 | 544.3956 | 626.6691 | 705.7093 | 898.6077 | 1097.7609 | 1284.3331 | 1453.5682 | 1606.0951 | 1758.1423 | 1903.3355
Knights Road |  | 30608 | 186.9 | 168.2167 | 172.9786 | 172.4469 | 169.5422 | 167.4814 | 167.5934 | 167.2691 | 171.0785 | 181.386 | 190.5259 | 195.4516 | 172.4349 | 162.6246 | 157.0149 | 158.2737 | 155.694 | 155.5952 | 155.8247 | 156.5211 | 158.5943 | 165.1425 | 170.4899 | 174.0462 | 158.2967 | 170.9375 | 173.8589 | 196.6386 | 228.2622 | 305.8604 | 385.9058 | 460.1667 | 526.2814 | 583.9014 | 638.6402 | 688.3216
Lindisfarne |  | 25305 | 60.3766 | 48.0402 | 49.4002 | 49.2483 | 48.4188 | 47.8303 | 47.8622 | 47.7696 | 48.8576 | 51.8012 | 54.4114 | 55.8182 | 90.1584 | 80.2913 | 77.5217 | 78.1432 | 76.8696 | 76.8208 | 76.9341 | 77.2779 | 78.3015 | 81.5345 | 84.1746 | 85.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25307 | 117.7657 | 89.109 | 91.6315 | 91.3499 | 89.8112 | 88.7195 | 88.7788 | 88.607 | 90.625 | 96.0852 | 100.9268 | 103.5361 | 167.7529 | 156.1493 | 150.763 | 151.9716 | 149.4947 | 149.3998 | 149.6201 | 150.2889 | 152.2795 | 158.567 | 163.7014 | 167.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25308 | 96.7784 | 86.9337 | 89.3946 | 89.1199 | 87.6187 | 86.5537 | 86.6116 | 86.444 | 88.4127 | 93.7396 | 98.463 | 101.0086 | 164.2691 | 152.6224 | 147.3577 | 148.5391 | 146.1181 | 146.0253 | 146.2407 | 146.8943 | 148.84 | 154.9855 | 160.0039 | 163.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25309 | 115.1603 | 98.4796 | 101.2673 | 100.9561 | 99.2556 | 98.0491 | 98.1147 | 97.9248 | 100.155 | 106.1893 | 111.5401 | 114.4238 | 146.6728 | 137.9741 | 133.2147 | 134.2827 | 132.0941 | 132.0102 | 132.2049 | 132.7958 | 134.5547 | 140.1104 | 144.6472 | 147.6644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25310 | 55.6547 | 51.1341 | 52.5816 | 52.42 | 51.5371 | 50.9106 | 50.9447 | 50.8461 | 52.0041 | 55.1373 | 57.9156 | 59.4129 | 96.1575 | 83.9633 | 81.067 | 81.7169 | 80.385 | 80.334 | 80.4525 | 80.8121 | 81.8825 | 85.2633 | 88.0241 | 89.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank |  | 45001 | 79 | 75.8989 | 78.0475 | 77.8076 | 76.497 | 75.5671 | 75.6177 | 75.4714 | 77.1902 | 81.8409 | 85.9647 | 88.1872 | 25.903 | 30.741 | 29.6806 | 29.9186 | 29.4309 | 29.4122 | 29.4556 | 29.5873 | 29.9792 | 31.217 | 32.2278 | 32.9 | 20.808 | 29.7404 | 33.3308 | 38.4259 | 46.436 | 65.6251 | 84.9793 | 102.5974 | 118.0745 | 131.4831 | 144.2581 | 156.4261
Meadowbank |  | 45002 | 75 | 73.9619 | 76.0557 | 75.8219 | 74.5448 | 73.6387 | 73.6879 | 73.5453 | 75.2203 | 79.7523 | 83.7709 | 85.9367 | 65 | 61.3288 | 59.2132 | 59.6879 | 58.7151 | 58.6778 | 58.7644 | 59.027 | 59.8089 | 62.2783 | 64.2949 | 65.6361 | 22.2352 | 22.2352 | 24.89 | 48.5258 | 86.954 | 182.3044 | 282.0276 | 376.2696 | 462.3181 | 539.846 | 616.5665 | 692.1847
Meadowbank |  | 45003 | 113 | 133.4913 | 137.2702 | 136.8483 | 134.5432 | 132.9078 | 132.9967 | 132.7394 | 135.7624 | 143.9421 | 151.1952 | 155.1041 | 77.2605 | 38.3055 | 36.9842 | 37.2807 | 36.6731 | 36.6498 | 36.7038 | 36.8679 | 37.3562 | 38.8986 | 40.1582 | 40.9958 | 51.7037 | 59.0408 | 62.4138 | 87.0436 | 126.9212 | 225.7764 | 329.2751 | 427.1423 | 516.2736 | 596.0071 | 674.0296 | 749.9312
Mornington |  | 24401 | 100.2288 | 95.825 | 98.5376 | 98.2348 | 96.5801 | 95.4062 | 95.4699 | 95.2852 | 97.4553 | 103.327 | 108.5335 | 111.3395 | 179.9288 | 150.0569 | 144.8807 | 146.0422 | 143.6619 | 143.5707 | 143.7825 | 144.4251 | 146.3381 | 152.3802 | 157.3143 | 160.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24402 | 92.0456 | 78.755 | 80.9844 | 80.7355 | 79.3756 | 78.4108 | 78.4632 | 78.3114 | 80.0949 | 84.9206 | 89.1996 | 91.5058 | 134.6321 | 129.0129 | 124.5626 | 125.5612 | 123.5147 | 123.4363 | 123.6184 | 124.1709 | 125.8156 | 131.0104 | 135.2525 | 138.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24405 | 178.6838 | 153.8267 | 158.1812 | 157.695 | 155.0388 | 153.1543 | 153.2567 | 152.9602 | 156.4437 | 165.8695 | 174.2275 | 178.7318 | 272.9969 | 261.2746 | 252.2619 | 254.2843 | 250.1398 | 249.981 | 250.3497 | 251.4687 | 254.7995 | 265.3199 | 273.911 | 279.6247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24406 | 100.1859 | 95.815 | 98.5274 | 98.2245 | 96.57 | 95.3962 | 95.46 | 95.2753 | 97.4451 | 103.3162 | 108.5222 | 111.3278 | 180.0619 | 149.7475 | 144.582 | 145.7411 | 143.3657 | 143.2747 | 143.486 | 144.1273 | 146.0364 | 152.0661 | 156.99 | 160.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mowbray |  | 62004 | 111.0486 | 83.8434 | 86.2169 | 85.9519 | 84.5041 | 83.4769 | 83.5327 | 83.3711 | 85.2698 | 90.4074 | 94.9629 | 97.418 | 204.6308 | 203.0946 | 196.0888 | 197.6609 | 194.4393 | 194.3158 | 194.6024 | 195.4722 | 198.0613 | 206.2391 | 212.9171 | 217.3585 | 734.179 | 808.4375 | 909.3219 | 994.801 | 1060.2982 | 1219.9796 | 1384.196 | 1537.0594 | 1674.9083 | 1798.0868 | 1919.7983 | 2040.9692
Mowbray |  | 62005 | 84.5833 | 74.3949 | 76.5009 | 76.2657 | 74.9811 | 74.0697 | 74.1192 | 73.9758 | 75.6606 | 80.2191 | 84.2613 | 86.4397 | 149.1 | 149.1822 | 144.0362 | 145.1909 | 142.8245 | 142.7338 | 142.9443 | 143.5832 | 145.4851 | 151.492 | 156.3973 | 159.6597 | 269.4376 | 307.3521 | 344.078 | 390.4606 | 452.3569 | 606.0983 | 767.1113 | 919.5103 | 1058.7875 | 1184.1455 | 1307.6404 | 1428.31
Mowbray |  | 62006 | 98.6586 | 71.8231 | 73.8563 | 73.6293 | 72.3891 | 71.5092 | 71.557 | 71.4185 | 73.045 | 77.446 | 81.3484 | 83.4515 | 132.2445 | 126.6308 | 122.2627 | 123.2428 | 121.2342 | 121.1572 | 121.3359 | 121.8782 | 123.4925 | 128.5914 | 132.7552 | 135.5244 | 258.5037 | 323.4958 | 382.4777 | 440.3965 | 497.5944 | 635.2106 | 773.6506 | 898.3902 | 1005.9974 | 1096.821 | 1180.4343 | 1256.8114
Mowbray |  | 62008 | 65.5314 | 160.1278 | 164.6607 | 164.1546 | 161.3896 | 159.4279 | 159.5345 | 159.2258 | 162.852 | 172.6639 | 181.3642 | 186.0531 | 110.2836 | 113.084 | 109.1832 | 110.0585 | 108.2647 | 108.196 | 108.3556 | 108.8399 | 110.2815 | 114.8349 | 118.5533 | 121.0263 | 305.6246 | 363.1643 | 398.3322 | 467.8619 | 537.6611 | 708.0841 | 883.8113 | 1047.8175 | 1195.7766 | 1327.3542 | 1455.5754 | 1579.7494
Mowbray |  | 62009 | 116.2486 | 96.2747 | 99.0001 | 98.6958 | 97.0333 | 95.8539 | 95.918 | 95.7324 | 97.9126 | 103.8119 | 109.0428 | 111.862 | 135.4389 | 124.7059 | 120.4042 | 121.3694 | 119.3913 | 119.3155 | 119.4915 | 120.0255 | 121.6153 | 126.6367 | 130.7372 | 133.4643 | 189.076 | 205.7728 | 236.9439 | 266.0744 | 314.5967 | 438.1392 | 570.5842 | 698.2786 | 816.2224 | 922.5281 | 1026.5147 | 1126.7621
Mowbray |  | 62010 | 69.3183 | 89.6176 | 92.1545 | 91.8713 | 90.3238 | 89.2259 | 89.2856 | 89.1128 | 91.1423 | 96.6336 | 101.5029 | 104.1271 | 121.4816 | 122.8104 | 118.5741 | 119.5247 | 117.5766 | 117.502 | 117.6753 | 118.2012 | 119.7669 | 124.7119 | 128.7501 | 131.4358 | 309.8897 | 356.3833 | 394.1357 | 451.9023 | 530.1729 | 723.5148 | 925.2901 | 1116.403 | 1292.3772 | 1453.416 | 1616.3458 | 1781.3564
Mowbray |  | 62013 | 140.5318 | 135.3623 | 139.1942 | 138.7664 | 136.429 | 134.7707 | 134.8608 | 134.5999 | 137.6653 | 145.9596 | 153.3144 | 157.2781 | 192.7691 | 185.3814 | 178.9867 | 180.4216 | 177.481 | 177.3683 | 177.6299 | 178.4239 | 180.7872 | 188.2517 | 194.3473 | 198.4013 | 118.0174 | 172.4863 | 179.2939 | 230.2669 | 279.2814 | 397.2249 | 516.9895 | 627.2881 | 726.1156 | 814.5239 | 903.004 | 993.5884
NA |  | 14072 | 22.2364 | 16.5597 | 17.0285 | 16.9762 | 16.6902 | 16.4873 | 16.4984 | 16.4664 | 16.8415 | 17.8562 | 18.7559 | 19.2408 | 24.9291 | 19.2603 | 23.4823 | 30.7363 | 30.2353 | 30.2161 | 30.2607 | 30.3959 | 30.7985 | 32.0702 | 33.1086 | 33.7992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 37001 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 39564 | 10.5 | 10.5 | 10.7972 | 10.7641 | 10.5827 | 10.4541 | 10.4611 | 10.4409 | 10.6786 | 11.322 | 11.8925 | 12.2 | 10.5 | 22.2191 | 49.8444 | 50.244 | 49.4251 | 49.3937 | 49.4666 | 49.6877 | 50.3458 | 52.4246 | 54.1221 | 55.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 39566 | 0 | 100.8856 | 103.7415 | 103.4226 | 101.6805 | 100.4446 | 100.5117 | 100.3173 | 102.6019 | 108.7837 | 114.2652 | 117.2193 | 0 | 77.2325 | 102.9602 | 103.7856 | 102.094 | 102.0292 | 102.1797 | 102.6364 | 103.9959 | 108.2898 | 111.7962 | 114.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 49302 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
NA |  | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 84121 | 39.6 | 36.0643 | 37.0853 | 36.9713 | 36.3485 | 35.9067 | 35.9307 | 35.8612 | 36.6779 | 38.8878 | 40.8473 | 41.9033 | 51.3942 | 50.1063 | 48.3779 | 48.7658 | 47.9709 | 47.9405 | 48.0112 | 48.2258 | 48.8646 | 50.8821 | 52.5297 | 53.6254 | 225.8866 | 247.1632 | 265.0574 | 311.604 | 378.093 | 539.6466 | 704.8 | 856.9938 | 992.1262 | 1110.2098 | 1223.3548 | 1328.8402
NA |  | 84122 | 27.9515 | 5.4045 | 5.5575 | 5.5404 | 5.4471 | 5.3809 | 5.3845 | 5.3741 | 5.4965 | 5.8276 | 6.1213 | 6.2795 | 28.2734 | 8.6789 | 8.3795 | 8.4467 | 8.309 | 8.3037 | 8.316 | 8.3532 | 8.4638 | 8.8133 | 9.0986 | 9.2884 | 3 | 3 | 3 | 7.4495 | 14.5687 | 31.9218 | 49.7198 | 66.1829 | 80.8663 | 93.7699 | 106.2285 | 118.2421
NA |  | 18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.416 | 33.3947 | 33.444 | 33.5935 | 34.0384 | 35.4439 | 36.5915 | 37.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.416 | 33.3947 | 33.444 | 33.5935 | 34.0384 | 35.4439 | 36.5915 | 37.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk |  | 39010 | 46.7 | 47.7011 | 49.0514 | 48.9006 | 48.0769 | 47.4926 | 47.5243 | 47.4324 | 48.5126 | 51.4355 | 54.0273 | 55.424 | 82.43 | 77.2668 | 74.6015 | 75.1996 | 73.974 | 73.927 | 74.036 | 74.3669 | 75.352 | 78.4632 | 81.0038 | 82.6935 | 257.9005 | 285.6999 | 324.4826 | 382.0516 | 432.6129 | 555.2891 | 680.2368 | 794.7892 | 895.9754 | 984.113 | 1068.6181 | 1149.7549
New Norfolk |  | 39011 | 47.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4223 | 0 | 28.3918 | 28.6194 | 28.153 | 28.1351 | 28.1766 | 28.3025 | 28.6774 | 29.8614 | 30.8284 | 31.4714 | 157.1768 | 188.0828 | 212.5719 | 239.0743 | 282.5468 | 391.6442 | 507.1764 | 617.577 | 719.0307 | 810.302 | 899.5713 | 980.6756
New Norfolk |  | 39012 | 56.6675 | 39.0518 | 40.1573 | 40.0338 | 39.3595 | 38.8811 | 38.9071 | 38.8318 | 39.7162 | 42.1091 | 44.2309 | 45.3744 | 25.3897 | 68.6956 | 66.3259 | 66.8577 | 65.768 | 65.7262 | 65.8232 | 66.1174 | 66.9931 | 69.7592 | 72.018 | 73.5203 | 65.7996 | 65.7996 | 78.476 | 102.1319 | 137.357 | 226.3421 | 319.7983 | 407.2988 | 485.5103 | 553.8239 | 618.8712 | 680.257
New Norfolk |  | 39013 | 56.6 | 53.7068 | 55.2271 | 55.0573 | 54.13 | 53.472 | 53.5077 | 53.4042 | 54.6205 | 57.9114 | 60.8294 | 62.4021 | 25.3897 | 87.7717 | 84.744 | 85.4234 | 84.0311 | 83.9778 | 84.1017 | 84.4775 | 85.5965 | 89.1307 | 92.0167 | 93.9362 | 208.0972 | 216.548 | 249.4023 | 272.2186 | 302.6605 | 376.4097 | 451.3269 | 519.6594 | 579.484 | 630.8888 | 679.2698 | 724.6649
NewNorfolk |  | 39565 | 44.2728 | 89.8604 | 92.4042 | 92.1202 | 90.5685 | 89.4676 | 89.5275 | 89.3543 | 91.3892 | 96.8954 | 101.7779 | 104.4092 | 69.8026 | 146.643 | 169.9764 | 171.339 | 168.5465 | 168.4395 | 168.6879 | 169.4419 | 171.6862 | 178.7749 | 184.5637 | 188.4136 | 424.245 | 465.5004 | 518.5152 | 587.6257 | 676.0281 | 890.5101 | 1109.7957 | 1312.464 | 1493.733 | 1653.774 | 1810.5639 | 1965.0714
NewNorfolk |  | 39568 | 25.8739 | 19.1166 | 19.6577 | 19.5973 | 19.2672 | 19.033 | 19.0457 | 19.0089 | 19.4418 | 20.6132 | 21.6518 | 22.2116 | 28.1123 | 27.1526 | 26.216 | 26.4262 | 25.9955 | 25.979 | 26.0173 | 26.1336 | 26.4797 | 27.573 | 28.4659 | 29.0597 | 217.625 | 228.2665 | 233.1543 | 259.1053 | 300.1891 | 399.8488 | 502.4355 | 598.7132 | 686.9108 | 767.4586 | 848.9774 | 929.7207
NewNorfolk |  | 39569 | 23.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 25.577 | 24.6947 | 24.8927 | 24.487 | 24.4714 | 24.5075 | 24.617 | 24.9431 | 25.973 | 26.814 | 27.3733 | 0 | 0 | 0 | 0.24245 | 0.63038 | 1.576 | 2.5458 | 3.4428 | 4.2429 | 4.9461 | 5.6249 | 6.2796
NewNorfolk |  | 39570 | 124.2161 | 26.12 | 26.8594 | 26.7768 | 26.3258 | 26.0058 | 26.0232 | 25.9728 | 26.5644 | 28.1649 | 29.5841 | 30.3489 | 102.1686 | 23.3293 | 22.5246 | 22.7051 | 22.3351 | 22.3209 | 22.3538 | 22.4537 | 22.7511 | 23.6905 | 24.4576 | 24.9678 | 26.65 | 26.65 | 26.65 | 31.3575 | 39.2787 | 59.5204 | 81.1026 | 101.6028 | 120.1189 | 136.3776 | 151.8827 | 166.523
NewNorfolk |  | 39571 | 116.9 | 94.3841 | 97.0559 | 96.7576 | 95.1278 | 93.9715 | 94.0344 | 93.8524 | 95.9898 | 101.7732 | 106.9015 | 109.6652 | 88.5671 | 58.0548 | 56.0522 | 56.5016 | 55.5807 | 55.5454 | 55.6274 | 55.876 | 56.6161 | 58.9537 | 60.8626 | 62.1322 | 84.5894 | 98.6034 | 102.267 | 124.7381 | 161.5396 | 253.8589 | 351.5997 | 444.895 | 530.4525 | 606.9688 | 681.9715 | 753.8633
Newton | Risdon | 96202 | 110.4845 | 95.3895 | 98.0898 | 97.7883 | 96.1412 | 94.9725 | 95.036 | 94.8522 | 97.0124 | 102.8574 | 108.0402 | 110.8334 | 115.8333 | 103.7322 | 100.154 | 100.9569 | 99.3115 | 99.2484 | 99.3948 | 99.839 | 101.1615 | 105.3383 | 108.7492 | 111.0176 | 49 | 49 | 49 | 64.6898 | 89.5848 | 149.3947 | 209.4217 | 263.3193 | 309.5852 | 348.3779 | 383.8038 | 415.8468
North Hobart |  | 18131A | 158 | 95.0518 | 97.7426 | 97.4422 | 95.8009 | 94.6364 | 94.6996 | 94.5164 | 96.669 | 102.4933 | 107.6578 | 110.4411 | 178.5728 | 158.3843 | 152.9208 | 154.1468 | 151.6344 | 151.5381 | 151.7616 | 152.4399 | 154.4591 | 160.8365 | 166.0445 | 169.5081 | 5 | 5 | 5 | 16.8605 | 37.2348 | 91.2917 | 152.2312 | 214.4423 | 275.5923 | 334.5174 | 396.533 | 461.4642
North Hobart |  | 18131B | 173.0051 | 153.6593 | 158.0092 | 157.5235 | 154.8702 | 152.9877 | 153.09 | 152.7938 | 156.2735 | 165.689 | 174.0379 | 178.5374 | 206.7787 | 174.4993 | 168.48 | 169.8306 | 167.0626 | 166.9566 | 167.2028 | 167.9501 | 170.1747 | 177.2011 | 182.9389 | 186.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18132A | 0 | 50.3939 | 51.8204 | 51.6611 | 50.791 | 50.1736 | 50.2071 | 50.11 | 51.2512 | 54.3391 | 57.0772 | 58.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18132B | 49.8 | 41.654 | 42.8332 | 42.7015 | 41.9823 | 41.472 | 41.4997 | 41.4194 | 42.3627 | 44.915 | 47.1783 | 48.398 | 50.9551 | 38.6877 | 37.3531 | 37.6526 | 37.0389 | 37.0154 | 37.07 | 37.2357 | 37.7289 | 39.2867 | 40.5588 | 41.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18133A | 45 | 74.5461 | 76.6564 | 76.4207 | 75.1335 | 74.2203 | 74.2699 | 74.1262 | 75.8143 | 80.3822 | 84.4325 | 86.6154 | 45.0664 | 37.2622 | 35.9768 | 36.2653 | 35.6742 | 35.6515 | 35.7041 | 35.8637 | 36.3387 | 37.8391 | 39.0644 | 39.8792 | 0 | 0 | 0 | 4.4357 | 12.4847 | 35.5685 | 64.2993 | 97.1525 | 133.4961 | 172.6877 | 218.1346 | 269.3588
North Hobart |  | 18133B | 35.8984 | 23.4107 | 24.0734 | 23.9994 | 23.5951 | 23.3083 | 23.3239 | 23.2788 | 23.809 | 25.2434 | 26.5154 | 27.2009 | 56.7327 | 42.4236 | 40.9602 | 41.2886 | 40.6156 | 40.5898 | 40.6497 | 40.8314 | 41.3722 | 43.0804 | 44.4754 | 45.4031 | 68.1579 | 77.2137 | 83.1924 | 103.7175 | 129.7592 | 190.5796 | 249.8839 | 301.675 | 345.0318 | 380.6232 | 412.5832 | 441.1464
North Hobart |  | 18134A | 42.0111 | 35.7668 | 36.7792 | 36.6662 | 36.0486 | 35.6104 | 35.6342 | 35.5653 | 36.3753 | 38.5669 | 40.5102 | 41.5575 | 66.1345 | 60.4675 | 58.3817 | 58.8497 | 57.8905 | 57.8538 | 57.9391 | 58.1981 | 58.9689 | 61.4037 | 63.392 | 64.7143 | 59.1449 | 70.0487 | 77.1234 | 83.6367 | 94.0155 | 119.0654 | 144.3364 | 167.1608 | 186.8875 | 203.56 | 218.9211 | 232.9561
North Hobart |  | 18134B | 30.1878 | 17.5474 | 18.0442 | 17.9887 | 17.6857 | 17.4707 | 17.4824 | 17.4486 | 17.846 | 18.9212 | 19.8746 | 20.3884 | 51.9148 | 42.2833 | 40.8247 | 41.152 | 40.4813 | 40.4556 | 40.5152 | 40.6963 | 41.2354 | 42.9379 | 44.3283 | 45.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.7584 | 178.0744 | 219.7683 | 245.9584 | 273.0125 | 338.2516 | 404.01 | 463.3533 | 514.6027 | 557.8854 | 597.7356 | 634.1216
North Hobart |  | 18135B | 76.9883 | 70.0551 | 72.0382 | 71.8168 | 70.6071 | 69.7489 | 69.7955 | 69.6604 | 71.2469 | 75.5395 | 79.3459 | 81.3973 | 128.6887 | 98.127 | 94.7421 | 95.5017 | 93.9451 | 93.8855 | 94.0239 | 94.4442 | 95.6951 | 99.6463 | 102.8729 | 105.0187 | 125.3247 | 135.931 | 138.8985 | 175.648 | 199.4522 | 257.3318 | 316.1651 | 369.6932 | 416.2717 | 455.8769 | 492.5578 | 526.2205
North Hobart |  | 18136A | 62.9714 | 40.2243 | 41.363 | 41.2359 | 40.5413 | 40.0485 | 40.0753 | 39.9977 | 40.9086 | 43.3734 | 45.5589 | 46.7368 | 114.4323 | 108.4125 | 104.6728 | 105.512 | 137.2082 | 137.1211 | 137.3234 | 137.9372 | 139.7642 | 145.5349 | 150.2474 | 153.3815 | 40.1356 | 61.4556 | 99.4423 | 143.7229 | 173.3235 | 249.1716 | 332.8212 | 418.0617 | 503.7282 | 590.1218 | 687.0333 | 796.3812
North Hobart |  | 18141B | 136.3688 | 139.1014 | 143.0392 | 142.5995 | 140.1976 | 138.4934 | 138.586 | 138.3179 | 141.468 | 149.9914 | 157.5493 | 161.6225 | 184.2653 | 181.8268 | 175.5547 | 176.9621 | 207.4938 | 207.3621 | 207.6679 | 208.5961 | 211.359 | 220.0858 | 227.2123 | 231.9518 | 25.3393 | 30.1538 | 38.2953 | 43.0323 | 50.5805 | 68.7986 | 87.1775 | 103.7771 | 118.1238 | 130.2492 | 141.4209 | 151.6282
North Hobart |  | 18142A | 20.3704 | 15.1184 | 15.5464 | 15.4986 | 15.2375 | 15.0523 | 15.0624 | 15.0332 | 15.3756 | 16.302 | 17.1234 | 17.5661 | 33.9027 | 29.4033 | 28.389 | 28.6166 | 28.1502 | 28.1323 | 28.1738 | 28.2998 | 28.6746 | 29.8585 | 30.8254 | 31.4684 | 0 | 0 | 0 | 0.47823 | 1.5916 | 5.5191 | 11.2695 | 18.7017 | 27.7075 | 38.1062 | 50.8105 | 65.709
North Hobart |  | 18142B | 32.0712 | 27.17 | 27.9392 | 27.8533 | 27.3841 | 27.0513 | 27.0694 | 27.017 | 27.6323 | 29.2971 | 30.7734 | 31.569 | 43.7114 | 37.1042 | 35.8243 | 36.1115 | 35.5229 | 35.5003 | 35.5527 | 35.7116 | 36.1846 | 37.6786 | 38.8987 | 39.7101 | 109.7499 | 116.7538 | 147.4535 | 166.3447 | 180.8394 | 217.3349 | 256.4373 | 294.9014 | 332.3575 | 369.5442 | 411.6152 | 460.6644
North Hobart |  | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.5204 | 728.0648 | 833.2577 | 903.9928 | 976.2374 | 1150.934 | 1327.9328 | 1488.9958 | 1629.7716 | 1750.5734 | 1863.9998 | 1969.9244
North Hobart |  | 18143B | 148.2572 | 94.1795 | 96.8455 | 96.5479 | 94.9216 | 93.7678 | 93.8305 | 93.649 | 95.7818 | 101.5526 | 106.6697 | 109.4275 | 263.2392 | 229.0104 | 221.1108 | 222.8834 | 219.2507 | 219.1115 | 219.4347 | 220.4154 | 223.3349 | 232.5562 | 240.0864 | 245.0945 | 97.0245 | 128.5019 | 173.5014 | 189.0204 | 207.3083 | 250.7803 | 293.9891 | 332.4776 | 365.3329 | 392.8073 | 417.9004 | 440.6696
North Hobart |  | 18144A | 64.3699 | 37.6158 | 38.6807 | 38.5618 | 37.9123 | 37.4514 | 37.4765 | 37.404 | 38.2558 | 40.5607 | 42.6045 | 43.706 | 118.1078 | 106.47 | 102.7974 | 103.6215 | 101.9326 | 101.8679 | 102.0181 | 102.4741 | 103.8314 | 108.1185 | 111.6194 | 113.9477 | 483.9383 | 589.4019 | 639.3161 | 718.2215 | 765.7772 | 879.9135 | 994.4295 | 1097.3173 | 1185.7975 | 1260.2235 | 1328.4854 | 1390.5856
North Hobart |  | 18144B | 87.2078 | 70.9893 | 72.9989 | 72.7745 | 71.5487 | 70.679 | 70.7263 | 70.5895 | 72.1971 | 76.547 | 80.4041 | 82.4828 | 207.6075 | 147.6451 | 142.5521 | 143.6949 | 141.3529 | 141.2632 | 141.4715 | 142.1039 | 143.9861 | 149.9311 | 154.7859 | 158.0147 | 32.5018 | 41.9273 | 45.7008 | 54.5654 | 63.5939 | 85.3891 | 107.3835 | 127.2579 | 144.4458 | 158.9843 | 172.3928 | 184.6589
North Hobart |  | 18145A | 49.9983 | 34.5626 | 35.541 | 35.4318 | 34.835 | 34.4115 | 34.4345 | 34.3679 | 35.1506 | 37.2685 | 39.1464 | 40.1584 | 66.6123 | 57.1594 | 55.1877 | 55.6301 | 54.7234 | 54.6887 | 54.7693 | 55.0141 | 55.7428 | 58.0444 | 59.9239 | 61.1738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.3914 | 349.0811 | 379.1786 | 418.1648 | 450.7281 | 528.9664 | 607.5611 | 678.2723 | 739.1757 | 790.4942 | 837.6546 | 880.6523
North Hobart |  | 18146A | 117.3616 | 77.4322 | 79.6242 | 79.3794 | 78.0424 | 77.0937 | 77.1453 | 76.996 | 78.7496 | 83.4942 | 87.7014 | 89.9688 | 188.6115 | 178.656 | 172.4933 | 173.8761 | 171.0422 | 170.9336 | 171.1857 | 171.9508 | 174.2284 | 181.4221 | 187.2966 | 191.2035 | 1045.6764 | 1266.54 | 1481.5708 | 1630.9011 | 1736.7186 | 1990.3186 | 2244.3636 | 2472.267 | 2667.9998 | 2832.477 | 2983.2367 | 3120.3535
North Hobart |  | 18146B | 172.376 | 112.1189 | 115.2928 | 114.9384 | 113.0024 | 111.6289 | 111.7035 | 111.4874 | 114.0264 | 120.8965 | 126.9883 | 130.2714 | 346.9505 | 284.748 | 274.9257 | 277.1297 | 272.6129 | 272.4398 | 272.8416 | 274.0611 | 277.6912 | 289.1567 | 298.5197 | 304.7467 | 36.2208 | 39.1008 | 43.4593 | 53.3228 | 67.9925 | 100.7871 | 131.2712 | 156.5854 | 176.7201 | 192.4407 | 205.9066 | 217.4334
Norwood |  | 65060 | 9 | 9.2048 | 9.4654 | 9.4363 | 9.2774 | 9.1646 | 9.1707 | 9.153 | 9.3614 | 9.9254 | 10.4256 | 10.6951 | 8.0092 | 9 | 8.6895 | 8.7592 | 8.6164 | 8.611 | 8.6237 | 8.6622 | 8.777 | 9.1393 | 9.4353 | 9.6321 | 329.3452 | 392.3245 | 446.5208 | 495.6722 | 558.6456 | 708.4635 | 857.4956 | 990.3214 | 1103.7197 | 1198.5026 | 1284.9745 | 1363.3036
Norwood |  | 65061 | 116 | 119 | 122.3687 | 121.9926 | 119.9377 | 118.4799 | 118.5591 | 118.3297 | 121.0246 | 128.3163 | 134.782 | 138.2666 | 107.0726 | 106 | 102.3435 | 103.164 | 101.4826 | 101.4182 | 101.5677 | 102.0217 | 103.373 | 107.6412 | 111.1266 | 113.4447 | 479.8046 | 566.7689 | 675.6808 | 755.6804 | 838.0014 | 1038.526 | 1243.8501 | 1433.0197 | 1600.4705 | 1745.914 | 1884.1597 | 2015.1952
Norwood |  | 65062 | 0 | 70.1869 | 72.1738 | 71.9519 | 70.74 | 69.8801 | 69.9268 | 69.7915 | 71.381 | 75.6817 | 79.4952 | 81.5504 | 0 | 133.8903 | 129.2717 | 130.3081 | 128.1842 | 128.1029 | 128.2918 | 128.8652 | 130.5721 | 135.9633 | 140.3658 | 143.2938 | 315.6522 | 410.6178 | 508.197 | 527.7843 | 551.5758 | 608.3206 | 664.9239 | 715.5123 | 758.8138 | 795.0901 | 828.249 | 858.332
Norwood |  | 65063 | 0 | 26.024 | 26.7607 | 26.6784 | 26.2291 | 25.9103 | 25.9276 | 25.8774 | 26.4667 | 28.0614 | 29.4754 | 30.2374 | 0 | 54.0918 | 52.2259 | 52.6446 | 51.7866 | 51.7537 | 51.83 | 52.0617 | 52.7512 | 54.9293 | 56.7079 | 57.8908 | 645.0531 | 726.3325 | 806.6939 | 865.2751 | 920.463 | 1053.2957 | 1186.8755 | 1307.0372 | 1410.3561 | 1497.1257 | 1576.4785 | 1648.3813
Norwood |  | 65064 | 0 | 40.2561 | 41.3957 | 41.2685 | 40.5733 | 40.0802 | 40.1069 | 40.0294 | 40.941 | 43.4077 | 45.595 | 46.7737 | 0 | 97.2758 | 93.9203 | 94.6732 | 93.1302 | 93.071 | 93.2083 | 93.6249 | 94.865 | 98.7819 | 101.9805 | 104.1078 | 833.9814 | 940.1543 | 1031.3221 | 1121.616 | 1176.8886 | 1310.4639 | 1446.2381 | 1570.8581 | 1681.4757 | 1778.6033 | 1872.5622 | 1963.3856
Norwood |  | 65065 | 143.5679 | 56.4978 | 58.0972 | 57.9186 | 56.943 | 56.2509 | 56.2885 | 56.1796 | 57.459 | 60.9209 | 63.9907 | 65.6451 | 196.5653 | 180.9538 | 174.7119 | 176.1125 | 173.2421 | 173.1321 | 173.3875 | 174.1624 | 176.4693 | 183.7555 | 189.7056 | 193.6627 | 496.6688 | 520.4243 | 621.8424 | 679.4093 | 759.5477 | 954.7079 | 1154.0051 | 1336.9728 | 1498.6604 | 1639.5565 | 1774.9398 | 1905.7079
Norwood |  | 65066 | 92.2046 | 103.5581 | 106.4896 | 106.1623 | 104.3741 | 103.1054 | 103.1744 | 102.9748 | 105.3199 | 111.6655 | 117.2922 | 120.3246 | 143.2829 | 117.8757 | 113.8096 | 114.722 | 112.8522 | 112.7806 | 112.9469 | 113.4517 | 114.9545 | 119.7008 | 123.5767 | 126.1545 | 252.144 | 319.6896 | 350.2393 | 389.0191 | 423.5158 | 507.0566 | 592.3658 | 671.1165 | 741.37 | 803.224 | 863.0625 | 920.7774
Norwood |  | 65067 | 55.5077 | 49.7448 | 51.153 | 50.9958 | 50.1368 | 49.5274 | 49.5605 | 49.4646 | 50.5911 | 53.6393 | 56.3421 | 57.7987 | 72.0058 | 70.0091 | 67.5942 | 68.136 | 67.0255 | 66.983 | 67.0818 | 67.3816 | 68.2741 | 71.0931 | 73.3951 | 74.9261 | 0 | 0 | 0 | 0.37167 | 0.96635 | 2.4159 | 3.9026 | 5.2778 | 6.5043 | 7.5821 | 8.6228 | 9.6263
Palmerston |  | 51001 | 27.9015 | 0.19278 | 0.19824 | 0.19763 | 0.1943 | 0.19194 | 0.19207 | 0.1917 | 0.19606 | 0.20788 | 0.21835 | 0.224 | 30.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0385 | 79.7824 | 96.6004 | 119.8266 | 157.0271 | 247.9895 | 341.6681 | 428.5923 | 506.1159 | 573.8984 | 638.6115 | 699.4132
Palmerston |  | 51002 | 9.2224 | 0.10942 | 0.11252 | 0.11217 | 0.11028 | 0.10894 | 0.10901 | 0.1088 | 0.11128 | 0.11798 | 0.12393 | 0.12713 | 8.2845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9057 | 25.7547 | 64.3869 | 104.0095 | 140.6605 | 173.3492 | 202.0757 | 229.8116 | 256.5569
Palmerston |  | 51003 | 272.9973 | 211.4144 | 217.3992 | 216.731 | 213.0804 | 210.4903 | 210.6311 | 210.2236 | 215.0112 | 227.9657 | 239.4526 | 245.6433 | 206.018 | 107.1187 | 103.4236 | 104.2528 | 102.5536 | 102.4885 | 102.6396 | 103.0984 | 104.464 | 108.7772 | 112.2994 | 114.6419 | 119.7902 | 128.6051 | 151.0979 | 186.4083 | 225.4577 | 318.9328 | 412.8587 | 497.7842 | 571.6753 | 634.9149 | 694.2918 | 749.9194
Palmerston |  | 51004 | 96.6002 | 198.558 | 204.1789 | 203.5513 | 200.1227 | 197.6902 | 197.8223 | 197.4396 | 201.9361 | 214.1028 | 224.8912 | 230.7054 | 38.3974 | 83.9625 | 81.0662 | 81.7161 | 80.3843 | 80.3332 | 80.4517 | 80.8113 | 81.8817 | 85.2625 | 88.0233 | 89.8594 | 127.2226 | 150.6878 | 158.5526 | 201.9511 | 255.3275 | 387.4765 | 525.5205 | 655.7829 | 774.2564 | 880.0679 | 983.1703 | 1078.8317
Port Latta |  | 94001 | 114.8 | 108.5933 | 111.6674 | 111.3242 | 109.4491 | 108.1187 | 108.191 | 107.9816 | 110.4408 | 117.0949 | 122.9952 | 126.175 | 66.9709 | 59.8386 | 57.7745 | 58.2377 | 57.2885 | 57.2521 | 57.3365 | 57.5928 | 58.3556 | 60.7651 | 62.7327 | 64.0413 | 522.5316 | 600.3608 | 669.2858 | 774.651 | 889.1623 | 1173.5869 | 1472.6235 | 1757.9277 | 2021.9022 | 2263.5658 | 2506.8971 | 2745.6119
Port Latta |  | 94002 | 190 | 197.2966 | 202.8817 | 202.2581 | 198.8513 | 196.4342 | 196.5655 | 196.1852 | 200.6532 | 212.7425 | 223.4624 | 229.2397 | 130.8172 | 176.6174 | 170.525 | 171.8921 | 169.0905 | 168.9831 | 169.2324 | 169.9888 | 172.2403 | 179.352 | 185.1594 | 189.0218 | 55.435 | 58.8753 | 64.0365 | 84.8639 | 120.2027 | 212.1738 | 313.4961 | 414.714 | 512.6936 | 606.5239 | 705.4308 | 809.4795
Queenstown |  | 98001 | 52.2644 | 41.5856 | 42.7628 | 42.6314 | 41.9133 | 41.4038 | 41.4315 | 41.3514 | 42.2931 | 44.8413 | 47.1008 | 48.3185 | 59.1292 | 58.8448 | 56.8149 | 57.2704 | 56.337 | 56.3012 | 56.3842 | 56.6362 | 57.3864 | 59.7558 | 61.6907 | 62.9776 | 142.3231 | 188.0936 | 194.6669 | 230.9889 | 270.182 | 368.32 | 472.8397 | 574.4418 | 670.765 | 761.4905 | 855.6191 | 952.8426
Queenstown |  | 98002 | 49.1613 | 39.1032 | 40.2101 | 40.0865 | 39.4113 | 38.9322 | 38.9583 | 38.8829 | 39.7684 | 42.1645 | 44.2891 | 45.4341 | 67.5717 | 65.1368 | 62.89 | 63.3941 | 62.3609 | 62.3213 | 62.4132 | 62.6922 | 63.5226 | 66.1454 | 68.2872 | 69.7116 | 78.338 | 104.2099 | 110.3468 | 128.3114 | 157.8792 | 232.0226 | 309.9784 | 383.3586 | 449.2519 | 506.7884 | 561.1639 | 611.7232
Queenstown |  | 98003 | 30.0487 | 22.7359 | 23.3795 | 23.3076 | 22.915 | 22.6365 | 22.6516 | 22.6078 | 23.1227 | 24.5158 | 25.7511 | 26.4169 | 46.5093 | 40.4536 | 39.0582 | 39.3713 | 38.7296 | 38.705 | 38.7621 | 38.9353 | 39.4511 | 41.08 | 42.4101 | 43.2948 | 435.729 | 515.3914 | 557.7259 | 632.0165 | 726.7054 | 951.6898 | 1176.267 | 1378.3461 | 1553.8698 | 1704.5352 | 1847.287 | 1982.8347
Railton |  | 85001 | 153.3534 | 118.2426 | 121.5898 | 121.2161 | 119.1743 | 117.7257 | 117.8044 | 117.5765 | 120.2542 | 127.4995 | 133.9241 | 137.3865 | 179.8661 | 144.4339 | 139.4517 | 140.5696 | 138.2785 | 138.1907 | 138.3946 | 139.0131 | 140.8544 | 146.6701 | 151.4194 | 154.5779 | 418.8944 | 439.9477 | 478.6088 | 548.2907 | 644.0061 | 875.3207 | 1110.673 | 1326.7915 | 1518.4431 | 1686.4317 | 1849.0815 | 2007.6576
Railton |  | 85002 | 170.9 | 214.3134 | 220.3803 | 219.7029 | 216.0023 | 213.3767 | 213.5193 | 213.1063 | 217.9596 | 231.0916 | 242.7361 | 249.0117 | 176.2466 | 222.5181 | 214.8424 | 216.5648 | 213.0351 | 212.8998 | 213.2138 | 214.1668 | 217.0035 | 225.9634 | 233.2801 | 238.1462 | 281.283 | 313.8152 | 323.9541 | 352.5729 | 388.8305 | 477.8995 | 570.1841 | 656.4607 | 734.1475 | 802.9234 | 869.6547 | 932.0846
Railton |  | 85003 | 86.8 | 82.6738 | 85.0141 | 84.7528 | 83.3253 | 82.3124 | 82.3674 | 82.2081 | 84.0803 | 89.1462 | 93.6381 | 96.059 | 106.7432 | 43.8028 | 42.2918 | 42.6309 | 41.936 | 41.9094 | 41.9712 | 42.1588 | 42.7172 | 44.481 | 45.9213 | 46.8792 | 71.564 | 96.495 | 103.9962 | 131.7203 | 160.3846 | 229.6004 | 299.933 | 364.3983 | 421.3842 | 471.0331 | 518.5739 | 564.0566
Railton |  | 85004 | 106.3 | 115.4497 | 118.7179 | 118.353 | 116.3595 | 114.9451 | 115.0219 | 114.7994 | 117.4138 | 124.488 | 130.7609 | 134.1415 | 67.9 | 100.9144 | 97.4334 | 98.2145 | 96.6137 | 96.5524 | 96.6948 | 97.127 | 98.4135 | 102.4769 | 105.7951 | 108.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton |  | 85005 | 317.6631 | 292.1797 | 300.4508 | 299.5274 | 294.4822 | 290.9027 | 291.0971 | 290.534 | 297.1506 | 315.0539 | 330.9292 | 339.4848 | 338.2496 | 286.5577 | 276.6729 | 278.891 | 274.3454 | 274.1713 | 274.5757 | 275.8029 | 279.456 | 290.9945 | 300.4169 | 306.6835 | 516.3141 | 564.6811 | 629.0731 | 733.7288 | 858.0279 | 1158.732 | 1464.3248 | 1744.0849 | 1991.0468 | 2205.8309 | 2412.3575 | 2612.2369
Railton |  | 85006 | 247.6 | 229.5292 | 236.0268 | 235.3013 | 231.3379 | 228.526 | 228.6787 | 228.2363 | 233.4342 | 247.4986 | 259.9698 | 266.6909 | 185.3413 | 188.6007 | 182.0949 | 183.5548 | 180.5631 | 180.4484 | 180.7146 | 181.5223 | 183.9267 | 191.5208 | 197.7223 | 201.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton |  | 85007 | 516.9818 | 382.5371 | 393.366 | 392.157 | 385.5515 | 380.8651 | 381.1196 | 380.3823 | 389.0452 | 412.4852 | 433.2699 | 444.4714 | 534.7612 | 317.3158 | 306.3701 | 308.8262 | 303.7928 | 303.5999 | 304.0477 | 305.4066 | 309.4519 | 322.2288 | 332.6627 | 339.6019 | 588.57 | 691.5437 | 798.197 | 875.343 | 970.4183 | 1200.2205 | 1434.0959 | 1649.2649 | 1840.944 | 2010.1216 | 2175.0134 | 2336.0997
Railton |  | 85008 | 110.7393 | 99.7532 | 102.577 | 102.2618 | 100.5393 | 99.3172 | 99.3836 | 99.1913 | 101.4503 | 107.5627 | 112.9827 | 115.9037 | 178.4351 | 162.4409 | 156.8375 | 158.0949 | 155.5182 | 155.4194 | 155.6487 | 156.3443 | 158.4152 | 164.956 | 170.2973 | 173.8496 | 83.9879 | 90.4084 | 99.4262 | 112.8903 | 129.405 | 170.6359 | 213.6473 | 253.6888 | 289.1728 | 319.7337 | 348.2575 | 374.5198
Richmond |  | 40001 | 27.2333 | 24.4617 | 25.1541 | 25.0768 | 24.6544 | 24.3547 | 24.371 | 24.3239 | 24.8778 | 26.3767 | 27.7058 | 28.4221 | 36.8226 | 37.6015 | 36.3044 | 36.5955 | 35.999 | 35.9761 | 36.0292 | 36.1902 | 36.6696 | 38.1836 | 39.42 | 40.2423 | 181.0362 | 200.9374 | 211.2904 | 249.1241 | 302.9018 | 434.0703 | 568.4961 | 692.4853 | 802.5404 | 898.6967 | 991.0403 | 1079.8185
Richmond |  | 40002 | 94.4 | 91.1811 | 93.7623 | 93.4741 | 91.8996 | 90.7826 | 90.8433 | 90.6675 | 92.7324 | 98.3195 | 103.2737 | 105.9437 | 122.4163 | 127.4894 | 123.0917 | 124.0785 | 122.0562 | 121.9787 | 122.1586 | 122.7046 | 124.3299 | 129.4633 | 133.6554 | 136.4434 | 66.5525 | 68.1372 | 75.6271 | 84.2184 | 97.7419 | 129.0955 | 161.2084 | 190.784 | 216.9705 | 239.7592 | 261.5083 | 282.2174
Richmond |  | 40003 | 40.1667 | 36.8133 | 37.8555 | 37.7391 | 37.1034 | 36.6524 | 36.6769 | 36.606 | 37.4396 | 39.6954 | 41.6956 | 42.7736 | 46.1729 | 69.2368 | 66.8485 | 67.3844 | 66.2861 | 66.2441 | 66.3418 | 66.6383 | 67.5209 | 70.3088 | 72.5854 | 74.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11004 | 137.2486 | 147.0825 | 151.2461 | 150.7813 | 148.2415 | 146.4396 | 146.5375 | 146.254 | 149.5848 | 158.5973 | 166.5889 | 170.8957 | 169.7399 | 166.7972 | 161.0436 | 162.3346 | 159.6888 | 159.5874 | 159.8228 | 160.5372 | 162.6635 | 169.3797 | 174.8643 | 178.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11005 | 122.4005 | 150.0787 | 154.3271 | 153.8528 | 151.2613 | 149.4227 | 149.5226 | 149.2333 | 152.632 | 161.828 | 169.9824 | 174.377 | 171.7295 | 160.1568 | 154.6322 | 155.8719 | 153.3314 | 153.234 | 153.46 | 154.1459 | 156.1877 | 162.6365 | 167.9027 | 171.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11006 | 137.5959 | 151.788 | 156.0849 | 155.6051 | 152.9841 | 151.1246 | 151.2256 | 150.933 | 154.3704 | 163.6712 | 171.9184 | 176.3631 | 173.6464 | 161.3701 | 155.8036 | 157.0527 | 154.4929 | 154.3948 | 154.6226 | 155.3137 | 157.3709 | 163.8685 | 169.1746 | 172.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11021 | 133.1441 | 99.9909 | 102.8215 | 102.5055 | 100.7789 | 99.5539 | 99.6204 | 99.4277 | 101.6921 | 107.819 | 113.2519 | 116.1799 | 175.0037 | 170.881 | 164.9865 | 166.3092 | 163.5986 | 163.4947 | 163.7358 | 164.4677 | 166.6461 | 173.5267 | 179.1456 | 182.8825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11023 | 134.038 | 111.1152 | 114.2607 | 113.9095 | 111.9908 | 110.6296 | 110.7035 | 110.4894 | 113.0057 | 119.8142 | 125.8516 | 129.1053 | 210.2886 | 197.8362 | 191.0118 | 192.5431 | 189.405 | 189.2847 | 189.5639 | 190.4112 | 192.9332 | 200.8993 | 207.4044 | 211.7308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11025 | 131.5821 | 104.9667 | 107.9381 | 107.6063 | 105.7938 | 104.5079 | 104.5777 | 104.3754 | 106.7525 | 113.1843 | 118.8875 | 121.9612 | 175.2023 | 173.2654 | 167.2886 | 168.6298 | 165.8813 | 165.776 | 166.0205 | 166.7626 | 168.9714 | 175.9481 | 181.6453 | 185.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11027 | 119.2429 | 108.4635 | 111.5339 | 111.1911 | 109.3182 | 107.9894 | 108.0616 | 107.8525 | 110.3087 | 116.9549 | 122.8481 | 126.0241 | 188.9457 | 185.4949 | 179.0963 | 180.532 | 177.5896 | 177.4769 | 177.7386 | 178.5331 | 180.8978 | 188.3669 | 194.4662 | 198.5227 | 374.0307 | 464.6561 | 515.2042 | 565.1905 | 628.0559 | 782.1903 | 940.4773 | 1086.2038 | 1214.6382 | 1325.2599 | 1428.9723 | 1525.1956
Rokeby |  | 28221 | 109.0672 | 95.0171 | 97.7069 | 97.4066 | 95.7659 | 94.6018 | 94.665 | 94.4819 | 96.6336 | 102.4558 | 107.6185 | 110.4008 | 141.7562 | 159.5228 | 154.0201 | 155.2548 | 152.7244 | 152.6274 | 152.8525 | 153.5357 | 155.5694 | 161.9927 | 167.238 | 170.7265 | 602.939 | 700.8652 | 823.9176 | 898.8732 | 948.6621 | 1066.8254 | 1184.6514 | 1290.4287 | 1381.7828 | 1459.2947 | 1531.2909 | 1597.2692
Rokeby |  | 28222 | 118.6208 | 103.4766 | 106.4058 | 106.0787 | 104.292 | 103.0243 | 103.0931 | 102.8937 | 105.237 | 111.5775 | 117.1998 | 120.2298 | 193.2413 | 160.9836 | 155.4305 | 156.6766 | 154.123 | 154.0251 | 154.2523 | 154.9418 | 156.994 | 163.4762 | 168.7695 | 172.29 | 921.8682 | 1103.4154 | 1306.3764 | 1378.8661 | 1451.2009 | 1625.0548 | 1799.9892 | 1957.797 | 2094.1536 | 2209.4062 | 2315.5649 | 2410.1594
Rokeby |  | 28223 | 193.9001 | 119.6371 | 123.0238 | 122.6456 | 120.5798 | 119.1141 | 119.1938 | 118.9632 | 121.6724 | 129.0032 | 135.5036 | 139.0068 | 294.1039 | 272.0964 | 262.7105 | 264.8166 | 260.5004 | 260.335 | 260.719 | 261.8843 | 265.3531 | 276.3092 | 285.2562 | 291.2065 | 376.6409 | 474.0857 | 616.1816 | 666.0801 | 718.0402 | 843.8497 | 971.3582 | 1087.2317 | 1188.1353 | 1274.1478 | 1354.1149 | 1427.8336
Rokeby |  | 28224 | 85.9979 | 86.8494 | 89.308 | 89.0335 | 87.5338 | 86.4698 | 86.5276 | 86.3602 | 88.327 | 93.6487 | 98.3676 | 100.9107 | 156.3631 | 136.0628 | 131.3694 | 132.4225 | 130.2642 | 130.1815 | 130.3735 | 130.9563 | 132.6908 | 138.1695 | 142.6434 | 145.6189 | 1.52 | 1.52 | 1.52 | 1.7164 | 2.0306 | 2.7966 | 3.5822 | 4.3089 | 4.957 | 5.5266 | 6.0765 | 6.6068
Rokeby |  | 28225 | 5.3219 | 3.7724 | 3.8792 | 3.8672 | 3.8021 | 3.7559 | 3.7584 | 3.7511 | 3.8365 | 4.0677 | 4.2727 | 4.3831 | 6.2242 | 4.6109 | 4.4519 | 4.4876 | 4.4144 | 4.4116 | 4.4181 | 4.4379 | 4.4967 | 4.6823 | 4.834 | 4.9348 | 213.7942 | 280.5297 | 320.8515 | 354.9969 | 395.2099 | 492.272 | 590.1998 | 678.6585 | 755.1258 | 819.7691 | 879.345 | 933.7972
Rokeby |  | 28228 | 74.3183 | 68.7773 | 70.7243 | 70.5069 | 69.3193 | 68.4767 | 68.5225 | 68.3899 | 69.9474 | 74.1618 | 77.8987 | 79.9127 | 134.7044 | 121.6737 | 117.4766 | 118.4184 | 116.4883 | 116.4143 | 116.586 | 117.1071 | 118.6583 | 123.5575 | 127.5584 | 130.2192 | 31.2018 | 37.4422 | 57.6609 | 64.0328 | 67.7545 | 76.737 | 85.7988 | 93.9833 | 101.0571 | 107.0356 | 112.5438 | 117.5766
Rokeby |  | 28229 | 8.6528 | 5.9061 | 6.0733 | 6.0547 | 5.9527 | 5.8803 | 5.8843 | 5.8729 | 6.0066 | 6.3685 | 6.6894 | 6.8624 | 14.3596 | 11.0102 | 10.6304 | 10.7156 | 10.541 | 10.5343 | 10.5498 | 10.597 | 10.7373 | 11.1807 | 11.5427 | 11.7835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby |  | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.0443 | 972.1924 | 1165.835 | 1252.0011 | 1309.5153 | 1447.2659 | 1585.3961 | 1709.6224 | 1816.7028 | 1907.072 | 1990.2743 | 2066.2614
Rokeby |  | 28231 | 187.7746 | 152.0661 | 156.3708 | 155.8902 | 153.2644 | 151.4014 | 151.5026 | 151.2095 | 154.6532 | 163.9711 | 172.2334 | 176.6862 | 290.6718 | 214.2061 | 206.8171 | 208.4751 | 205.0773 | 204.9471 | 205.2494 | 206.1667 | 208.8975 | 217.5227 | 224.5661 | 229.2504 | 535.2669 | 605.8822 | 673.5566 | 743.1335 | 810.3107 | 972.9782 | 1139.4127 | 1293.476 | 1431.4004 | 1553.3232 | 1671.765 | 1782.8457
Rokeby |  | 28232 | 121.429 | 98.5913 | 101.3822 | 101.0706 | 99.3682 | 98.1603 | 98.226 | 98.0359 | 100.2686 | 106.3098 | 111.6666 | 114.5536 | 210.4711 | 214.1777 | 206.7897 | 208.4475 | 205.0501 | 204.9199 | 205.2221 | 206.1394 | 208.8698 | 217.4938 | 224.5363 | 229.22 | 66.439 | 84.6631 | 86.3341 | 99.7146 | 121.9164 | 178.3714 | 239.1756 | 298.65 | 355.1153 | 408.2381 | 463.4067 | 520.9635
Rosebery 22kV |  | 97001 | 28.0568 | 17.7701 | 18.2732 | 18.217 | 17.9102 | 17.6925 | 17.7043 | 17.67 | 18.0725 | 19.1613 | 20.1268 | 20.6472 | 35.2223 | 33.2627 | 32.1153 | 32.3727 | 31.8451 | 31.8249 | 31.8718 | 32.0143 | 32.4383 | 33.7777 | 34.8714 | 35.5988 | 130.3652 | 148.3338 | 166.7803 | 198.6749 | 224.1819 | 287.359 | 353.022 | 414.1939 | 468.6334 | 515.8146 | 560.1419 | 601.1843
Rosebery 22kV |  | 97002 | 29.3522 | 22.2818 | 22.9125 | 22.8421 | 22.4574 | 22.1844 | 22.1992 | 22.1563 | 22.6609 | 24.0262 | 25.2368 | 25.8893 | 38.5929 | 36.0322 | 34.7893 | 35.0682 | 34.4966 | 34.4747 | 34.5256 | 34.6799 | 35.1393 | 36.5901 | 37.7749 | 38.5629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV |  | 97014 | 0 | 33.6942 | 34.648 | 34.5415 | 33.9597 | 33.5469 | 33.5693 | 33.5044 | 34.2674 | 36.332 | 38.1628 | 39.1494 | 0 | 243.0285 | 234.6453 | 236.5264 | 232.6714 | 232.5236 | 232.8666 | 233.9074 | 237.0056 | 246.7913 | 254.7825 | 260.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 44kV |  | 97013 | 0 | 50.8498 | 52.2893 | 52.1286 | 51.2505 | 50.6275 | 50.6614 | 50.5634 | 51.7149 | 54.8307 | 57.5936 | 59.0826 | 0 | 123.7236 | 119.4558 | 120.4135 | 118.4509 | 118.3757 | 118.5503 | 119.0802 | 120.6574 | 125.6393 | 129.7075 | 132.4131 | 111.7537 | 137.1794 | 144.2691 | 150.1108 | 159.6886 | 183.7351 | 209.2331 | 233.6444 | 256.1244 | 276.3877 | 296.2353 | 315.3856
Savage River |  | 95001 | 25.0935 | 22.3968 | 23.0308 | 22.96 | 22.5733 | 22.2989 | 22.3138 | 22.2706 | 22.7778 | 24.1502 | 25.3671 | 26.0229 | 33.2275 | 32.2834 | 31.1698 | 31.4197 | 30.9076 | 30.888 | 30.9335 | 31.0718 | 31.4834 | 32.7833 | 33.8448 | 34.5508 | 577.3695 | 653.3557 | 695.4537 | 778.5968 | 888.0136 | 1155.8923 | 1432.2982 | 1689.9662 | 1922.1611 | 2129.172 | 2333.113 | 2535.3371
Scottsdale |  | 54003 | 168.3333 | 168.5444 | 173.3156 | 172.7829 | 169.8726 | 167.8078 | 167.9199 | 167.5951 | 171.4119 | 181.7395 | 190.8971 | 195.8325 | 137.0581 | 127.1276 | 122.7424 | 123.7264 | 121.7098 | 121.6326 | 121.812 | 122.3564 | 123.9771 | 129.096 | 133.2761 | 136.0562 | 12.58 | 12.58 | 16.2942 | 23.6289 | 32.7492 | 54.9757 | 77.6578 | 98.4125 | 116.621 | 132.2893 | 147.0557 | 160.9325
Scottsdale |  | 54004 | 22.4171 | 1.1318 | 1.1638 | 1.1602 | 1.1407 | 1.1268 | 1.1276 | 1.1254 | 1.151 | 1.2204 | 1.2819 | 1.315 | 22.388 | 1.2287 | 1.1863 | 1.1958 | 1.1763 | 1.1756 | 1.1773 | 1.1826 | 1.1982 | 1.2477 | 1.2881 | 1.315 | 208.1658 | 219.6515 | 226.6599 | 274.1218 | 346.2209 | 521.9736 | 702.958 | 872.0398 | 1025.5843 | 1164.2746 | 1303.1013 | 1442.1459
Scottsdale |  | 54005 | 84.6667 | 80.6209 | 82.9031 | 82.6483 | 81.2562 | 80.2685 | 80.3221 | 80.1667 | 81.9925 | 86.9325 | 91.313 | 93.6737 | 104.9999 | 86.4728 | 83.49 | 84.1593 | 82.7876 | 82.7351 | 82.8571 | 83.2274 | 84.3298 | 87.8117 | 90.6551 | 92.5461 | 4.02 | 4.02 | 4.02 | 8.6204 | 15.981 | 33.9226 | 52.3242 | 69.3456 | 84.5269 | 97.8681 | 110.7492 | 123.1702
Scottsdale |  | 54006 | 9.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.9898 | 513.7843 | 562.0719 | 613.8807 | 670.6216 | 807.6142 | 947.9554 | 1079.1704 | 1199.2226 | 1309.1886 | 1421.4218 | 1536.939
Scottsdale |  | 54007 | 69.5314 | 49.6833 | 51.0898 | 50.9328 | 50.0748 | 49.4662 | 49.4992 | 49.4035 | 50.5286 | 53.5729 | 56.2724 | 57.7273 | 105.9316 | 97.8129 | 94.4389 | 95.196 | 93.6444 | 93.585 | 93.723 | 94.1419 | 95.3889 | 99.3274 | 102.5436 | 104.6826 | 80.26 | 83.7736 | 95.4767 | 125.418 | 168.4776 | 272.7141 | 379.0988 | 477.3 | 565.0103 | 642.4756 | 717.8351 | 791.0953
Smithton |  | 93001 | 134.456 | 134.051 | 137.8458 | 137.4221 | 135.1074 | 133.4651 | 133.5543 | 133.296 | 136.3317 | 144.5456 | 151.8291 | 155.7544 | 127.8758 | 143.138 | 138.2005 | 139.3084 | 137.0379 | 136.9508 | 137.1528 | 137.7659 | 139.5906 | 145.3542 | 150.0608 | 153.191 | 64.432 | 69.4248 | 71.1648 | 102.2147 | 152.2214 | 275.6495 | 404.8147 | 527.7684 | 641.5575 | 745.9449 | 851.3077 | 955.6618
Smithton |  | 93002 | 183.207 | 189.5093 | 194.8739 | 194.275 | 191.0026 | 188.6809 | 188.8071 | 188.4418 | 192.7334 | 204.3456 | 214.6423 | 220.1916 | 120.3792 | 120.3089 | 116.1589 | 117.0901 | 115.1817 | 115.1086 | 115.2784 | 115.7936 | 117.3273 | 122.1717 | 126.1276 | 128.7586 | 159.3585 | 179.8626 | 203.7944 | 230.3646 | 267.7225 | 359.8281 | 455.1291 | 543.6955 | 622.6317 | 691.512 | 757.0726 | 818.9528
Smithton |  | 93003 | 142.1124 | 131.2339 | 134.9489 | 134.5341 | 132.268 | 130.6603 | 130.7476 | 130.4947 | 133.4666 | 141.5079 | 148.6384 | 152.4812 | 132.4247 | 116.5196 | 112.5003 | 113.4022 | 111.5539 | 111.4831 | 111.6475 | 112.1465 | 113.6319 | 118.3237 | 122.155 | 124.7031 | 107.6714 | 114.5735 | 131.1609 | 146.5082 | 161.9375 | 198.0619 | 233.4327 | 264.479 | 290.6023 | 312.1413 | 331.5424 | 348.9082
Smithton |  | 93004 | 104.3774 | 98.4385 | 101.2251 | 100.914 | 99.2142 | 98.0083 | 98.0738 | 97.884 | 100.1133 | 106.1451 | 111.4936 | 114.3761 | 120.6386 | 115.6568 | 111.6672 | 112.5625 | 110.7279 | 110.6576 | 110.8208 | 111.3161 | 112.7905 | 117.4475 | 121.2505 | 123.7797 | 250.992 | 278.4441 | 301.4517 | 355.4906 | 434.1341 | 625.205 | 819.7206 | 997.4273 | 1153.1324 | 1286.3532 | 1411.2241 | 1527.5549
Smithton |  | 93005 | 101.651 | 94.9673 | 97.6557 | 97.3555 | 95.7156 | 94.5522 | 94.6154 | 94.4324 | 96.583 | 102.4021 | 107.562 | 110.3429 | 131.2911 | 128.1538 | 123.7331 | 124.7251 | 122.6922 | 122.6143 | 122.7952 | 123.344 | 124.9778 | 130.138 | 134.3519 | 137.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smithton |  | 93006 | 69.2202 | 83.3132 | 85.6717 | 85.4084 | 83.9697 | 82.9491 | 83.0045 | 82.8439 | 84.7306 | 89.8357 | 94.3624 | 96.802 | 63.2045 | 63.6133 | 61.419 | 61.9114 | 60.9023 | 60.8637 | 60.9534 | 61.2259 | 62.0368 | 64.5983 | 66.69 | 68.0811 | 651.2667 | 841.9093 | 1023.1312 | 1113.562 | 1196.3719 | 1393.4016 | 1589.6581 | 1765.0746 | 1915.5522 | 2042.2242 | 2158.9151 | 2265.9247
Sorell |  | 41511 | 80.3889 | 75.9745 | 78.1252 | 77.885 | 76.5731 | 75.6424 | 75.6929 | 75.5465 | 77.267 | 81.9224 | 86.0503 | 88.275 | 135.2786 | 138.2652 | 133.4958 | 134.566 | 132.3727 | 132.2887 | 132.4838 | 133.076 | 134.8386 | 140.406 | 144.9523 | 147.976 | 153.2509 | 170.5435 | 200.2176 | 222.0591 | 242.0653 | 289.6973 | 337.3222 | 380.1632 | 417.2317 | 448.7717 | 478.2132 | 505.647
Sorell |  | 41512 | 92.3436 | 98.4881 | 101.2761 | 100.9648 | 99.2642 | 98.0576 | 98.1232 | 97.9333 | 100.1637 | 106.1985 | 111.5498 | 114.4337 | 140.7368 | 141.8005 | 136.9091 | 138.0067 | 135.7574 | 135.6712 | 135.8713 | 136.4786 | 138.2863 | 143.996 | 148.6586 | 151.7596 | 802.0427 | 1045.7252 | 1256.2631 | 1345.614 | 1442.3542 | 1676.2045 | 1913.6195 | 2130.7179 | 2322.0439 | 2488.2206 | 2646.8134 | 2798.0029
Sorell |  | 41513 | 107.9511 | 104.658 | 107.6207 | 107.2899 | 105.4827 | 104.2005 | 104.2702 | 104.0685 | 106.4385 | 112.8515 | 118.5379 | 121.6026 | 154.3066 | 148.7919 | 143.6593 | 144.811 | 142.4508 | 142.3604 | 142.5703 | 143.2076 | 145.1044 | 151.0956 | 155.9881 | 159.242 | 153.6671 | 175.0495 | 196.5501 | 239.0782 | 290.6442 | 417.5661 | 549.9774 | 675.7183 | 792.0941 | 899.3488 | 1008.8205 | 1120.8902
Sorell |  | 41514 | 59.7655 | 64.2108 | 66.0285 | 65.8256 | 64.7168 | 63.9302 | 63.9729 | 63.8491 | 65.3032 | 69.2378 | 72.7266 | 74.6068 | 74.2285 | 70.8317 | 68.3884 | 68.9366 | 67.8131 | 67.77 | 67.87 | 68.1733 | 69.0763 | 71.9284 | 74.2574 | 75.8064 | 410.1948 | 460.9972 | 493.0281 | 625.7315 | 789.9264 | 1199.9813 | 1636.1193 | 2058.9812 | 2457.3393 | 2828.2528 | 3206.8742 | 3568.5084
Sorell |  | 41515 | 98.3201 | 63.1698 | 64.958 | 64.7584 | 63.6676 | 62.8937 | 62.9357 | 62.814 | 64.2445 | 68.1152 | 71.5475 | 73.3972 | 144.8894 | 133.7438 | 129.1303 | 130.1655 | 128.044 | 127.9627 | 128.1515 | 128.7243 | 130.4293 | 135.8146 | 140.2123 | 143.137 | 367.9298 | 400.0471 | 441.4956 | 528.6738 | 655.1152 | 968.4243 | 1294.0595 | 1597.6279 | 1868.5802 | 2105.0407 | 2330.0345 | 2540.5202
Sorell |  | 41516 | 118.869 | 97.5486 | 100.3101 | 100.0018 | 98.3173 | 97.1223 | 97.1872 | 96.9992 | 99.2082 | 105.1855 | 110.4857 | 113.3422 | 150.6998 | 152.2041 | 146.9539 | 148.132 | 145.7176 | 145.6251 | 145.8399 | 146.4917 | 148.4321 | 154.5607 | 159.5654 | 162.8939 | 867.503 | 1001.1435 | 1176.9602 | 1301.725 | 1401.5363 | 1639.0733 | 1876.6758 | 2090.875 | 2276.9857 | 2436.1818 | 2585.4077 | 2720.3359
Sorell |  | 41517 | 86.5886 | 80.8038 | 83.0912 | 82.8358 | 81.4406 | 80.4506 | 80.5044 | 80.3487 | 82.1785 | 87.1298 | 91.5202 | 93.8863 | 124.9496 | 128.0712 | 123.6534 | 124.6447 | 122.6132 | 122.5353 | 122.716 | 123.2645 | 124.8972 | 130.0541 | 134.2653 | 137.066 | 971.056 | 1137.5542 | 1365.5486 | 1473.3613 | 1583.9831 | 1846.8841 | 2109.1725 | 2344.4884 | 2547.3529 | 2718.9947 | 2877.7778 | 3022.198
Sorell |  | 41518 | 121.8409 | 81.3806 | 83.6844 | 83.4272 | 82.0219 | 81.0249 | 81.0791 | 80.9222 | 82.7652 | 87.7518 | 92.1735 | 94.5565 | 134.8525 | 147.236 | 142.1571 | 143.2968 | 140.9612 | 140.8717 | 141.0795 | 141.7101 | 143.5871 | 149.5156 | 154.357 | 157.5768 | 162.2862 | 176.1792 | 204.3312 | 229.0475 | 264.1985 | 347.4703 | 429.9897 | 503.2937 | 565.7061 | 617.7641 | 665.1922 | 708.1279
St Leonards |  | 66101 | 33 | 28.155 | 28.952 | 28.863 | 28.3769 | 28.0319 | 28.0507 | 27.9964 | 28.634 | 30.3592 | 31.889 | 32.7134 | 58.6284 | 56.4271 | 54.4807 | 54.9174 | 54.0223 | 53.988 | 54.0677 | 54.3093 | 55.0287 | 57.3008 | 59.1562 | 60.3901 | 646.886 | 735.5323 | 890.9025 | 986.1631 | 1077.226 | 1296.4654 | 1517.8745 | 1719.2075 | 1895.9421 | 2049.6091 | 2197.8335 | 2342.7496
St Leonards |  | 66102 | 133.7086 | 59.885 | 61.5802 | 61.391 | 60.3569 | 59.6232 | 59.6631 | 59.5477 | 60.9038 | 64.5733 | 67.8271 | 69.5806 | 178.4312 | 193.5394 | 186.8633 | 188.3614 | 185.2914 | 185.1737 | 185.4468 | 186.2757 | 188.743 | 196.536 | 202.8999 | 207.1323 | 638.8332 | 719.9602 | 815.2075 | 917.4078 | 999.0965 | 1197.9098 | 1402.0278 | 1591.9938 | 1763.8068 | 1918.4206 | 2072.6966 | 2227.4807
St Leonards |  | 66103 | 109.7493 | 76.065 | 78.2183 | 77.9779 | 76.6644 | 75.7325 | 75.7832 | 75.6365 | 77.3591 | 82.02 | 86.1529 | 88.3802 | 198.4505 | 217.9372 | 210.4194 | 212.1063 | 208.6493 | 208.5168 | 208.8244 | 209.7577 | 212.5361 | 221.3115 | 228.4776 | 233.2435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards |  | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.7301 | 478.3932 | 553.3131 | 596.1618 | 654.9368 | 798.8361 | 948.1448 | 1089.3987 | 1220.168 | 1341.6173 | 1467.9837 | 1601.9837
St Leonards |  | 66105 | 84.585 | 49.2417 | 50.6356 | 50.48 | 49.6297 | 49.0264 | 49.0592 | 48.9643 | 50.0794 | 53.0967 | 55.7722 | 57.2141 | 106.3183 | 108.0227 | 104.2965 | 105.1326 | 103.4191 | 103.3534 | 103.5058 | 103.9685 | 105.3456 | 109.6952 | 113.2471 | 115.6094 | 486.816 | 553.5116 | 623.6564 | 692.3774 | 779.4302 | 992.5586 | 1212.3826 | 1417.1904 | 1601.5946 | 1765.7017 | 1926.704 | 2085.0279
St Leonards |  | 66106 | 129.8307 | 72.155 | 74.1976 | 73.9695 | 72.7236 | 71.8396 | 71.8876 | 71.7486 | 73.3826 | 77.8039 | 81.7243 | 83.8372 | 180.4526 | 221.6678 | 214.0214 | 215.7372 | 212.221 | 212.0863 | 212.3991 | 213.3484 | 216.1743 | 225.0999 | 232.3887 | 237.2362 | 164.4552 | 196.7178 | 206.6484 | 231.5913 | 263.5794 | 342.4093 | 423.9586 | 499.6995 | 567.0827 | 625.6667 | 681.0937 | 732.96
St Leonards |  | 66107 | 87.3569 | 34.2183 | 35.187 | 35.0788 | 34.488 | 34.0688 | 34.0915 | 34.0256 | 34.8005 | 36.8972 | 38.7564 | 39.7584 | 101.2602 | 151.3017 | 146.0826 | 147.2537 | 144.8537 | 144.7617 | 144.9752 | 145.6232 | 147.552 | 153.6443 | 158.6193 | 161.9281 | 0 | 0 | 0 | 0.96375 | 2.3628 | 5.3947 | 8.107 | 10.259 | 11.8836 | 13.0809 | 14.0456 | 14.821
St Leonards |  | 66108 | 3.8224 | 0.5693 | 0.58542 | 0.58362 | 0.57379 | 0.56682 | 0.56719 | 0.5661 | 0.57899 | 0.61387 | 0.64481 | 0.66148 | 4.6163 | 0.75667 | 0.73057 | 0.73642 | 0.72442 | 0.72396 | 0.72503 | 0.72827 | 0.73791 | 0.76838 | 0.79326 | 0.80981 | 332.5099 | 395.6661 | 448.6872 | 483.6588 | 515.2871 | 591.4293 | 668.4248 | 738.4767 | 799.7381 | 852.3238 | 901.6918 | 947.7884
St Leonards |  | 66109 | 30.2947 | 23.3233 | 23.9836 | 23.9099 | 23.5071 | 23.2214 | 23.2369 | 23.192 | 23.7201 | 25.1493 | 26.4165 | 27.0995 | 58.4896 | 60.4677 | 58.3819 | 58.8499 | 57.8907 | 57.854 | 57.9393 | 58.1983 | 58.9691 | 61.4039 | 63.3922 | 64.7145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards |  | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.5733 | 200.7163 | 210.9051 | 232.6599 | 262.3607 | 334.2833 | 407.8133 | 475.6849 | 535.9459 | 588.3366 | 637.9009 | 684.0551
St Marys |  | 57003 | 32.0028 | 23.1705 | 23.8264 | 23.7532 | 23.3531 | 23.0692 | 23.0846 | 23.04 | 23.5647 | 24.9844 | 26.2434 | 26.9219 | 42.6117 | 43.9125 | 42.3977 | 42.7376 | 42.041 | 42.0143 | 42.0763 | 42.2644 | 42.8242 | 44.5924 | 46.0363 | 46.9966 | 669.8822 | 756.4733 | 826.549 | 919.6976 | 1036.3285 | 1319.8256 | 1611.3237 | 1883.8253 | 2132.2273 | 2358.5003 | 2588.4336 | 2822.9685
St Marys |  | 57004 | 143.7525 | 114.9569 | 118.2112 | 117.8478 | 115.8628 | 114.4545 | 114.531 | 114.3094 | 116.9127 | 123.9567 | 130.2028 | 133.5689 | 170.333 | 185.616 | 179.2132 | 180.6499 | 177.7056 | 177.5928 | 177.8547 | 178.6496 | 181.0159 | 188.4899 | 194.5932 | 198.6524 | 63.1705 | 89.402 | 96.3607 | 106.6832 | 123.5401 | 165.304 | 208.5383 | 248.538 | 283.8594 | 314.2676 | 342.7231 | 369.0565
St Marys |  | 57005 | 84.1718 | 38.5408 | 39.6319 | 39.51 | 38.8445 | 38.3724 | 38.398 | 38.3237 | 39.1965 | 41.5581 | 43.6522 | 44.7807 | 88.0837 | 38.3033 | 36.9821 | 37.2785 | 36.671 | 36.6477 | 36.7017 | 36.8658 | 37.3541 | 38.8964 | 40.1559 | 40.9935 | 1476.7204 | 1652.2157 | 1866.954 | 2055.4579 | 2236.3775 | 2674.1251 | 3119.8592 | 3528.8456 | 3890.1036 | 4203.7764 | 4501.9835 | 4781.5004
St Marys |  | 57006 | 150.9674 | 124.7867 | 128.3192 | 127.9248 | 125.77 | 124.2412 | 124.3243 | 124.0838 | 126.9097 | 134.556 | 141.3361 | 144.9901 | 246.5482 | 221.2574 | 213.6251 | 215.3377 | 211.828 | 211.6935 | 212.0058 | 212.9533 | 215.774 | 224.6831 | 231.9584 | 236.7969 | 655.322 | 763.6561 | 854.1567 | 958.8608 | 1054.3109 | 1289.4785 | 1534.1568 | 1764.3963 | 1973.5025 | 2160.2798 | 2342.5669 | 2516.8619
Trevallyn |  | 61021 | 145.1766 | 82.9278 | 85.2753 | 85.0132 | 83.5813 | 82.5653 | 82.6205 | 82.4607 | 84.3386 | 89.42 | 93.9258 | 96.3541 | 165.7615 | 171.9961 | 166.0631 | 167.3944 | 164.6661 | 164.5616 | 164.8043 | 165.5409 | 167.7336 | 174.6591 | 180.3146 | 184.0759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn |  | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391.553 | 413.2571 | 474.1536 | 543.4136 | 635.5032 | 860.2043 | 1091.3946 | 1306.4463 | 1499.8468 | 1671.669 | 1839.6852 | 2003.8347
Trevallyn |  | 61023 | 89.5006 | 76.0889 | 78.2428 | 78.0023 | 76.6885 | 75.7563 | 75.807 | 75.6603 | 77.3834 | 82.0457 | 86.1799 | 88.408 | 142.9073 | 147.1571 | 142.081 | 143.22 | 140.8857 | 140.7963 | 141.0039 | 141.6342 | 143.5102 | 149.4355 | 154.2743 | 157.4924 | 20 | 20 | 20 | 37.0695 | 65.7401 | 139.8829 | 221.6773 | 304.3926 | 386.3768 | 467.487 | 556.2036 | 652.96
Trevallyn |  | 61024 | 130.8243 | 116.9089 | 120.2184 | 119.8489 | 117.8301 | 116.3979 | 116.4757 | 116.2504 | 118.8979 | 126.0615 | 132.4136 | 135.8369 | 170.8388 | 173.1832 | 167.2092 | 168.5497 | 165.8026 | 165.6973 | 165.9417 | 166.6834 | 168.8912 | 175.8645 | 181.5591 | 185.3463 | 578.5569 | 686.7038 | 752.7904 | 845.0332 | 932.3138 | 1144.608 | 1361.3177 | 1560.1751 | 1735.4784 | 1887.223 | 2031.1588 | 2167.5908
Trevallyn |  | 61025 | 82.8894 | 73.8944 | 75.9863 | 75.7527 | 74.4767 | 73.5715 | 73.6206 | 73.4782 | 75.1516 | 79.6795 | 83.6945 | 85.8583 | 188.4667 | 242.3731 | 234.0125 | 235.8885 | 232.0438 | 231.8965 | 232.2386 | 233.2766 | 236.3664 | 246.1257 | 254.0953 | 259.3957 | 22.9499 | 22.9499 | 22.9499 | 31.3285 | 44.2362 | 74.2721 | 103.4517 | 128.8465 | 150.0415 | 167.3988 | 182.9604 | 196.8583
Trevallyn |  | 61026 | 112.6667 | 137.5833 | 141.4781 | 141.0432 | 138.6675 | 136.982 | 137.0735 | 136.8084 | 139.924 | 148.3545 | 155.8299 | 159.8586 | 107.7927 | 105.8396 | 102.1887 | 103.0079 | 101.329 | 101.2647 | 101.414 | 101.8673 | 103.2166 | 107.4783 | 110.9585 | 113.273 | 1266.7825 | 1439.7214 | 1561.2759 | 1687.0003 | 1811.1083 | 2111.9146 | 2417.0172 | 2694.171 | 2934.972 | 3139.326 | 3328.0947 | 3500.7375
Trevallyn |  | 61027 | 103.2996 | 85.9444 | 88.3774 | 88.1057 | 86.6217 | 85.5688 | 85.626 | 85.4603 | 87.4066 | 92.6729 | 97.3426 | 99.8592 | 205.2516 | 206.3477 | 199.2297 | 200.8269 | 197.5537 | 197.4283 | 197.7195 | 198.6032 | 201.2338 | 209.5425 | 216.3276 | 220.8401 | 1236.4134 | 1394.2827 | 1533.4222 | 1652.6834 | 1770.5662 | 2051.779 | 2332.9048 | 2587.7435 | 2811.135 | 3004.2591 | 3187.6863 | 3356.0337
Trevallyn |  | 61028 | 118.9476 | 95.8667 | 98.5805 | 98.2775 | 96.6221 | 95.4476 | 95.5114 | 95.3267 | 97.4976 | 103.3719 | 108.5807 | 111.3879 | 209.758 | 205.9434 | 198.8394 | 200.4335 | 197.1667 | 197.0415 | 197.3322 | 198.2141 | 200.8396 | 209.132 | 215.9038 | 220.4074 | 518.0775 | 613.0201 | 690.484 | 732.4759 | 781.5305 | 899.415 | 1017.9407 | 1124.7863 | 1217.1281 | 1295.3384 | 1367.7035 | 1434.2098
Trevallyn |  | 61029 | 58.2779 | 52.5722 | 54.0605 | 53.8943 | 52.9865 | 52.3424 | 52.3774 | 52.2761 | 53.4666 | 56.688 | 59.5445 | 61.0839 | 115.7946 | 124.7869 | 120.4824 | 121.4483 | 119.4688 | 119.393 | 119.5691 | 120.1035 | 121.6943 | 126.719 | 130.8222 | 133.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn |  | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527.5008 | 620.624 | 743.948 | 804.2199 | 848.0336 | 950.9699 | 1053.5232 | 1145.7417 | 1225.9315 | 1294.9669 | 1360.6008 | 1423.1967
Trevallyn |  | 61037 | 66.3904 | 48.9167 | 50.3014 | 50.1468 | 49.3021 | 48.7029 | 48.7354 | 48.6411 | 49.7489 | 52.7463 | 55.4041 | 56.8365 | 88.1399 | 89.8222 | 86.7238 | 87.4191 | 85.9943 | 85.9397 | 86.0664 | 86.4511 | 87.5962 | 91.2129 | 94.1664 | 96.1307 | 10 | 10 | 10 | 44.1282 | 102.7506 | 256.8939 | 427.9784 | 599.5339 | 765.5065 | 923.6479 | 1088.8935 | 1260.7597
Trevallyn |  | 61039 | 127.3687 | 114.1483 | 117.3797 | 117.0189 | 115.0478 | 113.6494 | 113.7254 | 113.5054 | 116.0903 | 123.0848 | 129.2869 | 132.6294 | 162.0643 | 244.3646 | 235.9353 | 237.8267 | 233.9505 | 233.8019 | 234.1468 | 235.1933 | 238.3086 | 248.1481 | 256.1831 | 261.527 | 106.2308 | 133.3017 | 142.6501 | 196.3903 | 282.1731 | 491.1403 | 706.0766 | 906.4199 | 1087.396 | 1249.0781 | 1407.8646 | 1563.1016
Trevallyn |  | 61040 | 115.8896 | 103.6 | 106.5327 | 106.2053 | 104.4164 | 103.1472 | 103.2161 | 103.0164 | 105.3626 | 111.7106 | 117.3396 | 120.3733 | 185.6106 | 198.4119 | 191.5677 | 193.1035 | 189.9562 | 189.8356 | 190.1156 | 190.9653 | 193.4947 | 201.4839 | 208.008 | 212.347 | 831.0693 | 998.5495 | 1163.8321 | 1271.4647 | 1360.4073 | 1572.9782 | 1785.8011 | 1977.1038 | 2142.1679 | 2281.8608 | 2411.0583 | 2529.754
Trevallyn |  | 61041 | 75.5885 | 65.9944 | 67.8626 | 67.654 | 66.5145 | 65.706 | 65.7499 | 65.6227 | 67.1172 | 71.161 | 74.7468 | 76.6792 | 151.0027 | 155.0923 | 149.7424 | 150.9429 | 148.4827 | 148.3884 | 148.6073 | 149.2715 | 151.2487 | 157.4936 | 162.5932 | 165.9849 | 1555.2425 | 1885.1667 | 2099.1643 | 2273.186 | 2411.5244 | 2740.3233 | 3068.7151 | 3364.2671 | 3620.5908 | 3837.7857 | 4040.7029 | 4228.326
Trevallyn |  | 61043 | 126.763 | 117.5889 | 120.9176 | 120.546 | 118.5155 | 117.0749 | 117.1532 | 116.9265 | 119.5894 | 126.7947 | 133.1838 | 136.627 | 251.9333 | 268.4599 | 259.1995 | 261.2774 | 257.019 | 256.8558 | 257.2346 | 258.3844 | 261.8068 | 272.6165 | 281.4439 | 287.3147 | 96.6826 | 103.8832 | 117.5561 | 127.7813 | 144.3364 | 185.0458 | 226.9222 | 265.4477 | 299.2824 | 328.253 | 355.2166 | 380.0439
Triabunna |  | 43505 | 18.6578 | 15.9255 | 16.3763 | 16.326 | 16.051 | 15.8559 | 15.8665 | 15.8358 | 16.1964 | 17.1723 | 18.0376 | 18.5039 | 22.0987 | 20.4094 | 19.7054 | 19.8634 | 19.5396 | 19.5272 | 19.556 | 19.6434 | 19.9036 | 20.7254 | 21.3965 | 21.8428 | 377.1965 | 413.4441 | 450.1398 | 511.1269 | 592.7314 | 788.9331 | 987.4638 | 1168.7332 | 1328.5229 | 1467.6051 | 1600.9144 | 1725.9775
Triabunna |  | 43506 | 50.254 | 49.3526 | 50.7497 | 50.5937 | 49.7415 | 49.1369 | 49.1697 | 49.0746 | 50.1922 | 53.2163 | 55.8979 | 57.343 | 64.1092 | 69.7037 | 67.2993 | 67.8388 | 66.7331 | 66.6908 | 66.7891 | 67.0877 | 67.9763 | 70.7829 | 73.0749 | 74.5992 | 393.7613 | 420.0721 | 457.1037 | 520.8713 | 603.0404 | 803.8826 | 1010.6901 | 1202.806 | 1374.8581 | 1526.6666 | 1673.8767 | 1815.0323
Triabunna |  | 43507 | 80.0239 | 70.8675 | 72.8737 | 72.6497 | 71.426 | 70.5578 | 70.6049 | 70.4683 | 72.0732 | 76.4156 | 80.2661 | 82.3413 | 85.8024 | 105.471 | 101.8328 | 102.6492 | 100.9761 | 100.912 | 101.0609 | 101.5126 | 102.8571 | 107.104 | 110.572 | 112.8785 | 17.36 | 17.36 | 17.36 | 27.5993 | 46.2755 | 99.0232 | 162.304 | 230.8525 | 301.9403 | 373.528 | 451.0962 | 531.3901
Tungatinah |  | 49303 | 22.4857 | 5.8411 | 6.0065 | 5.988 | 5.8871 | 5.8156 | 5.8195 | 5.8082 | 5.9405 | 6.2984 | 6.6158 | 6.7868 | 24 | 14.2111 | 13.7209 | 13.8309 | 13.6055 | 13.5968 | 13.6169 | 13.6778 | 13.8589 | 14.4311 | 14.8984 | 15.2092 | 0 | 0 | 0 | 0.63715 | 1.6566 | 4.1415 | 6.6901 | 9.0476 | 11.1502 | 12.9979 | 14.782 | 16.5023
Tungatinah |  | 49307 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9417 | 108.1079 | 118.9793 | 138.6468 | 161.5576 | 217.5563 | 275.4199 | 329.5083 | 378.2607 | 421.0584 | 462.3503 | 500.0564
Ulverstone |  | 82001 | 118.9 | 94.2665 | 96.935 | 96.6371 | 95.0093 | 93.8544 | 93.9172 | 93.7355 | 95.8702 | 101.6464 | 106.7683 | 109.5286 | 92.7773 | 78.4962 | 75.7885 | 76.3961 | 75.151 | 75.1033 | 75.214 | 75.5502 | 76.5509 | 79.7116 | 82.2927 | 84.0093 | 1123.256 | 1318.0637 | 1457.839 | 1572.7157 | 1692.9341 | 1980.3131 | 2267.5435 | 2524.6513 | 2744.9635 | 2929.6493 | 3098.5104 | 3251.7083
Ulverstone |  | 82002 | 161.3905 | 72.1073 | 74.1486 | 73.9207 | 72.6755 | 71.7922 | 71.8402 | 71.7012 | 73.3341 | 77.7525 | 81.6703 | 83.7818 | 176.6632 | 152.3864 | 147.1298 | 148.3093 | 145.8921 | 145.7995 | 146.0145 | 146.6671 | 148.6098 | 154.7458 | 159.7565 | 163.0889 | 1140.0542 | 1364.9105 | 1492.928 | 1631.7522 | 1758.9225 | 2063.892 | 2371.2079 | 2649.9151 | 2892.9929 | 3101.1699 | 3296.1072 | 3476.2536
Ulverstone |  | 82003 | 121.6848 | 90.9937 | 93.5695 | 93.2819 | 91.7107 | 90.5959 | 90.6565 | 90.4811 | 92.5417 | 98.1174 | 103.0614 | 105.7259 | 200.7833 | 182.1558 | 175.8724 | 177.2823 | 174.3929 | 174.2822 | 174.5392 | 175.3193 | 177.6415 | 184.9761 | 190.9657 | 194.9492 | 92.8609 | 96.6349 | 103.2159 | 131.3507 | 173.6554 | 278.6422 | 388.8935 | 493.6654 | 589.6623 | 675.9962 | 760.6861 | 839.3811
Ulverstone |  | 82004 | 58.6 | 58.8839 | 60.5508 | 60.3647 | 59.3479 | 94.6006 | 94.6639 | 94.4807 | 96.6324 | 102.4546 | 107.6171 | 110.3994 | 0 | 48.4938 | 46.821 | 47.1963 | 46.4271 | 46.3976 | 46.4661 | 46.6738 | 47.292 | 49.2446 | 50.8392 | 51.8996 | 622.0242 | 732.2128 | 829.3269 | 911.337 | 1016.6985 | 1265.192 | 1510.1874 | 1726.6555 | 1909.9843 | 2062.1299 | 2200.0922 | 2324.4206
Ulverstone |  | 82005 | 87.1851 | 0 | 0 | 0 | 0 | 35.9741 | 35.9982 | 35.9285 | 36.7468 | 38.9608 | 40.924 | 41.982 | 165.0258 | 152.1494 | 146.9011 | 148.0787 | 145.6653 | 145.5728 | 145.7875 | 146.4391 | 148.3787 | 154.5052 | 159.5081 | 162.8353 | 45.3678 | 60.6217 | 68.7456 | 75.9557 | 87.0622 | 112.9424 | 138.1496 | 160.159 | 178.5913 | 193.7336 | 207.3448 | 219.5255
Ulverstone |  | 82006 | 122.9859 | 135.6109 | 139.4498 | 139.0212 | 136.6795 | 170.9923 | 171.1066 | 170.7756 | 174.6648 | 185.1884 | 194.5198 | 199.5488 | 117 | 84.3578 | 81.4479 | 82.1008 | 80.7627 | 80.7114 | 80.8305 | 81.1918 | 82.2672 | 85.6639 | 88.4377 | 90.2825 | 69.838 | 77.244 | 77.439 | 97.6522 | 123.3403 | 185.7693 | 249.5408 | 308.2126 | 360.1914 | 405.5156 | 448.9053 | 490.3771
Ulverstone |  | 82007 | 42.5 | 86.86 | 89.3188 | 89.0443 | 87.5444 | 122.4544 | 122.5363 | 122.2992 | 125.0845 | 132.6208 | 139.3034 | 142.9049 | 68.7586 | 35.4419 | 34.2193 | 34.4936 | 33.9314 | 33.9099 | 33.9599 | 34.1117 | 34.5635 | 35.9906 | 37.156 | 37.931 | 1098.7541 | 1287.399 | 1411.6717 | 1548.7479 | 1644.8004 | 1873.7046 | 2101.7851 | 2305.2974 | 2479.101 | 2624.2864 | 2756.5492 | 2876.1034
Ulverstone |  | 82008 | 113.2031 | 96.2005 | 98.9238 | 98.6197 | 96.9586 | 95.78 | 95.844 | 95.6586 | 97.8371 | 103.7318 | 108.9588 | 111.7757 | 182.2266 | 169.324 | 163.4832 | 164.7939 | 162.108 | 162.005 | 162.244 | 162.9691 | 165.1277 | 171.9457 | 177.5133 | 181.2162 | 70.0136 | 73.9136 | 79.1925 | 103.9758 | 146.748 | 261.0145 | 391.4264 | 527.3923 | 665.3751 | 804.1594 | 957.9001 | 1128.1213
Waddamana |  | 49202 | 16.6212 | 12.0526 | 12.3938 | 12.3557 | 12.1476 | 11.9999 | 12.0079 | 11.9847 | 12.2577 | 12.9962 | 13.651 | 14.004 | 18.9205 | 18.847 | 18.1969 | 18.3428 | 18.0438 | 18.0323 | 18.0589 | 18.1396 | 18.3799 | 19.1388 | 19.7585 | 20.1707 | 0 | 0 | 0 | 1.7096 | 5.4432 | 18.0782 | 36.1111 | 59.0599 | 86.5871 | 118.1172 | 156.3312 | 200.7458
Wayatinah |  | 49411 | 16.9754 | 10.7678 | 11.0726 | 11.0386 | 10.8526 | 10.7207 | 10.7279 | 10.7071 | 10.951 | 11.6108 | 12.1958 | 12.5111 | 18 | 11.6242 | 11.2233 | 11.3132 | 11.1289 | 11.1218 | 11.1382 | 11.188 | 11.3362 | 11.8042 | 12.1864 | 12.4407 | 0 | 0 | 0 | 0.67237 | 1.7482 | 4.3704 | 7.0599 | 9.5476 | 11.7665 | 13.7163 | 15.599 | 17.4144
Wayatinah |  | 49412 | 33 | 27.8286 | 28.6164 | 28.5284 | 28.0479 | 27.707 | 27.7255 | 27.6719 | 28.3021 | 30.0073 | 31.5193 | 32.3342 | 30 | 17.4378 | 16.8363 | 16.9712 | 16.6946 | 16.684 | 16.7086 | 16.7833 | 17.0056 | 17.7078 | 18.2811 | 18.6625 | 109.0721 | 140.7551 | 162.2277 | 184.2506 | 214.0893 | 289.7462 | 370.7649 | 449.0505 | 521.7478 | 587.7926 | 653.0088 | 716.5161
Wesley Vale |  | 81001 | 36 | 31.32 | 32.2066 | 32.1076 | 31.5668 | 31.1831 | 31.2039 | 31.1436 | 31.8528 | 33.772 | 35.4737 | 36.3908 | 47.2 | 201.8057 | 194.8444 | 196.4064 | 193.2053 | 193.0826 | 193.3674 | 194.2317 | 196.8044 | 204.9302 | 211.5659 | 215.9791 | 421.6238 | 464.6598 | 504.0969 | 540.0746 | 584.5908 | 691.8869 | 801.8567 | 903.2784 | 993.1844 | 1071.5244 | 1146.4756 | 1218.2042
Wesley Vale |  | 81002 | 64.7525 | 53.9257 | 55.4522 | 55.2818 | 54.3506 | 53.69 | 53.7259 | 53.6219 | 54.8431 | 58.1474 | 61.0774 | 62.6565 | 70.2212 | 63.7495 | 61.5504 | 62.0439 | 61.0326 | 60.9939 | 61.0839 | 61.3569 | 62.1696 | 64.7365 | 66.8327 | 68.2268 | 1361.0297 | 1534.8994 | 1702.5796 | 1857.7961 | 1996.1132 | 2322.8455 | 2646.8053 | 2934.9295 | 3180.7203 | 3386.3738 | 3574.7061 | 3746.6404
Wesley Vale |  | 81003 | 120.1386 | 104.5543 | 107.5141 | 107.1836 | 105.3782 | 104.0973 | 104.1669 | 103.9654 | 106.3331 | 112.7397 | 118.4205 | 121.4821 | 207.1816 | 180.8676 | 174.6286 | 176.0285 | 173.1595 | 173.0496 | 173.3048 | 174.0794 | 176.3852 | 183.6679 | 189.6152 | 193.5704 | 462.1673 | 568.942 | 683.6493 | 752.9895 | 803.4015 | 924.1364 | 1045.031 | 1153.4553 | 1246.5541 | 1324.7679 | 1396.4355 | 1461.5896
Zs-Bellerive | Lindisfarne | 27171 | 114.244 | 88.5278 | 91.0338 | 90.754 | 89.2254 | 88.1408 | 88.1998 | 88.0291 | 90.0339 | 95.4584 | 100.2685 | 102.8608 | 191.5197 | 167.4631 | 172.8073 | 174.1927 | 171.3536 | 171.2448 | 171.4974 | 172.2639 | 174.5456 | 181.7524 | 187.6376 | 191.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27172 | 0 | 77.5389 | 79.7339 | 79.4888 | 78.1499 | 77.2 | 77.2516 | 77.1021 | 78.8581 | 83.6093 | 87.8222 | 90.0927 | 0 | 0 | 11.1208 | 11.21 | 11.0273 | 11.0203 | 11.0365 | 11.0859 | 11.2327 | 11.6965 | 12.0752 | 12.3271 | 77.6711 | 82.2454 | 89.5413 | 98.7251 | 113.0849 | 147.122 | 180.8918 | 210.9432 | 236.5876 | 258.0357 | 277.6386 | 295.4498
Zs-Bellerive | Lindisfarne | 27173 | 29.4375 | 26.4667 | 27.2159 | 27.1322 | 26.6752 | 26.351 | 26.3686 | 26.3176 | 26.9169 | 28.5387 | 29.9767 | 30.7517 | 46.8616 | 42.0504 | 51.7207 | 52.1353 | 51.2856 | 51.253 | 51.3286 | 51.558 | 52.2409 | 54.3979 | 56.1593 | 57.3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363.3368 | 442.1784 | 527.4105 | 566.5799 | 620.2013 | 748.9911 | 878.3061 | 994.5906 | 1094.6987 | 1179.0181 | 1256.4805 | 1327.0858
Zs-Bellerive | Lindisfarne | 27175 | 102.2178 | 71.4278 | 73.4498 | 73.224 | 71.9906 | 71.1156 | 71.1631 | 71.0254 | 72.643 | 77.0197 | 80.9007 | 82.9922 | 160.7896 | 132.7614 | 128.1818 | 129.2094 | 127.1035 | 127.0228 | 127.2101 | 127.7787 | 129.4712 | 134.8169 | 139.1823 | 142.0856 | 85.5475 | 89.1797 | 109.1934 | 117.3336 | 130.3062 | 161.6245 | 193.2332 | 221.8002 | 246.5119 | 267.4211 | 286.7129 | 304.3693
Zs-Bellerive | Lindisfarne | 27176 | 61 | 52.3222 | 53.8034 | 53.638 | 52.7345 | 52.0935 | 52.1283 | 52.0275 | 53.2124 | 56.4184 | 59.2613 | 60.7934 | 85.3378 | 83.4599 | 80.5809 | 81.2269 | 79.903 | 79.8523 | 79.9701 | 80.3275 | 81.3915 | 84.7521 | 87.4964 | 89.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.0428 | 247.7069 | 322.1735 | 346.3725 | 381.2009 | 464.8131 | 548.7279 | 624.1543 | 689.0623 | 743.7146 | 793.9095 | 839.655
Zs-Bellerive | Lindisfarne | 27178 | 84.6088 | 66.7278 | 68.6167 | 68.4058 | 67.2536 | 66.4361 | 66.4805 | 66.3519 | 67.863 | 71.9518 | 75.5773 | 77.5313 | 125.2791 | 114.3457 | 110.4014 | 111.2864 | 109.4726 | 109.4031 | 109.5645 | 110.0542 | 111.5119 | 116.1161 | 119.876 | 122.3766 | 139.6121 | 152.361 | 176.7503 | 197.9691 | 216.3228 | 260.4844 | 305.0214 | 345.358 | 380.4316 | 410.3562 | 438.2907 | 464.244
Zs-Cambridge | Mornington | 29481 | 45.7225 | 37.0556 | 38.1045 | 37.9874 | 37.3476 | 36.8936 | 36.9183 | 36.8468 | 37.686 | 39.9566 | 41.9699 | 43.055 | 75.8819 | 74.2167 | 71.6566 | 72.231 | 71.0538 | 71.0087 | 71.1134 | 71.4312 | 72.3774 | 75.3658 | 77.8061 | 79.4291 | 5 | 5 | 5 | 16.0003 | 33.0534 | 73.268 | 113.3433 | 149.7796 | 182.3106 | 211.554 | 241.0153 | 271.0536
Zs-Cambridge | Mornington | 29482 | 41.0992 | 39.2056 | 40.3154 | 40.1915 | 39.5145 | 39.0342 | 39.0603 | 38.9847 | 39.8726 | 42.2749 | 44.4051 | 45.5531 | 43.3054 | 40.5394 | 39.141 | 39.4548 | 38.8118 | 38.7871 | 38.8443 | 39.018 | 39.5348 | 41.1671 | 42.5001 | 43.3867 | 734.4957 | 898.9152 | 1021.0324 | 1114.2155 | 1160.5237 | 1269.7349 | 1377.5728 | 1473.0915 | 1553.5189 | 1620.2277 | 1680.9202 | 1735.8307
Zs-Cambridge | Mornington | 29483 | 100.5926 | 70.3644 | 72.3563 | 72.1339 | 70.9189 | 70.0569 | 70.1037 | 69.9681 | 71.5616 | 75.8731 | 79.6963 | 81.7567 | 174.8467 | 159.766 | 154.2549 | 155.4915 | 152.9573 | 152.8601 | 153.0856 | 153.7698 | 155.8066 | 162.2397 | 167.493 | 170.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Mornington | 29485 | 107.0333 | 86.2422 | 88.6836 | 88.411 | 86.9218 | 85.8653 | 85.9227 | 85.7564 | 87.7095 | 92.994 | 97.6798 | 100.2052 | 104.9288 | 94.4227 | 91.1656 | 91.8964 | 90.3986 | 90.3413 | 90.4745 | 90.8789 | 92.0826 | 95.8846 | 98.9894 | 101.0542 | 0 | 0 | 0 | 8.6718 | 22.1548 | 53.5819 | 83.9052 | 109.9263 | 131.2639 | 148.4711 | 163.8082 | 177.6391
Zs-Cambridge | Mornington | 29486 | 46.9998 | 40.0739 | 41.2083 | 41.0817 | 40.3897 | 39.8987 | 39.9254 | 39.8482 | 40.7557 | 43.2112 | 45.3886 | 46.562 | 48.4838 | 50.9872 | 49.2284 | 49.6231 | 48.8143 | 48.7833 | 48.8553 | 49.0736 | 49.7236 | 51.7767 | 53.4532 | 54.5682 | 28.5242 | 32.0026 | 32.0026 | 39.4264 | 50.7539 | 76.934 | 102.2696 | 124.2725 | 142.5871 | 157.4995 | 170.7365 | 182.3891
Zs-Cambridge | Lindisfarne | 29488 | 203.4826 | 179.7184 | 184.8059 | 184.2379 | 181.1346 | 178.9329 | 179.0525 | 178.7061 | 182.776 | 193.7882 | 203.553 | 208.8155 | 236.2038 | 218.3333 | 210.8019 | 212.4919 | 209.0286 | 208.8959 | 209.204 | 210.139 | 212.9224 | 221.7138 | 228.8929 | 233.6675 | 26.53 | 26.53 | 33.93 | 39.2281 | 47.6352 | 67.9365 | 88.5495 | 107.4331 | 124.1603 | 138.8552 | 153.1901 | 167.347
Zs-Cambridge | Lindisfarne | 29489 | 97.9312 | 77.5628 | 79.7584 | 79.5133 | 78.174 | 77.2238 | 77.2754 | 77.1259 | 78.8824 | 83.635 | 87.8493 | 90.1205 | 118.2906 | 109.703 | 105.9188 | 106.768 | 105.0278 | 104.9611 | 105.1159 | 105.5857 | 106.9843 | 111.4015 | 115.0087 | 117.4078 | 313.7326 | 360.7028 | 427.4939 | 452.0797 | 468.0474 | 504.96 | 540.0085 | 570.525 | 596.2242 | 617.4544 | 636.6387 | 653.8956
Zs-Cambridge | Lindisfarne | 29490 | 47.9016 | 36.0911 | 37.1128 | 36.9987 | 36.3755 | 35.9334 | 35.9574 | 35.8878 | 36.7051 | 38.9166 | 40.8776 | 41.9344 | 77.9099 | 74.135 | 71.5777 | 72.1515 | 70.9756 | 70.9305 | 71.0351 | 71.3526 | 72.2977 | 75.2828 | 77.7205 | 79.3417 | 0 | 0 | 0 | 4.2705 | 11.3112 | 28.7383 | 46.5322 | 62.5493 | 76.1373 | 87.2664 | 97.1214 | 105.7424
Zs-Cambridge | Lindisfarne | 29491 | 65.7782 | 67.8089 | 69.7284 | 69.5141 | 68.3432 | 67.5125 | 67.5576 | 67.4269 | 68.9625 | 73.1175 | 76.8018 | 78.7874 | 78.3568 | 78.9131 | 76.191 | 76.8018 | 75.55 | 75.5021 | 75.6134 | 75.9514 | 76.9574 | 80.1349 | 82.7297 | 84.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Lindisfarne | 29492 | 3.0738 | 2.3852 | 2.4528 | 2.4452 | 2.404 | 2.3748 | 2.3764 | 2.3718 | 2.4258 | 2.572 | 2.7016 | 2.7714 | 3.0716 | 2.3373 | 2.2566 | 2.2747 | 2.2377 | 2.2362 | 2.2395 | 2.2495 | 2.2793 | 2.3734 | 2.4503 | 2.5014 | 211.3684 | 246.8316 | 285.4581 | 329.8824 | 392.1891 | 553.5592 | 728.8151 | 899.3123 | 1057.7398 | 1201.1545 | 1341.9564 | 1478.211
Zs-Claremont | Creek Road | 21081 | 107.2365 | 103.9778 | 106.9212 | 106.5926 | 104.7971 | 103.5233 | 103.5925 | 103.3921 | 105.7468 | 112.118 | 117.7675 | 120.8122 | 173.0621 | 169.7983 | 163.9412 | 165.2554 | 162.562 | 162.4588 | 162.6984 | 163.4256 | 165.5903 | 172.4273 | 178.0105 | 181.7238 | 160.7694 | 180.745 | 213.7437 | 221.922 | 234.9542 | 266.4104 | 298.1477 | 326.817 | 351.6008 | 372.5533 | 391.8645 | 409.5162
Zs-Claremont | Creek Road | 21082 | 27.4121 | 24.3111 | 24.9993 | 24.9225 | 24.5027 | 24.2048 | 24.221 | 24.1742 | 24.7247 | 26.2144 | 27.5353 | 28.2472 | 47.4133 | 46.9867 | 45.3659 | 45.7295 | 44.9842 | 44.9557 | 45.022 | 45.2232 | 45.8222 | 47.7141 | 49.2591 | 50.2867 | 127.3621 | 149.0161 | 162.5459 | 174.3741 | 190.0995 | 228.054 | 266.3433 | 300.9258 | 330.8147 | 356.0761 | 379.3504 | 400.6156
Zs-Claremont | Creek Road | 21083 | 180.4313 | 166.4167 | 171.1276 | 170.6017 | 167.728 | 165.6893 | 165.8 | 165.4793 | 169.2479 | 179.4451 | 188.4872 | 193.3602 | 191.6625 | 174.9238 | 168.8898 | 170.2438 | 167.469 | 167.3627 | 167.6095 | 168.3587 | 170.5887 | 177.6321 | 183.3839 | 187.2092 | 38.5164 | 38.5164 | 38.5164 | 41.9375 | 47.389 | 60.5465 | 73.8202 | 85.8088 | 96.1703 | 104.9276 | 112.996 | 120.3679
Zs-Claremont | Creek Road | 21084 | 152.9562 | 142.6833 | 146.7224 | 146.2715 | 143.8077 | 142.0597 | 142.1546 | 141.8796 | 145.1108 | 153.8537 | 161.6063 | 165.7843 | 180.8427 | 141.792 | 136.9009 | 137.9984 | 135.7492 | 135.663 | 135.8631 | 136.4704 | 138.278 | 143.9873 | 148.6497 | 151.7504 | 848.0377 | 1046.5598 | 1184.9272 | 1298.6798 | 1380.5071 | 1577.0676 | 1774.4561 | 1951.9598 | 2104.7454 | 2233.3806 | 2351.473 | 2459.0102
Zs-Claremont | Creek Road | 21085 | 138.5026 | 134.2444 | 138.0447 | 137.6204 | 135.3023 | 133.6577 | 133.747 | 133.4883 | 136.5283 | 144.7542 | 152.0482 | 155.9792 | 274.5987 | 259.4834 | 250.5325 | 252.541 | 248.425 | 248.2672 | 248.6334 | 249.7447 | 253.0527 | 263.501 | 272.0332 | 277.7077 | 259.8792 | 314.0637 | 333.6511 | 360.9251 | 397.8921 | 488.2437 | 580.7375 | 665.6187 | 740.1823 | 804.1942 | 864.0182 | 919.3626
Zs-Claremont | Creek Road | 21086 | 74.9733 | 60.4944 | 62.2069 | 62.0157 | 60.9711 | 60.23 | 60.2703 | 60.1537 | 61.5236 | 65.2304 | 68.5173 | 70.2887 | 140.9581 | 137.3564 | 132.6183 | 133.6815 | 131.5027 | 131.4192 | 131.613 | 132.2013 | 133.9523 | 139.4831 | 143.9996 | 147.0033 | 262.1134 | 282.653 | 349.2671 | 392.1228 | 424.1949 | 501.4619 | 579.2727 | 649.4312 | 709.9702 | 761.0581 | 808.0593 | 850.9439
Zs-Claremont | Creek Road | 21087 | 53.4906 | 47.8444 | 49.1988 | 49.0476 | 48.2215 | 47.6353 | 47.6672 | 47.5749 | 48.6584 | 51.5901 | 54.1897 | 55.5907 | 104.1457 | 97.2151 | 93.8617 | 94.6141 | 93.0721 | 93.013 | 93.1502 | 93.5665 | 94.8058 | 98.7203 | 101.9168 | 104.0428 | 132.6122 | 150.6776 | 180.8977 | 196.1885 | 220.5542 | 279.3651 | 338.6989 | 392.2936 | 438.6208 | 477.7819 | 513.8703 | 546.8519
Zs-Claremont | Creek Road | 21088 | 32.3294 | 30.3833 | 31.2434 | 31.1474 | 30.6228 | 30.2505 | 30.2708 | 30.2122 | 30.9002 | 32.762 | 34.4128 | 35.3025 | 61.5053 | 54.1614 | 52.2931 | 52.7123 | 51.8532 | 51.8203 | 51.8967 | 52.1287 | 52.8191 | 55 | 56.7809 | 57.9653 | 323.0615 | 358.7665 | 413.057 | 448.8673 | 492.2481 | 596.9127 | 703.0038 | 799.9111 | 885.2366 | 959.1955 | 1029.3838 | 1093.2519
Zs-Claremont | Creek Road | 21089 | 86.8468 | 84.1222 | 86.5036 | 86.2377 | 84.7851 | 83.7545 | 83.8105 | 83.6484 | 85.5534 | 90.708 | 95.2787 | 97.7419 | 150.5987 | 151.2684 | 146.0504 | 147.2212 | 144.8217 | 144.7298 | 144.9433 | 145.5911 | 147.5195 | 153.6104 | 158.5844 | 161.8924 | 0 | 0 | 0 | 2.0655 | 5.2291 | 12.5604 | 19.6734 | 25.8812 | 30.6795 | 34.5136 | 38.0231 | 41.2513
Zs-Derwent Park | Risdon | 17100 | 105.1587 | 87.0721 | 89.5369 | 89.2617 | 87.7582 | 86.6915 | 86.7494 | 86.5816 | 88.5534 | 93.8888 | 98.6197 | 101.1694 | 128.8158 | 108.1778 | 104.4462 | 105.2835 | 103.5676 | 103.5018 | 103.6545 | 104.1178 | 105.4968 | 109.8527 | 113.4097 | 115.7754 | 193.4983 | 196.9566 | 200.5072 | 217.3664 | 232.4316 | 269.1977 | 307.0857 | 342.2751 | 373.5996 | 400.7787 | 426.3255 | 449.7632
Zs-Derwent Park | Risdon | 17101 | 91.9384 | 65.25 | 67.0971 | 66.8909 | 65.7642 | 64.9648 | 65.0082 | 64.8825 | 66.3601 | 70.3583 | 73.9036 | 75.8142 | 123.661 | 108.5324 | 104.7886 | 105.6287 | 103.9071 | 103.8411 | 103.9943 | 104.4591 | 105.8427 | 110.2128 | 113.7816 | 116.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Derwent Park | Risdon | 17102 | 15.7741 | 1.4778 | 1.5196 | 1.5149 | 1.4894 | 1.4713 | 1.4723 | 1.4695 | 1.5029 | 1.5935 | 1.6738 | 1.717 | 15.2214 | 1.8533 | 1.7894 | 1.8037 | 1.7743 | 1.7732 | 1.7758 | 1.7837 | 1.8074 | 1.882 | 1.9429 | 1.9835 | 97.5618 | 122.1237 | 142.0101 | 162.0821 | 194.5287 | 273.9693 | 355.1226 | 429.1022 | 493.3688 | 547.7316 | 597.6844 | 643.0863
Zs-Derwent Park | Risdon | 17103 | 98.3907 | 90.8111 | 93.3818 | 93.0948 | 91.5267 | 90.4142 | 90.4746 | 90.2996 | 92.3561 | 97.9205 | 102.8547 | 105.5138 | 171.4361 | 161.7816 | 156.201 | 157.4532 | 154.887 | 154.7886 | 155.0169 | 155.7098 | 157.7722 | 164.2865 | 169.6061 | 173.144 | 3 | 3 | 3 | 11.4995 | 24.3347 | 54.0306 | 83.4201 | 110.3781 | 135.0433 | 158.0205 | 182.1017 | 207.5627
Zs-Derwent Park | Risdon | 17104 | 117.6067 | 74.7556 | 76.8718 | 76.6355 | 75.3446 | 74.4288 | 74.4786 | 74.3345 | 76.0274 | 80.608 | 84.6698 | 86.8588 | 130.2547 | 96.6181 | 93.2853 | 94.0331 | 92.5005 | 92.4418 | 92.5781 | 92.9919 | 94.2237 | 98.114 | 101.291 | 103.4039 | 199.8402 | 232.7474 | 253.1613 | 301.4471 | 351.0692 | 475.2338 | 605.503 | 728.1674 | 838.8845 | 936.6784 | 1030.7956 | 1120.4368
Zs-Derwent Park | Risdon | 17105 | 155.1789 | 127.9111 | 131.5321 | 131.1278 | 128.9191 | 127.352 | 127.4372 | 127.1906 | 130.0873 | 137.925 | 144.8749 | 148.6204 | 219.5472 | 213.6902 | 206.319 | 207.973 | 204.5833 | 204.4535 | 204.755 | 205.6702 | 208.3944 | 216.9988 | 224.0252 | 228.6983 | 128.7419 | 162.1599 | 189.7473 | 206.3381 | 230.7317 | 288.2566 | 344.9657 | 395.0708 | 437.5123 | 472.75 | 504.7287 | 533.5854
Zs-Derwent Park | Risdon | 17106 | 166.8491 | 138.9818 | 142.9161 | 142.4768 | 140.077 | 138.3743 | 138.4668 | 138.1989 | 141.3463 | 149.8624 | 157.4138 | 161.4835 | 199.9601 | 183.9796 | 177.6333 | 179.0573 | 176.1389 | 176.0271 | 176.2867 | 177.0746 | 179.4201 | 186.8281 | 192.8777 | 196.901 | 5 | 5 | 5 | 12.5357 | 24.271 | 52.1822 | 80.2699 | 105.9419 | 128.709 | 148.6743 | 167.9128 | 186.3889
Zs-Derwent Park | Risdon | 17107 | 84.385 | 82.3944 | 84.7269 | 84.4665 | 83.0437 | 82.0343 | 82.0891 | 81.9303 | 83.7962 | 88.8449 | 93.3218 | 95.7344 | 117.9023 | 110.1093 | 106.3111 | 107.1634 | 105.4168 | 105.3499 | 105.5052 | 105.9768 | 107.3805 | 111.8141 | 115.4347 | 117.8426 | 0 | 0 | 0 | 1.6164 | 4.1171 | 10.0641 | 16.1319 | 21.882 | 27.3233 | 32.5676 | 38.2561 | 44.484
Zs-Derwent Park | Risdon | 17108 | 33.3598 | 29.9148 | 30.7616 | 30.6671 | 30.1505 | 29.784 | 29.804 | 29.7463 | 30.4237 | 32.2568 | 33.8822 | 34.7581 | 48.6265 | 29.35 | 28.3376 | 28.5648 | 28.0992 | 28.0813 | 28.1228 | 28.2485 | 28.6226 | 29.8044 | 30.7695 | 31.4113 | 0 | 0 | 0 | 5.2284 | 13.7946 | 35.1306 | 57.5413 | 78.9691 | 99.0618 | 118.0408 | 138.1751 | 159.8581
Zs-Derwent Park | Risdon | 17109 | 62.0732 | 47.1389 | 48.4733 | 48.3243 | 47.5103 | 46.9328 | 46.9642 | 46.8734 | 47.9409 | 50.8293 | 53.3905 | 54.7709 | 84.531 | 64.8935 | 62.655 | 63.1573 | 62.1279 | 62.0885 | 62.1801 | 62.458 | 63.2853 | 65.8983 | 68.0321 | 69.4512 | 0 | 0 | 0 | 6.4755 | 19.7044 | 60.256 | 111.46 | 168.2948 | 227.4214 | 286.2548 | 348.6596 | 412.8733
Zs-East Hobart | Risdon | 14060 | 92.8986 | 90.7278 | 93.2961 | 93.0094 | 91.4427 | 90.3312 | 90.3916 | 90.2167 | 92.2713 | 97.8307 | 102.7603 | 105.417 | 122.6469 | 109.867 | 106.0771 | 106.9275 | 105.1848 | 105.118 | 105.273 | 105.7435 | 107.1442 | 111.568 | 115.1806 | 117.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14061 | 64.7033 | 56.8 | 58.4079 | 58.2284 | 57.2476 | 56.5517 | 56.5895 | 56.4801 | 57.7663 | 61.2468 | 64.3329 | 65.9961 | 81.2819 | 73.0015 | 70.4834 | 71.0484 | 69.8904 | 69.846 | 69.9491 | 70.2617 | 71.1923 | 74.1318 | 76.5322 | 78.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14062 | 34.3333 | 28.1056 | 28.9012 | 28.8123 | 28.327 | 27.9827 | 28.0014 | 27.9472 | 28.5837 | 30.3059 | 31.833 | 32.656 | 35.9002 | 32.6397 | 31.5138 | 31.7665 | 31.2487 | 31.2289 | 31.2749 | 31.4147 | 31.8308 | 33.1451 | 34.2183 | 34.9321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14063 | 94.2976 | 82.9278 | 85.2753 | 85.0132 | 83.5813 | 82.5653 | 82.6205 | 82.4607 | 84.3386 | 89.42 | 93.9258 | 96.3541 | 129.6898 | 122.455 | 118.231 | 119.1788 | 117.2364 | 117.1619 | 117.3347 | 117.8592 | 119.4203 | 124.351 | 128.3775 | 131.0554 | 0 | 0 | 0 | 1.2678 | 4.0578 | 13.3494 | 26.1799 | 41.8267 | 59.7578 | 79.4244 | 102.3914 | 128.3175
Zs-East Hobart | Risdon | 14064 | 8.0056 | 1.2617 | 1.2974 | 1.2934 | 1.2716 | 1.2562 | 1.257 | 1.2546 | 1.2831 | 1.3605 | 1.429 | 1.466 | 9.3257 | 1.1714 | 1.131 | 1.14 | 1.1215 | 1.1208 | 1.1224 | 1.1274 | 1.1424 | 1.1895 | 1.228 | 1.2537 | 0 | 0 | 0 | 8.3579 | 26.0904 | 82.5839 | 156.7258 | 242.3086 | 335.1281 | 431.9671 | 540.7594 | 660.9575
Zs-East Hobart | Risdon | 14065 | 190.6281 | 182.4 | 187.5634 | 186.9869 | 183.8373 | 181.6027 | 181.7241 | 181.3726 | 185.5032 | 196.6797 | 206.5902 | 211.9313 | 196.8699 | 203.3947 | 196.3786 | 197.953 | 194.7266 | 194.603 | 194.89 | 195.7611 | 198.354 | 206.5439 | 213.2318 | 217.6797 | 0 | 0 | 0 | 1.1038 | 3.0328 | 8.2582 | 14.2716 | 20.5072 | 26.6687 | 32.5448 | 38.5427 | 44.4868
Zs-East Hobart | Risdon | 14066 | 79.7364 | 113.9611 | 117.1872 | 116.827 | 114.8591 | 113.463 | 113.5388 | 113.3192 | 115.8999 | 122.8829 | 129.0749 | 132.4119 | 101.5481 | 95.8875 | 92.5799 | 93.3221 | 91.8011 | 91.7428 | 91.8781 | 92.2887 | 93.5112 | 97.3721 | 100.5251 | 102.622 | 0 | 0 | 0 | 3.5251 | 10.8645 | 34.5078 | 66.5597 | 105.1907 | 148.944 | 196.1585 | 250.0348 | 309.0859
Zs-East Hobart | Risdon | 14067 | 60.4505 | 46.9944 | 48.3248 | 48.1762 | 47.3648 | 46.789 | 46.8203 | 46.7297 | 47.794 | 50.6736 | 53.2269 | 54.603 | 98.9989 | 62.9611 | 60.7893 | 61.2766 | 60.2779 | 60.2396 | 60.3285 | 60.5981 | 61.4008 | 63.9359 | 66.0062 | 67.3831 | 0 | 0 | 0 | 5.6543 | 17.2821 | 53.2421 | 99.1665 | 150.8946 | 205.7468 | 261.6863 | 322.8917 | 388.3049
Zs-East Hobart | Risdon | 14068 | 125.4829 | 125.5444 | 129.0984 | 128.7016 | 126.5337 | 124.9957 | 125.0793 | 124.8373 | 127.6803 | 135.3731 | 142.1944 | 145.8706 | 178.6573 | 173.7206 | 167.7282 | 169.0728 | 166.3172 | 166.2116 | 166.4567 | 167.2007 | 169.4154 | 176.4103 | 182.1225 | 185.9215 | 0 | 0 | 0 | 3.613 | 10.6858 | 31.5333 | 57.035 | 84.8183 | 113.7395 | 143.2471 | 176.2306 | 212.97
Zs-East Hobart | Risdon | 14069 | 202.2456 | 124.8444 | 128.3786 | 127.984 | 125.8282 | 124.2988 | 124.3818 | 124.1412 | 126.9684 | 134.6183 | 141.4016 | 145.0573 | 148.4557 | 133.8944 | 129.2758 | 130.3122 | 128.1883 | 128.1069 | 128.2958 | 128.8692 | 130.5762 | 135.9675 | 140.3702 | 143.2982 | 0 | 0 | 0 | 7.889 | 22.1492 | 62.0563 | 109.5446 | 160.7257 | 213.8197 | 267.7046 | 327.0784 | 391.3723
Zs-East Hobart | Risdon | 14070 | 151.2155 | 146.7 | 150.8528 | 150.3892 | 147.856 | 146.0588 | 146.1564 | 145.8737 | 149.1958 | 158.1849 | 166.1556 | 170.4513 | 194.9709 | 180.3726 | 174.1507 | 175.5468 | 172.6856 | 172.576 | 172.8306 | 173.603 | 175.9025 | 183.1653 | 189.0962 | 193.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14071 | 163.4964 | 163.8889 | 168.5283 | 168.0103 | 165.1803 | 163.1725 | 163.2816 | 162.9657 | 166.6771 | 176.7194 | 185.6241 | 190.4232 | 179.3901 | 172.2063 | 166.2661 | 167.599 | 164.8674 | 164.7627 | 165.0057 | 165.7432 | 167.9386 | 174.8726 | 180.535 | 184.3009 | 262.8721 | 283.5795 | 312.5971 | 359.2358 | 408.3922 | 527.6802 | 649.1498 | 760.2951 | 857.8753 | 941.7468 | 1020.2917 | 1090.7848
Zs-Geilston Bay | Lindisfarne | 26161 | 170.3333 | 93.0944 | 95.7298 | 95.4355 | 93.828 | 92.6875 | 92.7495 | 92.5701 | 94.6783 | 100.3826 | 105.4408 | 108.1668 | 153.1883 | 251.9322 | 243.2418 | 245.1918 | 241.1955 | 241.0424 | 241.3979 | 242.4769 | 245.6886 | 255.8328 | 264.1167 | 269.6261 | 302.6172 | 356.574 | 412.6309 | 460.9246 | 503.5071 | 604.8903 | 705.7745 | 795.6934 | 872.4566 | 936.6164 | 995.154 | 1048.1878
Zs-Geilston Bay | Lindisfarne | 26162 | 38.0329 | 88.4778 | 90.9824 | 90.7028 | 89.175 | 88.091 | 88.1499 | 87.9794 | 89.9831 | 95.4045 | 100.2119 | 102.8027 | 178.781 | 163.7608 | 158.1119 | 159.3795 | 156.7818 | 156.6823 | 156.9134 | 157.6147 | 159.7024 | 166.2963 | 171.681 | 175.2622 | 249.5069 | 306.0355 | 332.3841 | 378.2432 | 405.7896 | 471.8873 | 538.1979 | 597.7811 | 649.0396 | 692.1851 | 731.796 | 767.8768
Zs-Geilston Bay | Lindisfarne | 26163 | 69.5738 | 52.8222 | 54.3175 | 54.1506 | 53.2385 | 52.5913 | 52.6265 | 52.5247 | 53.7209 | 56.9576 | 59.8276 | 61.3744 | 109.4599 | 93.5056 | 90.2802 | 91.0039 | 89.5207 | 89.4639 | 89.5958 | 89.9963 | 91.1883 | 94.9534 | 98.028 | 100.0728 | 683.7563 | 788.4756 | 1010.7338 | 1093.3889 | 1157.5405 | 1312.8637 | 1470.6718 | 1614.7299 | 1740.8497 | 1848.8363 | 1949.428 | 2038.1479
Zs-Geilston Bay | Lindisfarne | 26164 | 188.284 | 114.6556 | 117.9013 | 117.5389 | 115.5591 | 114.1544 | 114.2307 | 114.0097 | 116.6062 | 123.6317 | 129.8614 | 133.2188 | 218.9563 | 223.3207 | 215.6173 | 217.3459 | 213.8034 | 213.6677 | 213.9828 | 214.9392 | 217.7862 | 226.7784 | 234.1215 | 239.0052 | 167.3144 | 184.3136 | 208.9569 | 227.49 | 239.7493 | 268.9243 | 297.9644 | 323.8658 | 345.9944 | 364.5003 | 381.389 | 396.6889
Zs-Geilston Bay | Lindisfarne | 26165 | 102.3143 | 72.1611 | 74.2039 | 73.9758 | 72.7297 | 71.8457 | 71.8937 | 71.7546 | 73.3888 | 77.8105 | 81.7313 | 83.8443 | 143.4032 | 111.4309 | 107.5871 | 108.4496 | 106.682 | 106.6143 | 106.7715 | 107.2488 | 108.6693 | 113.1562 | 116.8202 | 119.257 | 155.2946 | 213.7492 | 310.2872 | 352.1612 | 376.1587 | 433.1704 | 489.8019 | 540.1923 | 583.1258 | 618.9212 | 651.4764 | 680.8565
Zs-Geilston Bay | Lindisfarne | 26166 | 54.943 | 44.9778 | 46.251 | 46.1089 | 45.3322 | 44.7812 | 44.8111 | 44.7244 | 45.743 | 48.499 | 50.9428 | 52.2599 | 94.6895 | 86.4149 | 83.434 | 84.1029 | 82.7322 | 82.6796 | 82.8016 | 83.1717 | 84.2733 | 87.7529 | 90.5943 | 92.4841 | 312.9922 | 371.6944 | 384.5445 | 444.9198 | 486.8686 | 587.3263 | 687.9468 | 778.2541 | 855.89 | 921.2242 | 981.225 | 1035.9256
Zs-Geilston Bay | Lindisfarne | 26167 | 139.9584 | 116.1569 | 119.4451 | 119.078 | 117.0723 | 115.6492 | 115.7265 | 115.5026 | 118.1331 | 125.2506 | 131.5619 | 134.9632 | 233.2233 | 213.3248 | 205.9662 | 207.6174 | 204.2335 | 204.1039 | 204.4049 | 205.3185 | 208.038 | 216.6277 | 223.6421 | 228.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Geilston Bay | Lindisfarne | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292.0394 | 392.6701 | 466.4343 | 502.6159 | 529.9583 | 595.7192 | 661.5659 | 720.3669 | 770.4556 | 812.0922 | 849.7886 | 883.6352
Zs-Howrah | Mornington | 22323 | 68.8897 | 56.6228 | 58.2257 | 58.0467 | 57.069 | 56.3753 | 56.413 | 56.3038 | 57.5861 | 61.0557 | 64.1322 | 65.7902 | 104.239 | 94.0092 | 90.7664 | 91.494 | 90.0028 | 89.9456 | 90.0783 | 90.4809 | 91.6794 | 95.4647 | 98.5559 | 100.6117 | 102.2427 | 156.5537 | 168.6242 | 186.6092 | 215.3014 | 284.8247 | 355.4178 | 419.7051 | 475.7632 | 523.5422 | 567.8861 | 608.6468
Zs-Howrah | Mornington | 22324 | 98.6559 | 83.57 | 85.9357 | 85.6716 | 84.2285 | 83.2047 | 83.2603 | 83.0993 | 84.9918 | 90.1125 | 94.6532 | 97.1003 | 145.9686 | 140.8127 | 135.9553 | 137.0453 | 134.8116 | 134.726 | 134.9248 | 135.5278 | 137.3229 | 142.9929 | 147.623 | 150.7023 | 483.4361 | 655.4993 | 752.816 | 822.8176 | 869.3647 | 981.7099 | 1095.0464 | 1197.4104 | 1285.8818 | 1360.6554 | 1429.5474 | 1492.4922
Zs-Howrah | Mornington | 22325 | 98.7317 | 84.9983 | 87.4045 | 87.1358 | 85.6681 | 84.6268 | 84.6834 | 84.5196 | 86.4444 | 91.6527 | 96.271 | 98.7599 | 175.0863 | 150.7481 | 145.5481 | 146.7149 | 144.3237 | 144.232 | 144.4448 | 145.0904 | 147.0122 | 153.0821 | 158.039 | 161.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Howrah | Mornington | 22326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.8623 | 441.0173 | 587.415 | 624.9288 | 673.1147 | 789.8751 | 908.0629 | 1015.2409 | 1108.5002 | 1188.2637 | 1263.1892 | 1333.5994
Zs-Howrah | Mornington | 22328 | 139.0604 | 123.5639 | 127.0618 | 126.6712 | 124.5376 | 123.0238 | 123.106 | 122.8679 | 125.6661 | 133.2375 | 139.9512 | 143.5694 | 198.2958 | 193.5743 | 186.8969 | 188.3953 | 185.3247 | 185.207 | 185.4802 | 186.3092 | 188.777 | 196.5714 | 202.9364 | 207.1695 | 574.644 | 718.7111 | 810.0778 | 880.8856 | 934.9104 | 1064.6092 | 1194.7798 | 1311.773 | 1412.4221 | 1497.1202 | 1574.8405 | 1645.583
Zs-Howrah | Mornington | 22329 | 120.0448 | 103.0733 | 105.9912 | 105.6654 | 103.8856 | 102.6228 | 102.6914 | 102.4927 | 104.8269 | 111.1428 | 116.7431 | 119.7613 | 276.3709 | 187.5991 | 181.1279 | 182.58 | 179.6042 | 179.4901 | 179.7549 | 180.5583 | 182.9499 | 190.5037 | 196.6722 | 200.7747 | 45.4667 | 49.5587 | 54.5145 | 61.1267 | 65.5822 | 76.3359 | 87.1846 | 96.983 | 105.4515 | 112.6089 | 119.2033 | 125.2284
Zs-Howrah | Mornington | 22330 | 10.594 | 6.0505 | 6.2218 | 6.2027 | 6.0982 | 6.0241 | 6.0281 | 6.0165 | 6.1535 | 6.5242 | 6.853 | 7.0301 | 14.5145 | 15.1273 | 14.6054 | 14.7225 | 14.4826 | 14.4734 | 14.4947 | 14.5595 | 14.7524 | 15.3615 | 15.8589 | 16.1897 | 880.6274 | 1068.3141 | 1229.0017 | 1329.0829 | 1390.4975 | 1538.0907 | 1686.3777 | 1819.7927 | 1934.6848 | 2031.4604 | 2120.341 | 2201.3066
Zs-Howrah | Mornington | 22331 | 123.4277 | 124.3706 | 127.8913 | 127.4982 | 125.3506 | 123.8269 | 123.9097 | 123.67 | 126.4865 | 134.1073 | 140.8648 | 144.5067 | 234.1418 | 200.8049 | 193.8782 | 195.4325 | 192.2472 | 192.1252 | 192.4085 | 193.2685 | 195.8284 | 203.914 | 210.5168 | 214.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-New Town | Risdon | 16091 | 121.9411 | 97.2944 | 100.0487 | 99.7412 | 98.0611 | 96.8692 | 96.9339 | 96.7464 | 98.9497 | 104.9114 | 110.1978 | 113.0468 | 204.1462 | 192.6888 | 190.9285 | 199.5248 | 196.2728 | 196.1482 | 196.4375 | 197.3155 | 199.929 | 208.1839 | 214.9249 | 219.4082 | 263.276 | 297.6028 | 349.6252 | 401.6825 | 466.2134 | 621.3268 | 778.1337 | 921.0659 | 1046.5855 | 1154.9363 | 1257.194 | 1352.9366
Zs-New Town | Risdon | 16092 | 93.7603 | 72.1957 | 74.2394 | 74.0112 | 96.9674 | 95.7887 | 95.8528 | 95.6673 | 97.8461 | 103.7413 | 108.9687 | 111.7859 | 131.1657 | 124.3678 | 124.9642 | 133.0317 | 130.8634 | 130.7803 | 130.9732 | 131.5586 | 133.3012 | 138.8051 | 143.2996 | 146.2888 | 200.7433 | 249.302 | 281.7691 | 342.7424 | 379.1378 | 465.2527 | 550.4139 | 625.8741 | 689.9539 | 743.2702 | 791.736 | 835.5216
Zs-New Town | Risdon | 16093 | 92.5129 | 88.5333 | 91.0396 | 90.7597 | 113.4338 | 112.055 | 112.1299 | 111.9129 | 114.4617 | 121.358 | 127.4731 | 130.7687 | 128.6872 | 122.166 | 122.8384 | 130.8888 | 128.7555 | 128.6738 | 128.8636 | 129.4395 | 131.154 | 136.5692 | 140.9914 | 143.9324 | 4.6 | 4.6 | 11.776 | 32.9314 | 69.8039 | 166.3925 | 270.8259 | 370.3586 | 459.6409 | 536.7245 | 608.3044 | 673.5094
Zs-New Town | Risdon | 16094 | 162.1109 | 59.75 | 61.4414 | 61.2526 | 84.4236 | 83.3974 | 83.4532 | 83.2917 | 85.1886 | 90.3213 | 94.8725 | 97.3252 | 236.6309 | 231.0786 | 223.1076 | 224.8962 | 221.2307 | 221.0903 | 221.4164 | 222.406 | 225.3519 | 234.6564 | 242.2546 | 247.308 | 261.8119 | 296.0549 | 361.2152 | 409.2214 | 453.1564 | 558.6151 | 664.4365 | 759.5228 | 841.3026 | 910.0993 | 973.2041 | 1030.618
Zs-New Town | Risdon | 16095 | 72.1224 | 130.4889 | 134.1828 | 133.7704 | 155.72 | 153.8271 | 153.93 | 153.6322 | 157.131 | 166.5982 | 174.9929 | 179.517 | 75 | 77.0719 | 74.4133 | 75.0098 | 73.7873 | 73.7404 | 73.8492 | 74.1793 | 75.1618 | 78.2652 | 80.7994 | 82.4848 | 61.338 | 66.5598 | 79.2232 | 95.2792 | 123.5345 | 202.4049 | 296.3088 | 397.45 | 501.6324 | 605.5136 | 716.547 | 831.8707
Zs-New Town | Risdon | 16096 | 122.9727 | 105.45 | 108.4351 | 108.1018 | 106.281 | 104.9891 | 105.0593 | 104.856 | 107.244 | 113.7055 | 119.435 | 122.5228 | 224.0123 | 224.4705 | 216.7274 | 218.4649 | 214.9042 | 214.7678 | 215.0846 | 216.0459 | 218.9075 | 227.946 | 235.3269 | 240.2357 | 342.4872 | 426.5533 | 507.6712 | 567.8775 | 624.6751 | 762.5873 | 903.3392 | 1032.9779 | 1148.4352 | 1250.2285 | 1349.3097 | 1446.0083
Zs-New Town | Risdon | 16097 | 45.3333 | 42.9444 | 44.1601 | 44.0244 | 43.2829 | 42.7567 | 42.7853 | 42.7025 | 43.6751 | 46.3065 | 48.6398 | 49.8973 | 62.9122 | 50.5532 | 48.8094 | 49.2007 | 48.3988 | 48.3681 | 48.4394 | 48.6559 | 49.3004 | 51.3359 | 52.9982 | 54.1037 | 54.1133 | 61.5407 | 67.3642 | 76.9215 | 91.7705 | 126.6453 | 160.854 | 190.9104 | 216.221 | 237.1135 | 255.9681 | 272.8925
Zs-New Town | Risdon | 16098 | 125.2147 | 97.3889 | 100.1458 | 99.838 | 98.1563 | 96.9632 | 97.028 | 96.8403 | 99.0458 | 105.0133 | 110.3048 | 113.1565 | 212.7631 | 205.6194 | 198.5266 | 200.1181 | 196.8565 | 196.7315 | 197.0217 | 197.9023 | 200.5236 | 208.803 | 215.564 | 220.0606 | 416.2477 | 524.4815 | 567.857 | 611.1558 | 670.9983 | 819.5162 | 974.5635 | 1120.2138 | 1251.5274 | 1367.3468 | 1478.4971 | 1583.8921
Zs-Rosny Park | Mornington | 23340 | 95.5333 | 87.4611 | 89.937 | 89.6606 | 88.1503 | 87.0788 | 87.137 | 86.9685 | 88.9491 | 94.3083 | 99.0604 | 101.6214 | 88.5388 | 76.8314 | 74.1811 | 74.7758 | 73.5571 | 73.5104 | 73.6188 | 73.9478 | 74.9273 | 78.021 | 80.5473 | 82.2275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Mornington | 23341 | 82.9543 | 72.0361 | 74.0753 | 73.8477 | 72.6038 | 71.7212 | 71.7692 | 71.6303 | 73.2617 | 77.6757 | 81.5897 | 83.699 | 129.9241 | 119.9652 | 115.8271 | 116.7556 | 114.8527 | 114.7797 | 114.949 | 115.4628 | 116.9922 | 121.8227 | 125.7673 | 128.3908 | 287.312 | 469.842 | 494.7493 | 532.3506 | 568.4817 | 654.7139 | 740.7461 | 817.606 | 883.3264 | 938.2908 | 988.4197 | 1033.7764
Zs-Rosny Park | Mornington | 23342 | 149.3584 | 90.9044 | 93.4778 | 93.1905 | 91.6208 | 90.5071 | 90.5676 | 90.3924 | 92.451 | 98.0212 | 102.9604 | 105.6222 | 209.9646 | 190.2306 | 183.6687 | 185.1411 | 182.1235 | 182.0079 | 182.2764 | 183.0911 | 185.5162 | 193.176 | 199.431 | 203.5911 | 403.3243 | 516.201 | 640.8588 | 710.1046 | 751.3135 | 850.7794 | 951.1321 | 1041.7811 | 1120.1414 | 1186.3845 | 1247.4344 | 1303.2335
Zs-Rosny Park | Mornington | 23343 | 121.7079 | 129.8233 | 133.4984 | 133.0881 | 130.8464 | 129.2559 | 129.3423 | 129.0921 | 132.032 | 139.987 | 147.0408 | 150.8423 | 189.9266 | 176.7934 | 170.6949 | 172.0634 | 169.259 | 169.1515 | 169.401 | 170.1582 | 172.412 | 179.5307 | 185.3439 | 189.2101 | 150.8688 | 167.1103 | 195.0728 | 226.8008 | 260.6104 | 342.2124 | 424.5346 | 498.8868 | 563.1481 | 617.46 | 667.4998 | 713.2198
Zs-Rosny Park | Mornington | 23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Mornington | 23347 | 81.5108 | 61.0162 | 62.7435 | 62.5506 | 61.497 | 60.7495 | 60.7901 | 60.6725 | 62.0543 | 65.7931 | 69.1083 | 70.895 | 121.6255 | 132.6265 | 128.0515 | 129.0781 | 126.9743 | 126.8937 | 127.0808 | 127.6488 | 129.3396 | 134.6799 | 139.0409 | 141.9412 | 392.7866 | 480.3851 | 577.7174 | 623.8692 | 652.4556 | 722.048 | 792.8371 | 857.2424 | 913.2408 | 960.7819 | 1004.7162 | 1044.9274
Zs-Rosny Park | Mornington | 23348 | 92.6928 | 77.8772 | 80.0818 | 79.8357 | 78.4909 | 77.5368 | 77.5887 | 77.4386 | 79.2022 | 83.9741 | 88.2055 | 90.4859 | 150.6928 | 149.0096 | 143.8695 | 145.0229 | 142.6592 | 142.5686 | 142.7789 | 143.4171 | 145.3167 | 151.3167 | 156.2163 | 159.475 | 418.4606 | 472.1844 | 532.6808 | 588.2025 | 629.0391 | 727.2215 | 825.9433 | 914.8948 | 991.7049 | 1056.7198 | 1116.9437 | 1172.6108
Zs-Sandy Bay | Creek Road | 12017 | 116.2599 | 69.485 | 71.452 | 71.2324 | 70.0325 | 69.1813 | 69.2275 | 69.0936 | 70.6671 | 74.9248 | 78.7002 | 80.7349 | 169.5196 | 156.2893 | 150.8981 | 152.1078 | 149.6287 | 149.5337 | 149.7542 | 150.4236 | 152.416 | 158.7091 | 163.8481 | 167.2659 | 658.6955 | 749.3254 | 884.4896 | 953.9563 | 1007.2855 | 1137.9241 | 1272.3069 | 1396.5565 | 1506.8086 | 1602.6637 | 1693.659 | 1779.5215
Zs-Sandy Bay | Creek Road | 12018 | 99.4679 | 63.3859 | 65.1802 | 64.9799 | 63.8854 | 63.1088 | 63.151 | 63.0288 | 64.4643 | 68.3482 | 71.7922 | 73.6483 | 158.075 | 151.9868 | 146.744 | 147.9204 | 145.5095 | 145.4171 | 145.6316 | 146.2825 | 148.2201 | 154.34 | 159.3375 | 162.6612 | 617.042 | 731.4658 | 799.7585 | 853.2282 | 900.5093 | 1014.6256 | 1129.749 | 1233.7268 | 1323.593 | 1399.5455 | 1469.5236 | 1533.4608
Zs-Sandy Bay | Creek Road | 12019 | 121.1366 | 88.2211 | 90.7184 | 90.4396 | 88.9162 | 87.8354 | 87.8942 | 87.7241 | 89.722 | 95.1277 | 99.9211 | 102.5044 | 215.0868 | 187.9984 | 181.5134 | 182.9686 | 179.9864 | 179.8722 | 180.1375 | 180.9426 | 183.3393 | 190.9092 | 197.0908 | 201.2021 | 247.1879 | 277.8928 | 322.9747 | 401.4028 | 459.5006 | 607.7568 | 766.3211 | 918.0887 | 1056.6367 | 1179.6497 | 1297.9289 | 1409.9312
Zs-Sandy Bay | Creek Road | 12030 | 112.7079 | 66.9561 | 68.8515 | 68.6399 | 67.4837 | 66.6635 | 66.708 | 66.579 | 68.0952 | 72.198 | 75.836 | 77.7966 | 171.6398 | 169.3139 | 163.4735 | 164.784 | 162.0983 | 161.9954 | 162.2343 | 162.9594 | 165.1179 | 171.9354 | 177.5027 | 181.2054 | 585.0962 | 722.3401 | 826.5732 | 881.6612 | 929.4422 | 1046.6964 | 1168.1474 | 1282.0144 | 1385.3256 | 1477.9642 | 1569.3788 | 1659.5627
Zs-Sandy Bay | Creek Road | 12031 | 146.4817 | 93.441 | 96.0861 | 95.7908 | 94.1773 | 93.0326 | 93.0947 | 92.9146 | 95.0307 | 100.7563 | 105.8333 | 108.5694 | 244.6077 | 202.6335 | 195.6437 | 197.2122 | 193.9979 | 193.8747 | 194.1607 | 195.0285 | 197.6117 | 205.7709 | 212.4338 | 216.8651 | 225.3937 | 256.4387 | 303.0667 | 325.4465 | 342.1567 | 381.9271 | 421.5068 | 456.7938 | 486.9205 | 512.0918 | 535.0359 | 555.7913
Zs-Sandy Bay | Creek Road | 12032 | 66.7503 | 65.6983 | 67.5581 | 67.3505 | 66.216 | 65.4112 | 65.4549 | 65.3283 | 66.8161 | 70.8417 | 74.4114 | 76.3352 | 111.0559 | 103.7568 | 100.1777 | 100.9808 | 99.335 | 99.2719 | 99.4183 | 99.8627 | 101.1854 | 105.3632 | 108.7749 | 111.0439 | 362.6905 | 467.7855 | 559.9177 | 607.5644 | 639.0806 | 714.8755 | 791.2108 | 860.2406 | 920.2281 | 971.5024 | 1019.6371 | 1064.8435
Zs-Sandy Bay | Creek Road | 12033 | 42.5436 | 22.5739 | 23.2129 | 23.1416 | 22.7518 | 22.4752 | 22.4902 | 22.4467 | 22.9579 | 24.3411 | 25.5677 | 26.2287 | 67.0621 | 64.7075 | 62.4754 | 62.9763 | 61.9499 | 61.9105 | 62.0018 | 62.279 | 63.1039 | 65.7094 | 67.837 | 69.2521 | 384.9888 | 427.8192 | 478.7081 | 510.1204 | 526.3085 | 565.3028 | 604.5659 | 639.9627 | 670.5024 | 696.271 | 719.9756 | 741.6015
Zs-Sandy Bay | Creek Road | 12034 | 2.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Sandy Bay | Creek Road | 12035 | 100.5143 | 68.2735 | 70.2062 | 69.9904 | 68.8115 | 67.9751 | 68.0205 | 67.8889 | 69.435 | 73.6185 | 77.328 | 79.3272 | 177.6698 | 174.5904 | 168.5679 | 169.9193 | 167.1499 | 167.0437 | 167.2901 | 168.0378 | 170.2636 | 177.2936 | 183.0344 | 186.8524 | 403.6917 | 510.5496 | 581.994 | 640.1492 | 687.8948 | 803.1384 | 919.4094 | 1024.4377 | 1115.2281 | 1191.9793 | 1262.7138 | 1327.3646
Zs-Sandy Bay | Creek Road | 12036 | 149.766 | 138.8356 | 142.7658 | 142.3269 | 139.9296 | 138.2287 | 138.3211 | 138.0535 | 141.1976 | 149.7047 | 157.2482 | 161.3136 | 220.5128 | 224.0597 | 216.3308 | 218.0651 | 214.5109 | 214.3747 | 214.6909 | 215.6505 | 218.5069 | 227.5288 | 234.8962 | 239.7961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Sandy Bay | Creek Road | 12037 | 121.8171 | 106.3939 | 109.4057 | 109.0694 | 107.2323 | 105.9289 | 105.9997 | 105.7946 | 108.204 | 114.7233 | 120.5041 | 123.6195 | 160.1629 | 154.8522 | 149.5106 | 150.7092 | 148.2529 | 148.1587 | 148.3773 | 149.0404 | 151.0145 | 157.2498 | 162.3416 | 165.7279 | 48.8007 | 61.2619 | 73.4623 | 82.3892 | 92.2866 | 115.7664 | 139.0549 | 159.7594 | 177.4078 | 192.1545 | 205.6252 | 217.8628
Zs-Sandy Bay | Creek Road | 12038 | 106.3002 | 70.7668 | 72.7701 | 72.5464 | 71.3245 | 70.4575 | 70.5046 | 70.3682 | 71.9708 | 76.307 | 80.152 | 82.2242 | 157.6949 | 146.3608 | 141.3121 | 142.445 | 140.1233 | 140.0344 | 140.2409 | 140.8677 | 142.7336 | 148.6269 | 153.4395 | 156.6401 | 411.6235 | 466.1309 | 541.4237 | 600.8215 | 630.901 | 703.4874 | 776.7516 | 843.0071 | 900.3906 | 949.0338 | 994.0276 | 1035.3399
Zs-Sandy Bay | Creek Road | 12039 | 108.1286 | 107.1872 | 110.2215 | 109.8827 | 108.0319 | 106.7187 | 106.7901 | 106.5835 | 109.0108 | 115.5787 | 121.4026 | 124.5413 | 202.9551 | 185.6811 | 179.2761 | 180.7133 | 177.7679 | 177.6551 | 177.9171 | 178.7123 | 181.0794 | 188.556 | 194.6615 | 198.722 | 121.4641 | 165.033 | 194.8722 | 236.7798 | 301.3295 | 459.4418 | 620.5668 | 766.7151 | 892.8158 | 998.6677 | 1095.1823 | 1182.2651
Zs-Summerleas | Kingston 33kV | 32374 | 131.7144 | 106.6611 | 109.6805 | 109.3434 | 107.5016 | 106.1949 | 106.2659 | 106.0603 | 108.4757 | 115.0114 | 120.8067 | 123.93 | 244.2669 | 214.1523 | 206.7651 | 208.4227 | 205.0257 | 204.8956 | 205.1978 | 206.1149 | 208.845 | 217.468 | 224.5096 | 229.1928 | 813.9135 | 914.9937 | 1054.4874 | 1173.5565 | 1233.9229 | 1379.6113 | 1526.5909 | 1659.3625 | 1774.1499 | 1871.2096 | 1960.691 | 2042.5139
Zs-Summerleas | Kingston 33kV | 32377 | 118.7085 | 119.8167 | 123.2085 | 122.8298 | 120.7608 | 119.293 | 119.3727 | 119.1418 | 121.8551 | 129.1969 | 135.707 | 139.2155 | 167.0216 | 151.5546 | 146.3267 | 147.4998 | 145.0957 | 145.0036 | 145.2175 | 145.8666 | 147.7986 | 153.9011 | 158.8844 | 162.1987 | 9.54 | 14.3112 | 21.4241 | 34.1218 | 57.7163 | 123.9598 | 200.8418 | 279.3254 | 354.3464 | 422.8898 | 489.7429 | 553.2691
Zs-Summerleas | Kingston 33kV | 32379 | 155.8666 | 128.1722 | 131.8006 | 131.3955 | 129.1822 | 127.612 | 127.6973 | 127.4503 | 130.3528 | 138.2066 | 145.1707 | 148.9238 | 278.1166 | 247.5286 | 250.111 | 252.1161 | 248.007 | 247.8495 | 248.2151 | 249.3245 | 252.6269 | 263.0576 | 271.5754 | 277.2404 | 1031.628 | 1188.4558 | 1355.3893 | 1481.5198 | 1563.0361 | 1757.7429 | 1952.3698 | 2126.7614 | 2276.4503 | 2402.1913 | 2517.393 | 2622.0871
Zs-Trial Harbour | Rosebery 44kV | 99981 | 35.9056 | 26.9092 | 27.6709 | 27.5859 | 27.1212 | 26.7916 | 26.8095 | 26.7576 | 27.367 | 29.0159 | 30.4779 | 31.2659 | 52.7418 | 48.5295 | 46.8555 | 47.2311 | 46.4613 | 46.4318 | 46.5003 | 46.7082 | 47.3268 | 49.2809 | 50.8766 | 51.9379 | 88.8022 | 96.7338 | 112.1165 | 136.8403 | 167.8976 | 246.7371 | 330.8126 | 411.4757 | 485.9638 | 553.7069 | 621.365 | 688.743
Zs-Trial Harbour | Rosebery 44kV | 99982 | 202.8644 | 198.4722 | 204.0906 | 203.4633 | 200.0362 | 197.6047 | 197.7368 | 197.3543 | 201.8488 | 214.0102 | 224.794 | 230.6057 | 60.3333 | 207.7778 | 200.6105 | 202.2188 | 198.9229 | 198.7966 | 199.0898 | 199.9797 | 202.6285 | 210.9948 | 217.8268 | 222.3706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Rosebery 44kV | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-West Hobart | Creek Road | 13043 | 45.4081 | 31.3389 | 32.226 | 32.127 | 31.5858 | 31.2019 | 31.2228 | 31.1624 | 31.8721 | 33.7924 | 35.4951 | 36.4128 | 83.3441 | 73.1538 | 70.6304 | 71.1966 | 70.0362 | 69.9917 | 70.095 | 70.4083 | 71.3409 | 74.2864 | 76.6919 | 78.2916 | 100.6974 | 113.3564 | 139.7779 | 157.6201 | 179.3728 | 231.4577 | 283.581 | 330.2947 | 370.3802 | 404.0435 | 434.8883 | 462.9395
Zs-West Hobart | Creek Road | 13044 | 110.9798 | 173.3 | 178.2058 | 177.6581 | 174.6656 | 172.5425 | 172.6579 | 172.3238 | 176.2484 | 186.8673 | 196.2834 | 201.358 | 181.8303 | 177.3039 | 171.1878 | 172.5602 | 169.7477 | 169.6399 | 169.8901 | 170.6495 | 172.9098 | 180.0491 | 185.8791 | 189.7564 | 6.5664 | 6.5664 | 6.5664 | 21.8666 | 49.226 | 123.7986 | 208.6751 | 294.509 | 376.5427 | 452.0602 | 526.6742 | 598.7117
Zs-West Hobart | Creek Road | 13045 | 146.6747 | 115.5778 | 118.8496 | 118.4843 | 116.4885 | 115.0726 | 115.1495 | 114.9267 | 117.5441 | 124.6261 | 130.9059 | 134.2903 | 264.519 | 229.7146 | 221.7907 | 223.5687 | 219.9249 | 219.7852 | 220.1094 | 221.0932 | 224.0217 | 233.2713 | 240.8247 | 245.8482 | 926.1013 | 1119.8395 | 1303.2469 | 1403.6228 | 1481.9648 | 1672.3433 | 1866.9181 | 2046.2648 | 2205.7104 | 2345.4009 | 2479.688 | 2608.2661
Zs-West Hobart | Creek Road | 13046 | 53.3908 | 53.25 | 54.7574 | 54.5891 | 53.6696 | 53.0172 | 53.0527 | 52.9501 | 54.1559 | 57.4188 | 60.3121 | 61.8714 | 66.7657 | 77.5001 | 74.8268 | 75.4266 | 74.1973 | 74.1502 | 74.2596 | 74.5915 | 75.5795 | 78.7001 | 81.2484 | 82.9432 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Zs-West Hobart | Creek Road | 13047 | 42.7804 | 46.3667 | 89.6723 | 89.3967 | 87.8909 | 86.8225 | 86.8806 | 86.7125 | 88.6873 | 94.0307 | 98.7688 | 101.3223 | 77.6386 | 55.0762 | 53.1763 | 53.6026 | 52.729 | 52.6955 | 52.7732 | 53.0091 | 53.7112 | 55.9289 | 57.7399 | 58.9443 | 0 | 0 | 0 | 11.2783 | 29.2117 | 72.9185 | 118.0417 | 160.2582 | 198.3707 | 232.1357 | 264.7276 | 295.8069
Zs-West Hobart | Creek Road | 13048 | 87.4009 | 79.7833 | 124.0349 | 123.6537 | 121.5709 | 120.0931 | 120.1734 | 119.9409 | 122.6725 | 130.0635 | 136.6173 | 140.1493 | 130.3457 | 130.9214 | 126.4053 | 127.4186 | 125.3419 | 125.2623 | 125.4471 | 126.0078 | 127.6768 | 132.9484 | 137.2533 | 140.1164 | 34.67 | 34.67 | 34.67 | 54.0978 | 87.9007 | 177.6926 | 277.4413 | 375.9439 | 467.783 | 550.0792 | 629.0341 | 702.8741
Zs-West Hobart | Creek Road | 13049 | 101.1609 | 64.0056 | 107.8105 | 107.4791 | 105.6688 | 104.3843 | 104.4541 | 104.252 | 106.6263 | 113.0505 | 118.747 | 121.817 | 159.6904 | 151.9299 | 146.6891 | 147.8651 | 145.4551 | 145.3628 | 145.5772 | 146.2278 | 148.1647 | 154.2822 | 159.2779 | 162.6004 | 250.8377 | 286.8219 | 374.9651 | 417.8176 | 471.5336 | 605.6522 | 747.7778 | 884.9633 | 1013.8163 | 1133.7468 | 1256.3392 | 1380.6887
Zs-West Hobart | Creek Road | 13050 | 52.2443 | 45.2556 | 88.5297 | 88.2576 | 86.771 | 85.7163 | 85.7736 | 85.6076 | 87.5573 | 92.8326 | 97.5104 | 100.0313 | 80.3642 | 51.6757 | 49.8931 | 50.2931 | 49.4734 | 49.442 | 49.5149 | 49.7362 | 50.395 | 52.4758 | 54.175 | 55.305 | 88.3163 | 95.1455 | 119.7654 | 130.7865 | 144.9675 | 179.1979 | 213.7357 | 244.937 | 271.9123 | 294.7203 | 315.7449 | 334.9663
Zs-West Hobart | Creek Road | 13052 | 146.0604 | 137.9389 | 141.8437 | 141.4077 | 139.0259 | 137.336 | 137.4278 | 137.1619 | 140.2856 | 148.7379 | 156.2326 | 160.2718 | 241.1405 | 230.5289 | 222.5769 | 224.3612 | 220.7045 | 220.5643 | 220.8897 | 221.8769 | 224.8158 | 234.0982 | 241.6784 | 246.7197 | 110.0848 | 122.3229 | 143.3479 | 171.4534 | 209.0968 | 302.2672 | 399.8996 | 493.0671 | 580.0492 | 661.6722 | 747.8121 | 840.7462
Zs-West Hobart | Creek Road | 13053 | 95.1687 | 68.7722 | 70.719 | 70.5017 | 69.3142 | 68.4716 | 68.5174 | 68.3848 | 69.9422 | 74.1563 | 77.8929 | 79.9067 | 150.9579 | 140.046 | 135.2151 | 136.2991 | 134.0776 | 133.9925 | 134.1901 | 134.7899 | 136.5752 | 142.2143 | 146.8192 | 149.8818 | 38.0058 | 40.5913 | 51.4034 | 86.1973 | 133.9272 | 262.3044 | 408.6106 | 559.4182 | 709.0649 | 854.5234 | 1008.3124 | 1168.6095
Zs-West Hobart | Creek Road | 13054 | 59.8133 | 56.7148 | 58.3202 | 58.141 | 57.1617 | 56.4669 | 56.5046 | 56.3953 | 57.6796 | 61.1548 | 64.2364 | 65.8971 | 80.9392 | 79.4501 | 76.7094 | 77.3244 | 76.0641 | 76.0158 | 76.128 | 76.4682 | 77.4811 | 80.6802 | 83.2926 | 85.0301 | 0 | 0 | 0 | 3.985 | 12.0628 | 36.7919 | 68.1771 | 103.3684 | 140.4572 | 177.8671 | 218.0428 | 259.8162
Zs-West Hobart | Creek Road | 13055 | 147.5841 | 84.2143 | 86.5983 | 86.3321 | 84.8779 | 83.8462 | 83.9023 | 83.74 | 85.6471 | 90.8073 | 95.383 | 97.849 | 211.8493 | 184.1565 | 177.8041 | 179.2295 | 176.3083 | 176.1964 | 176.4563 | 177.245 | 179.5926 | 187.0078 | 193.0632 | 197.0904 | 326.0837 | 439.3662 | 516.6037 | 557.0249 | 614.3729 | 757.8377 | 907.4285 | 1046.5014 | 1169.6476 | 1275.7847 | 1375.091 | 1466.9073
Zs-West Hobart | Creek Road | 13056 | 52.4416 | 51.3401 | 52.7935 | 52.6312 | 51.7447 | 51.1157 | 51.1499 | 51.0509 | 52.2136 | 55.3594 | 58.1489 | 59.6523 | 97.0009 | 166.3051 | 160.5684 | 161.8557 | 159.2177 | 159.1166 | 159.3513 | 160.0635 | 162.1836 | 168.88 | 174.3484 | 177.9852 | 52.1514 | 60.2982 | 81.947 | 104.277 | 132.202 | 198.338 | 263.7859 | 321.8023 | 371.0779 | 412.076 | 449.3376 | 482.9906
Zs-West Hobart | Creek Road | 13057 | 153.3256 | 108.2553 | 111.3198 | 110.9777 | 109.1084 | 107.7821 | 107.8542 | 107.6455 | 110.097 | 116.7304 | 122.6123 | 125.7823 | 221.9983 | 196.8057 | 190.0169 | 191.5403 | 188.4184 | 188.2988 | 188.5765 | 189.4194 | 191.9283 | 199.8529 | 206.3241 | 210.628 | 521.7969 | 588.9074 | 684.7019 | 749.4315 | 804.5854 | 936.0348 | 1068.0228 | 1187.7194 | 1292.4599 | 1382.655 | 1467.6087 | 1542.4398
Zs-West Hobart | Creek Road | 13058 | 67.2172 | 4.7667 | 4.9016 | 4.8865 | 4.8042 | 4.7458 | 4.749 | 4.7398 | 4.8478 | 5.1398 | 5.3988 | 5.5384 | 60.4773 | 5.0352 | 4.8615 | 4.9005 | 4.8206 | 4.8175 | 4.8246 | 4.8462 | 4.9104 | 5.1131 | 5.2787 | 5.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Information
TRANSMISSION - DISTRIBUTION |  | 2023 (Actuals) | 2024 (Actuals) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Load transfer point | Peaking season | General info
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Notes (see chapter 4.9 of the APR)
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Arthurs Lake (DL) | Central | Distribution lines | 110/6.6 kV | 1 | Summer
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Avoca | Eastern | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Maximum demand (peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599 |  |  | Bridgewater | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.0090368 | 0.0746 | 0.076712 | 0.076476 | 0.075188 | 0.074274 | 0.074324 | 0.07418 | 0.075869 | 0.08044 | 0.084494 | 0.086678 |  |  | Burnie | North West | Distribution lines | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Burnie Substation supply transformers (2033)
Arthurs Lake (DL) | Maximum demand (peak season) (MVA) | 0.040228 | 0.33209 | 0.34149 | 0.34044 | 0.3347 | 0.33064 | 0.33086 | 0.33022 | 0.33774 | 0.35809 | 0.37613 | 0.38585 |  |  | Chapel Street | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Maximum demand (peak season) Power factor (coincident) | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 | 0.97444 |  |  | Creek Road | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter
Arthurs Lake (DL) | Maximum demand (non-peak season) (MW) | 0.0212 | 0.0378 | 0.036496 | 0.036789 | 0.036189 | 0.036166 | 0.036219 | 0.036381 | 0.036863 | 0.038385 | 0.039628 | 0.040455 |  |  | Derby | Northern | Distribution lines | 110/22 kV | 1 | Winter
Arthurs Lake (DL) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.023668 | 0.0422 | 0.040744 | 0.041071 | 0.040402 | 0.040376 | 0.040435 | 0.040616 | 0.041154 | 0.042853 | 0.044241 | 0.045164 |  |  | Derwent Bridge | Central | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Maximum demand (non-peak season) (MVA) | 0.031774 | 0.056654 | 0.0547 | 0.055138 | 0.05424 | 0.054205 | 0.054285 | 0.054528 | 0.05525 | 0.057531 | 0.059394 | 0.060633 |  |  | Devonport | North West | Distribution lines | 110/22 kV | 3 | Winter
Arthurs Lake (DL) | Hours exceeding 95% of maximum demand | 1 | [13 empty] | Electrona | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Hours exceeding Firm capacity (continuous rating) | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 |  |  | Emu Bay (RT) | North West | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Hours exceeding Firm capacity (short-term rating) | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 | 8768.5 |  |  | George Town | Northern | Distribution lines | 110/22 kV | 2 | Winter
Arthurs Lake (DL) | Regional Diversity Factor (Summer) | 0.05686 | [13 empty] | Hadspen | Northern | Distribution lines | 110/22 kV | 2 | Winter
Arthurs Lake (DL) | Regional Diversity Factor (Winter) | 0.44974 | [13 empty] | Huon River | Kingston-South | Distribution lines | 110/11 kV | 1 | Summer
Arthurs Lake (DL) | Load transfer capacity (MVA)1 | 0.1 | [11 empty] | Waddmana |  | Kermandie | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Load transfer capacity (MVA)2 | [14 empty] | Kingston 11kV | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Proposed retirement/ replacement of Kingston Substation 110 kV circuit breakers (2033)
Arthurs Lake (DL) | Load transfer capacity (MVA)3 | [14 empty] | Kingston 33kV | Kingston-South | Sub-transmission lines | 110/33 kV | 2 | Winter | Proposed retirement/ replacement of Kingston Substation 110 kV circuit breakers (2033)
Arthurs Lake (DL) | Load transfer capacity (MVA)4 | [14 empty] | Knights Road | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Proposed retirement/ replacement of Knights Road Substation 11 kV switchgear (2032)
Arthurs Lake (DL) | Load transfer capacity (MVA)5 | [14 empty] | Lindisfarne | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Arthurs Lake (DL) | Embedded generation capacity (MVA) Units less than 100 kVA | 0.012 | [13 empty] | Meadowbank | Central | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0 | [13 empty] | Mornington | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Total | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | Summer | Mowbray | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | New Norfolk | Central | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Newton | West Cost | Distribution lines | 110/22 kV | 1 | Winter
Avoca | Maximum demand (peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617 |  |  | North Hobart | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Avoca | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.3141 | 2.7934 | 2.8724 | 2.8636 | 2.8154 | 2.7812 | 2.783 | 2.7776 | 2.8409 | 3.012 | 3.1638 | 3.2456 |  |  | Norwood | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (peak season) (MVA) | 10.364 | 8.7356 | 8.9829 | 8.9553 | 8.8044 | 8.6974 | 8.7032 | 8.6864 | 8.8842 | 9.4195 | 9.8941 | 10.1499 |  |  | Palmerston | Northern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Maximum demand (peak season) Power factor (coincident) | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 | 0.9475 |  |  | Port Latta (RT) | North West | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Summer
Avoca | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599 |  |  | Queenstown | West Coast | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.00081512 | 0.0067289 | 0.0069193 | 0.0068981 | 0.0067819 | 0.0066995 | 0.0067039 | 0.006691 | 0.0068433 | 0.0072557 | 0.0076213 | 0.0078183 |  |  | Railton | North West | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (non-peak season) (MVA) | 0.039208 | 0.32367 | 0.33283 | 0.33181 | 0.32622 | 0.32226 | 0.32247 | 0.32185 | 0.32918 | 0.34901 | 0.3666 | 0.37607 |  |  | Risdon 33kV | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter
Avoca | Hours exceeding 95% of maximum demand | 0.5 | [13 empty] | Rokeby | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Avoca | Hours exceeding Firm capacity (continuous rating) | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 |  |  | Rosebery 22kV | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Proposed retirement/ replacement of Rosebery supply transformers and associated asset replacement (2028)
Avoca | Hours exceeding Firm capacity (short-term rating) | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 | 8244 |  |  | Rosebery 44kV | West Coast | Distribution lines and transmission-connected customer | 110/44 kV | 2 | Winter
Avoca | Regional Diversity Factor (Summer) | 0.58769 | [13 empty] | Savage River DL | West Coast | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Savage River Substation supply transformers (2032)
Avoca | Regional Diversity Factor (Winter) | 0.32578 | [13 empty] | Scottsdale | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)1 | 4.6 | [11 empty] | St Marys |  | Sheffield | North West | Distribution lines | 110/22 kV | 1 | Winter | Proposed retirement/ replacement of network transformer T1 (2027)
Avoca | Load transfer capacity (MVA)2 | 4.6 | [11 empty] | Palmerston |  | Smithton | North West | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)3 | [14 empty] | Sorell | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)4 | [14 empty] | St Leonards | Northern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Load transfer capacity (MVA)5 | [14 empty] | St Marys | Eastern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Embedded generation capacity (MVA) Units less than 100 kVA | 3.267 | [13 empty] | Trevallyn | Northern | Distribution lines | 110/22 kV | 3 | Winter
Avoca | Embedded generation capacity (MVA) Units greater than 100 kVA | 0 | [13 empty] | Triabunna (RT) | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter | Tungatinah | Central | Distribution lines | 110/22 kV | 1 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | Ulverstone | North West | Distribution lines | 110/22 kV | 2 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  |  | Waddamana | Central | Distribution lines | 110/22 kV | 1 | Winter | Proposed retirement/ replacement of Waddamana supply transformer (2030)
Bridgewater | Maximum demand (peak season) (MW) | 37.3301 | 35.704 | 34.4724 | 34.7488 | 34.5845 | 34.5626 | 34.6136 | 34.7683 | 35.2288 | 36.6834 | 37.8712 | 38.6611 |  |  | Wesley Vale | North West | Distribution lines | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Wesley Vale supply transformers (2033)
Bridgewater | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.72364 | 0.69212 | 0.66824 | 0.6736 | 0.67042 | 0.66999 | 0.67098 | 0.67398 | 0.68291 | 0.7111 | 0.73413 | 0.74944 |  |  | Zs-Bellerive | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | 1) Proposed retirement/ replacement of Lindisfarne-Bellerive 33 kV sub-transmission cable (2032). 2) Proposed retirement/ replacement of Bellerive Substation supply transformers (2301)
Bridgewater | Maximum demand (peak season) (MVA) | 37.3371 | 35.7108 | 34.4789 | 34.7553 | 34.591 | 34.5691 | 34.6201 | 34.7748 | 35.2354 | 36.6902 | 37.8783 | 38.6684 |  |  | Zs-Cambridge | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter
Bridgewater | Maximum demand (peak season) Power factor (coincident) | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 | 0.99981 |  |  | Zs-Claremont | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Claremont 33 kV sub-transmission cable (2030)
Bridgewater | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599 |  |  | Zs-Derwent Park | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Derwent Park Substation supply transformers (2030)
Bridgewater | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.00066003 | 0.0054487 | 0.0056029 | 0.0055857 | 0.0054916 | 0.0054248 | 0.0054285 | 0.005418 | 0.0055413 | 0.0058752 | 0.0061713 | 0.0063308 |  |  | Zs-East Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Proposed retirement/ replacement of East Hobart 33 kV sub-transmission cable (2027)
Bridgewater | Maximum demand (non-peak season) (MVA) | 0.039206 | 0.32365 | 0.33281 | 0.33178 | 0.3262 | 0.32223 | 0.32245 | 0.32182 | 0.32915 | 0.34898 | 0.36657 | 0.37605 |  |  | Zs-Geilston Bay | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Geilston Bay Substation supply transformers (2033)
Bridgewater | Hours exceeding 95% of maximum demand | 13.5 | [13 empty] | Zs-Howrah | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter
Bridgewater | Hours exceeding Firm capacity (continuous rating) | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 |  |  | Zs-New Town | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Newtown 33 kV sub-transmission cable (2031)
Bridgewater | Hours exceeding Firm capacity (short-term rating) | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 |  |  | Zs-Rosny Park | Greater Hobart | Distribution lines | 33/11 kV | 1 | Winter
Bridgewater | Regional Diversity Factor (Summer) | 1 | [13 empty] | Zs-Sandy Bay | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Proposed retirement/ replacement of Sandy Bay 33 kV sub-transmission cable (2032)
Bridgewater | Regional Diversity Factor (Winter) | 0.95489 | [13 empty] | Zs-Summerleas | Kingston-South | Distribution lines | 33/11 kV | 1 | Winter
Bridgewater | Load transfer capacity (MVA)1 | [14 empty] | Zs-Trial Harbour | West Coast | Distribution lines | 44/22 kV | 2 | Winter
Bridgewater | Load transfer capacity (MVA)2 | [14 empty] | Zs-West Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter
Bridgewater | Load transfer capacity (MVA)3
Bridgewater | Load transfer capacity (MVA)4
Bridgewater | Load transfer capacity (MVA)5
Bridgewater | Embedded generation capacity (MVA) Units less than 100 kVA | 21.781
Bridgewater | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Burnie | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Burnie | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Burnie | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Burnie | Maximum demand (peak season) (MW) | 63.5022 | 60.651 | 59.6977 | 60.1763 | 59.1955 | 59.1579 | 59.2452 | 59.51 | 60.2982 | 62.7879 | 64.8209 | 66.1731
Burnie | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.6574 | 3.4932 | 3.4383 | 3.4659 | 3.4094 | 3.4072 | 3.4122 | 3.4275 | 3.4729 | 3.6163 | 3.7334 | 3.8113
Burnie | Maximum demand (peak season) (MVA) | 63.6075 | 60.7516 | 59.7966 | 60.276 | 59.2936 | 59.256 | 59.3434 | 59.6086 | 60.3981 | 62.8919 | 64.9284 | 66.2827
Burnie | Maximum demand (peak season) Power factor (coincident) | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835
Burnie | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Burnie | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0042943 | 0.03545 | 0.036454 | 0.036342 | 0.03573 | 0.035295 | 0.035319 | 0.035251 | 0.036053 | 0.038226 | 0.040152 | 0.04119
Burnie | Maximum demand (non-peak season) (MVA) | 0.039435 | 0.32554 | 0.33475 | 0.33372 | 0.3281 | 0.32411 | 0.32433 | 0.3237 | 0.33107 | 0.35102 | 0.36871 | 0.37824
Burnie | Hours exceeding 95% of maximum demand | 7
Burnie | Hours exceeding Firm capacity (continuous rating) | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236 | 1236
Burnie | Hours exceeding Firm capacity (short-term rating) | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
Burnie | Regional Diversity Factor (Summer) | 0.90257
Burnie | Regional Diversity Factor (Winter) | 0.98096
Burnie | Load transfer capacity (MVA)1 | 8.8 | [11 empty] | Port Latta
Burnie | Load transfer capacity (MVA)2 | 8.8 | [11 empty] | Ulverstone
Burnie | Load transfer capacity (MVA)3
Burnie | Load transfer capacity (MVA)4
Burnie | Load transfer capacity (MVA)5
Burnie | Embedded generation capacity (MVA) Units less than 100 kVA | 32.961
Burnie | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.003
Creek Road | Substation capacity (winter and summer) (MVA) Total | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | Winter
Creek Road | Substation capacity (winter and summer) (MVA) Firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Creek Road | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Creek Road | Maximum demand (peak season) (MW) | 100.1103 | 88.7406 | 85.6795 | 86.3664 | 84.9588 | 84.9048 | 85.03 | 85.4101 | 86.5414 | 90.1146 | 93.0325 | 94.9731
Creek Road | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 13.6055 | 12.0603 | 11.6442 | 11.7376 | 11.5463 | 11.539 | 11.556 | 11.6076 | 11.7614 | 12.247 | 12.6436 | 12.9073
Creek Road | Maximum demand (peak season) (MVA) | 101.0306 | 89.5564 | 86.4672 | 87.1604 | 85.7398 | 85.6853 | 85.8117 | 86.1952 | 87.3369 | 90.943 | 93.8877 | 95.8462
Creek Road | Maximum demand (peak season) Power factor (coincident) | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089 | 0.99089
Creek Road | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Creek Road | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0034063 | 0.02812 | 0.028916 | 0.028827 | 0.028341 | 0.027997 | 0.028015 | 0.027961 | 0.028598 | 0.030321 | 0.031849 | 0.032672
Creek Road | Maximum demand (non-peak season) (MVA) | 0.039348 | 0.32482 | 0.33401 | 0.33299 | 0.32738 | 0.3234 | 0.32362 | 0.32299 | 0.33035 | 0.35025 | 0.3679 | 0.37741
Creek Road | Hours exceeding 95% of maximum demand | 26
Creek Road | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Creek Road | Hours exceeding Firm capacity (short-term rating) | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921
Creek Road | Regional Diversity Factor (Summer) | 0.98172
Creek Road | Regional Diversity Factor (Winter) | 1
Creek Road | Load transfer capacity (MVA)1
Creek Road | Load transfer capacity (MVA)2
Creek Road | Load transfer capacity (MVA)3
Creek Road | Load transfer capacity (MVA)4
Creek Road | Load transfer capacity (MVA)5
Creek Road | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Creek Road | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Chapel Street | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Chapel Street | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Chapel Street | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Chapel Street | Maximum demand (peak season) (MW) | 43.726 | 38.5718 | 37.2413 | 37.5399 | 36.928 | 36.9046 | 36.959 | 37.1242 | 37.6159 | 39.1691 | 40.4374 | 41.2809
Chapel Street | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.22191 | 0.19576 | 0.189 | 0.19052 | 0.18741 | 0.18729 | 0.18757 | 0.18841 | 0.1909 | 0.19879 | 0.20522 | 0.2095
Chapel Street | Maximum demand (peak season) (MVA) | 43.7265 | 38.5723 | 37.2418 | 37.5404 | 36.9285 | 36.9051 | 36.9595 | 37.1247 | 37.6164 | 39.1696 | 40.4379 | 41.2814
Chapel Street | Maximum demand (peak season) Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Chapel Street | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Chapel Street | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 3.0996e-05 | 0.00025587 | 0.00026312 | 0.00026231 | 0.00025789 | 0.00025475 | 0.00025492 | 0.00025443 | 0.00026023 | 0.0002759 | 0.00028981 | 0.0002973
Chapel Street | Maximum demand (non-peak season) (MVA) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Chapel Street | Hours exceeding 95% of maximum demand | 10
Chapel Street | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | Regional Diversity Factor (Summer) | 1
Chapel Street | Regional Diversity Factor (Winter) | 0.93981
Chapel Street | Load transfer capacity (MVA)1
Chapel Street | Load transfer capacity (MVA)2
Chapel Street | Load transfer capacity (MVA)3
Chapel Street | Load transfer capacity (MVA)4
Chapel Street | Load transfer capacity (MVA)5
Chapel Street | Embedded generation capacity (MVA) Units less than 100 kVA | 20.875
Chapel Street | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Derwent Bridge | Substation capacity (winter and summer) (MVA) Total | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Summer
Derwent Bridge | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | Maximum demand (peak season) (MW) | 0.30421 | 0.2645 | 0.27199 | 0.27115 | 0.26659 | 0.26335 | 0.26352 | 0.26301 | 0.269 | 0.28521 | 0.29958 | 0.30733
Derwent Bridge | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.044653 | 0.038824 | 0.039923 | 0.0398 | 0.03913 | 0.038654 | 0.03868 | 0.038605 | 0.039485 | 0.041863 | 0.043973 | 0.04511
Derwent Bridge | Maximum demand (peak season) (MVA) | 0.30747 | 0.26734 | 0.2749 | 0.27406 | 0.26944 | 0.26617 | 0.26635 | 0.26583 | 0.27188 | 0.28827 | 0.30279 | 0.31062
Derwent Bridge | Maximum demand (peak season) Power factor (coincident) | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894
Derwent Bridge | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Derwent Bridge | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0046301 | 0.038222 | 0.039304 | 0.039183 | 0.038523 | 0.038055 | 0.03808 | 0.038007 | 0.038872 | 0.041214 | 0.043291 | 0.04441
Derwent Bridge | Maximum demand (non-peak season) (MVA) | 0.039472 | 0.32585 | 0.33507 | 0.33404 | 0.32842 | 0.32443 | 0.32464 | 0.32401 | 0.33139 | 0.35136 | 0.36906 | 0.37861
Derwent Bridge | Hours exceeding 95% of maximum demand | 1.5
Derwent Bridge | Hours exceeding Firm capacity (continuous rating) | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763
Derwent Bridge | Hours exceeding Firm capacity (short-term rating) | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763 | 8763
Derwent Bridge | Regional Diversity Factor (Summer) | 0.54945
Derwent Bridge | Regional Diversity Factor (Winter) | 0.90392
Derwent Bridge | Load transfer capacity (MVA)1
Derwent Bridge | Load transfer capacity (MVA)2
Derwent Bridge | Load transfer capacity (MVA)3
Derwent Bridge | Load transfer capacity (MVA)4
Derwent Bridge | Load transfer capacity (MVA)5
Derwent Bridge | Embedded generation capacity (MVA) Units less than 100 kVA | 0.055
Derwent Bridge | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Derby | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Derby | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | Maximum demand (peak season) (MW) | 6.0741 | 2.7947 | 2.6983 | 2.72 | 2.6756 | 2.6739 | 2.6779 | 2.6898 | 2.7255 | 2.838 | 2.9299 | 2.991
Derby | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.7681 | 0.81351 | 0.78545 | 0.79174 | 0.77884 | 0.77835 | 0.77949 | 0.78298 | 0.79335 | 0.8261 | 0.85285 | 0.87064
Derby | Maximum demand (peak season) (MVA) | 6.3262 | 2.9107 | 2.8103 | 2.8328 | 2.7867 | 2.7849 | 2.789 | 2.8015 | 2.8386 | 2.9558 | 3.0515 | 3.1151
Derby | Maximum demand (peak season) Power factor (coincident) | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015 | 0.96015
Derby | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Derby | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0070388 | 0.058106 | 0.059751 | 0.059567 | 0.058564 | 0.057852 | 0.057891 | 0.057779 | 0.059095 | 0.062655 | 0.065812 | 0.067514
Derby | Maximum demand (non-peak season) (MVA) | 0.039827 | 0.32878 | 0.33808 | 0.33704 | 0.33137 | 0.32734 | 0.32756 | 0.32692 | 0.33437 | 0.35451 | 0.37238 | 0.38201
Derby | Hours exceeding 95% of maximum demand | 4
Derby | Hours exceeding Firm capacity (continuous rating) | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5
Derby | Hours exceeding Firm capacity (short-term rating) | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5 | 8726.5
Derby | Regional Diversity Factor (Summer) | 0.55412
Derby | Regional Diversity Factor (Winter) | 0.65718
Derby | Load transfer capacity (MVA)1 | 5.3 | [11 empty] | Scottsdale
Derby | Load transfer capacity (MVA)2
Derby | Load transfer capacity (MVA)3
Derby | Load transfer capacity (MVA)4
Derby | Load transfer capacity (MVA)5
Derby | Embedded generation capacity (MVA) Units less than 100 kVA | 2.841
Derby | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Devonport | Substation capacity (winter and summer) (MVA) Total | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | Winter
Devonport | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Devonport | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Devonport | Maximum demand (peak season) (MW) | 54.919 | 52.7679 | 51.3937 | 52.7595 | 51.8996 | 51.8667 | 51.9432 | 52.1753 | 52.8664 | 55.0492 | 56.8317 | 58.0172
Devonport | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 4.2853 | 4.1174 | 4.0102 | 4.1168 | 4.0497 | 4.0471 | 4.0531 | 4.0712 | 4.1251 | 4.2954 | 4.4345 | 4.527
Devonport | Maximum demand (peak season) (MVA) | 55.0859 | 52.9283 | 51.55 | 52.9199 | 52.0574 | 52.0243 | 52.1011 | 52.3339 | 53.0271 | 55.2165 | 57.0045 | 58.1936
Devonport | Maximum demand (peak season) Power factor (coincident) | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697 | 0.99697
Devonport | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Devonport | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0048777 | 0.040266 | 0.041406 | 0.041279 | 0.040584 | 0.04009 | 0.040117 | 0.040039 | 0.040951 | 0.043419 | 0.045606 | 0.046786
Devonport | Maximum demand (non-peak season) (MVA) | 0.039502 | 0.3261 | 0.33533 | 0.3343 | 0.32867 | 0.32467 | 0.32489 | 0.32426 | 0.33164 | 0.35162 | 0.36934 | 0.37889
Devonport | Hours exceeding 95% of maximum demand | 4
Devonport | Hours exceeding Firm capacity (continuous rating) | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323
Devonport | Hours exceeding Firm capacity (short-term rating) | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Devonport | Regional Diversity Factor (Summer) | 0.856
Devonport | Regional Diversity Factor (Winter) | 0.93495
Devonport | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Railton
Devonport | Load transfer capacity (MVA)2 | 6.3 | [11 empty] | Ulverstone
Devonport | Load transfer capacity (MVA)3
Devonport | Load transfer capacity (MVA)4
Devonport | Load transfer capacity (MVA)5
Devonport | Embedded generation capacity (MVA) Units less than 100 kVA | 24.972
Devonport | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.013
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Total | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | Winter
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Emu Bay (RT) | Maximum demand (peak season) (MW) | 9.5638 | 9.0796 | 8.7664 | 8.8366 | 8.6926 | 8.6871 | 8.6999 | 8.7388 | 8.8546 | 9.2201 | 9.5187 | 9.7173
Emu Bay (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.2058 | 2.0941 | 2.0219 | 2.0381 | 2.0049 | 2.0036 | 2.0066 | 2.0155 | 2.0422 | 2.1265 | 2.1954 | 2.2412
Emu Bay (RT) | Maximum demand (peak season) (MVA) | 9.8148 | 9.3179 | 8.9965 | 9.0686 | 8.9208 | 8.9152 | 8.9283 | 8.9682 | 9.087 | 9.4622 | 9.7686 | 9.9724
Emu Bay (RT) | Maximum demand (peak season) Power factor (coincident) | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442 | 0.97442
Emu Bay (RT) | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Emu Bay (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.010243 | 0.084558 | 0.086951 | 0.086684 | 0.085224 | 0.084188 | 0.084244 | 0.084081 | 0.085996 | 0.091177 | 0.095772 | 0.098248
Emu Bay (RT) | Maximum demand (non-peak season) (MVA) | 0.040516 | 0.33447 | 0.34393 | 0.34288 | 0.3371 | 0.333 | 0.33323 | 0.33258 | 0.34016 | 0.36065 | 0.37882 | 0.38862
Emu Bay (RT) | Hours exceeding 95% of maximum demand | 11.5
Emu Bay (RT) | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay (RT) | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay (RT) | Regional Diversity Factor (Summer) | 0.49385
Emu Bay (RT) | Regional Diversity Factor (Winter) | 0.81405
Emu Bay (RT) | Load transfer capacity (MVA)1
Emu Bay (RT) | Load transfer capacity (MVA)2
Emu Bay (RT) | Load transfer capacity (MVA)3
Emu Bay (RT) | Load transfer capacity (MVA)4
Emu Bay (RT) | Load transfer capacity (MVA)5
Emu Bay (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Emu Bay (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Electrona | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Electrona | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Electrona | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Electrona | Maximum demand (peak season) (MW) | 17.2978 | 17.4324 | 16.831 | 16.966 | 16.6894 | 16.6788 | 16.7035 | 16.7781 | 17.0003 | 17.7023 | 18.2755 | 18.6567
Electrona | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.71639 | 0.72196 | 0.69706 | 0.70265 | 0.6912 | 0.69076 | 0.69178 | 0.69487 | 0.70407 | 0.73314 | 0.75688 | 0.77267
Electrona | Maximum demand (peak season) (MVA) | 17.3126 | 17.4473 | 16.8455 | 16.9805 | 16.7038 | 16.6931 | 16.7178 | 16.7925 | 17.0149 | 17.7174 | 18.2911 | 18.6727
Electrona | Maximum demand (peak season) Power factor (coincident) | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914
Electrona | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Electrona | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0030451 | 0.025138 | 0.02585 | 0.02577 | 0.025336 | 0.025028 | 0.025045 | 0.024996 | 0.025566 | 0.027106 | 0.028472 | 0.029208
Electrona | Maximum demand (non-peak season) (MVA) | 0.039318 | 0.32457 | 0.33376 | 0.33274 | 0.32713 | 0.32316 | 0.32337 | 0.32275 | 0.3301 | 0.34999 | 0.36762 | 0.37712
Electrona | Hours exceeding 95% of maximum demand | 14
Electrona | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrona | Regional Diversity Factor (Summer) | 1
Electrona | Regional Diversity Factor (Winter) | 0.93363
Electrona | Load transfer capacity (MVA)1 | 8 | [11 empty] | Kingston
Electrona | Load transfer capacity (MVA)2 | 3 | [11 empty] | Knights Road
Electrona | Load transfer capacity (MVA)3
Electrona | Load transfer capacity (MVA)4
Electrona | Load transfer capacity (MVA)5
Electrona | Embedded generation capacity (MVA) Units less than 100 kVA | 20.258
Electrona | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
George Town | Substation capacity (winter and summer) (MVA) Total | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | Winter
George Town | Substation capacity (winter and summer) (MVA) Firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
George Town | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
George Town | Maximum demand (peak season) (MW) | 19.4828 | 20.5861 | 20.2044 | 22.0696 | 21.7099 | 21.6961 | 21.7281 | 21.8252 | 22.1143 | 23.0274 | 23.773 | 24.2689
George Town | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.89378 | 0.94439 | 0.92688 | 1.0124 | 0.99595 | 0.99531 | 0.99678 | 1.0012 | 1.0145 | 1.0564 | 1.0906 | 1.1133
George Town | Maximum demand (peak season) (MVA) | 19.5033 | 20.6077 | 20.2257 | 22.0928 | 21.7327 | 21.7189 | 21.751 | 21.8482 | 22.1376 | 23.0516 | 23.798 | 24.2944
George Town | Maximum demand (peak season) Power factor (coincident) | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895 | 0.99895
George Town | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
George Town | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0026899 | 0.022205 | 0.022834 | 0.022764 | 0.02238 | 0.022108 | 0.022123 | 0.02208 | 0.022583 | 0.023944 | 0.02515 | 0.025801
George Town | Maximum demand (non-peak season) (MVA) | 0.039292 | 0.32436 | 0.33354 | 0.33252 | 0.32692 | 0.32294 | 0.32316 | 0.32253 | 0.32988 | 0.34975 | 0.36738 | 0.37688
George Town | Hours exceeding 95% of maximum demand | 3
George Town | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | Regional Diversity Factor (Summer) | 0.81511
George Town | Regional Diversity Factor (Winter) | 0.97224
George Town | Load transfer capacity (MVA)1 | 2.1 | [11 empty] | Scottsdale
George Town | Load transfer capacity (MVA)2 | 2.1 | [11 empty] | Trevallyn
George Town | Load transfer capacity (MVA)3 | 2.1 | [11 empty] | Mowbray
George Town | Load transfer capacity (MVA)4
George Town | Load transfer capacity (MVA)5
George Town | Embedded generation capacity (MVA) Units less than 100 kVA | 18.704
George Town | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Hadspen | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Hadspen | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hadspen | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hadspen | Maximum demand (peak season) (MW) | 57.2165 | 58.1832 | 56.9622 | 57.4188 | 57.8233 | 57.7866 | 57.8719 | 58.1305 | 58.9005 | 61.3324 | 63.3184 | 64.6392
Hadspen | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.5394 | 2.5823 | 2.5282 | 2.5484 | 2.5664 | 2.5647 | 2.5685 | 2.58 | 2.6142 | 2.7221 | 2.8103 | 2.8689
Hadspen | Maximum demand (peak season) (MVA) | 57.2728 | 58.2405 | 57.0183 | 57.4754 | 57.8803 | 57.8435 | 57.9288 | 58.1877 | 58.9585 | 61.3928 | 63.3807 | 64.7028
Hadspen | Maximum demand (peak season) Power factor (coincident) | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902 | 0.99902
Hadspen | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Hadspen | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.00066466 | 0.0054868 | 0.0056422 | 0.0056248 | 0.0055301 | 0.0054629 | 0.0054665 | 0.0054559 | 0.0055802 | 0.0059164 | 0.0062145 | 0.0063752
Hadspen | Maximum demand (non-peak season) (MVA) | 0.039206 | 0.32365 | 0.33281 | 0.33179 | 0.3262 | 0.32223 | 0.32245 | 0.32182 | 0.32915 | 0.34898 | 0.36657 | 0.37605
Hadspen | Hours exceeding 95% of maximum demand | 4
Hadspen | Hours exceeding Firm capacity (continuous rating) | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451 | 1451
Hadspen | Hours exceeding Firm capacity (short-term rating) | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
Hadspen | Regional Diversity Factor (Summer) | 0.97117
Hadspen | Regional Diversity Factor (Winter) | 1
Hadspen | Load transfer capacity (MVA)1 | 26.7 | [11 empty] | Trevallyn
Hadspen | Load transfer capacity (MVA)2 | 13.4 | [11 empty] | Norwood
Hadspen | Load transfer capacity (MVA)3 | 5.3 | [11 empty] | Palmerston
Hadspen | Load transfer capacity (MVA)4
Hadspen | Load transfer capacity (MVA)5
Hadspen | Embedded generation capacity (MVA) Units less than 100 kVA | 32.642
Hadspen | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.043
Huon River | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
Huon River | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | Maximum demand (peak season) (MW) | 0.57438 | 0.6402 | 0.65832 | 0.6563 | 0.64524 | 0.6374 | 0.63783 | 0.63659 | 0.65109 | 0.69032 | 0.7251 | 0.74385
Huon River | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.77374 | 0.86241 | 0.88683 | 0.8841 | 0.86921 | 0.85864 | 0.85922 | 0.85756 | 0.87709 | 0.92993 | 0.97679 | 1.002
Huon River | Maximum demand (peak season) (MVA) | 0.96363 | 1.0741 | 1.1045 | 1.1011 | 1.0825 | 1.0694 | 1.0701 | 1.068 | 1.0923 | 1.1582 | 1.2165 | 1.248
Huon River | Maximum demand (peak season) Power factor (coincident) | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605 | 0.59605
Huon River | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Huon River | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.057749 | 0.47673 | 0.49022 | 0.48871 | 0.48048 | 0.47464 | 0.47496 | 0.47404 | 0.48484 | 0.51405 | 0.53995 | 0.55391
Huon River | Maximum demand (non-peak season) (MVA) | 0.069797 | 0.57618 | 0.59249 | 0.59067 | 0.58072 | 0.57366 | 0.57405 | 0.57294 | 0.58598 | 0.62129 | 0.6526 | 0.66947
Huon River | Hours exceeding 95% of maximum demand | 4
Huon River | Hours exceeding Firm capacity (continuous rating) | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5
Huon River | Hours exceeding Firm capacity (short-term rating) | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5 | 8747.5
Huon River | Regional Diversity Factor (Summer) | 0.90316
Huon River | Regional Diversity Factor (Winter) | 0.83073
Huon River | Load transfer capacity (MVA)1
Huon River | Load transfer capacity (MVA)2
Huon River | Load transfer capacity (MVA)3
Huon River | Load transfer capacity (MVA)4
Huon River | Load transfer capacity (MVA)5
Huon River | Embedded generation capacity (MVA) Units less than 100 kVA | 0.012
Huon River | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Kermandie | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Kermandie | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Kermandie | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Kermandie | Maximum demand (peak season) (MW) | 9.0397 | 8.6602 | 8.3614 | 8.4285 | 8.2911 | 8.9792 | 8.9924 | 9.0326 | 9.1522 | 9.5301 | 9.8387 | 10.0439
Kermandie | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.4673 | 1.4057 | 1.3572 | 1.3681 | 1.3458 | 1.4574 | 1.4596 | 1.4661 | 1.4855 | 1.5469 | 1.597 | 1.6303
Kermandie | Maximum demand (peak season) (MVA) | 9.158 | 8.7735 | 8.4709 | 8.5388 | 8.3996 | 9.0967 | 9.1101 | 9.1508 | 9.272 | 9.6548 | 9.9675 | 10.1754
Kermandie | Maximum demand (peak season) Power factor (coincident) | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708 | 0.98708
Kermandie | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Kermandie | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0096151 | 0.079374 | 0.081621 | 0.08137 | 0.079999 | 0.079027 | 0.079079 | 0.078926 | 0.080724 | 0.085588 | 0.0899 | 0.092224
Kermandie | Maximum demand (non-peak season) (MVA) | 0.040362 | 0.33319 | 0.34262 | 0.34157 | 0.33582 | 0.33174 | 0.33196 | 0.33132 | 0.33886 | 0.35928 | 0.37738 | 0.38714
Kermandie | Hours exceeding 95% of maximum demand | 11
Kermandie | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kermandie | Regional Diversity Factor (Summer) | 0.96803
Kermandie | Regional Diversity Factor (Winter) | 0.92768
Kermandie | Load transfer capacity (MVA)1 | 4.4 | [11 empty] | Knights Road
Kermandie | Load transfer capacity (MVA)2
Kermandie | Load transfer capacity (MVA)3
Kermandie | Load transfer capacity (MVA)4
Kermandie | Load transfer capacity (MVA)5
Kermandie | Embedded generation capacity (MVA) Units less than 100 kVA | 8.18
Kermandie | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Kingston 11kV | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Kingston 11kV | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Kingston 11kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Kingston 11kV | Maximum demand (peak season) (MW) | 29.9108 | 26.6514 | 25.732 | 26.5417 | 26.1091 | 26.0925 | 26.131 | 26.2478 | 26.5954 | 27.6935 | 28.5902 | 29.1866
Kingston 11kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.022156 | 0.019742 | 0.019061 | 0.019661 | 0.01934 | 0.019328 | 0.019356 | 0.019443 | 0.0197 | 0.020514 | 0.021178 | 0.02162
Kingston 11kV | Maximum demand (peak season) (MVA) | 29.9108 | 26.6514 | 25.732 | 26.5417 | 26.1091 | 26.0925 | 26.131 | 26.2478 | 26.5954 | 27.6935 | 28.5903 | 29.1866
Kingston 11kV | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
Kingston 11kV | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Kingston 11kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0018793 | 0.015514 | 0.015953 | 0.015904 | 0.015636 | 0.015446 | 0.015456 | 0.015426 | 0.015778 | 0.016728 | 0.017571 | 0.018026
Kingston 11kV | Maximum demand (non-peak season) (MVA) | 0.039245 | 0.32397 | 0.33314 | 0.33212 | 0.32652 | 0.32256 | 0.32277 | 0.32215 | 0.32948 | 0.34933 | 0.36694 | 0.37642
Kingston 11kV | Hours exceeding 95% of maximum demand | 14.5
Kingston 11kV | Hours exceeding Firm capacity (continuous rating) | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Kingston 11kV | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV | Regional Diversity Factor (Summer) | 1
Kingston 11kV | Regional Diversity Factor (Winter) | 0.88817
Kingston 11kV | Load transfer capacity (MVA)1
Kingston 11kV | Load transfer capacity (MVA)2
Kingston 11kV | Load transfer capacity (MVA)3
Kingston 11kV | Load transfer capacity (MVA)4
Kingston 11kV | Load transfer capacity (MVA)5
Kingston 11kV | Embedded generation capacity (MVA) Units less than 100 kVA | 22.799
Kingston 11kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.005
Kingston 33kV | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Kingston 33kV | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kingston 33kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Kingston 33kV | Maximum demand (peak season) (MW) | 12.0349 | 10.7332 | 10.363 | 10.446 | 10.2758 | 10.2693 | 10.2844 | 10.3304 | 10.4672 | 10.8994 | 11.2523 | 11.487
Kingston 33kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.067 | 0.95161 | 0.91879 | 0.92615 | 0.91106 | 0.91048 | 0.91182 | 0.9159 | 0.92803 | 0.96635 | 0.99764 | 1.0184
Kingston 33kV | Maximum demand (peak season) (MVA) | 12.0821 | 10.7753 | 10.4036 | 10.487 | 10.3161 | 10.3095 | 10.3247 | 10.3709 | 10.5083 | 10.9421 | 11.2964 | 11.5321
Kingston 33kV | Maximum demand (peak season) Power factor (coincident) | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609 | 0.99609
Kingston 33kV | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Kingston 33kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 7.895e-05 | 0.00065174 | 0.00067019 | 0.00066813 | 0.00065688 | 0.00064889 | 0.00064933 | 0.00064807 | 0.00066283 | 0.00070277 | 0.00073818 | 0.00075726
Kingston 33kV | Maximum demand (non-peak season) (MVA) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Kingston 33kV | Hours exceeding 95% of maximum demand | 17.5
Kingston 33kV | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 33kV | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 33kV | Regional Diversity Factor (Summer) | 1
Kingston 33kV | Regional Diversity Factor (Winter) | 1
Kingston 33kV | Load transfer capacity (MVA)1
Kingston 33kV | Load transfer capacity (MVA)2
Kingston 33kV | Load transfer capacity (MVA)3
Kingston 33kV | Load transfer capacity (MVA)4
Kingston 33kV | Load transfer capacity (MVA)5
Kingston 33kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Kingston 33kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Knights Road | Substation capacity (winter and summer) (MVA) Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Knights Road | Substation capacity (winter and summer) (MVA) Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Knights Road | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Knights Road | Maximum demand (peak season) (MW) | 20.908 | 20.1729 | 19.477 | 19.6332 | 19.3132 | 21.9799 | 22.0123 | 22.1107 | 22.4036 | 23.3286 | 24.084 | 24.5863
Knights Road | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.0954 | 2.9866 | 2.8836 | 2.9067 | 2.8593 | 3.2541 | 3.2589 | 3.2735 | 3.3168 | 3.4538 | 3.5656 | 3.64
Knights Road | Maximum demand (peak season) (MVA) | 21.1359 | 20.3928 | 19.6893 | 19.8472 | 19.5237 | 22.2195 | 22.2522 | 22.3517 | 22.6478 | 23.5829 | 24.3465 | 24.8543
Knights Road | Maximum demand (peak season) Power factor (coincident) | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922 | 0.98922
Knights Road | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Knights Road | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.008411 | 0.069433 | 0.071399 | 0.071179 | 0.06998 | 0.06913 | 0.069176 | 0.069042 | 0.070615 | 0.074869 | 0.078642 | 0.080675
Knights Road | Maximum demand (non-peak season) (MVA) | 0.040092 | 0.33097 | 0.34033 | 0.33929 | 0.33357 | 0.32952 | 0.32974 | 0.3291 | 0.3366 | 0.35688 | 0.37486 | 0.38455
Knights Road | Hours exceeding 95% of maximum demand | 9
Knights Road | Hours exceeding Firm capacity (continuous rating) | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5 | 1492.5
Knights Road | Hours exceeding Firm capacity (short-term rating) | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5 | 261.5
Knights Road | Regional Diversity Factor (Summer) | 0.98793
Knights Road | Regional Diversity Factor (Winter) | 0.93681
Knights Road | Load transfer capacity (MVA)1 | 1.7 | [11 empty] | Electrona
Knights Road | Load transfer capacity (MVA)2 | 3.4 | [11 empty] | Kermandie
Knights Road | Load transfer capacity (MVA)3 | 1.7 | [11 empty] | Kingston
Knights Road | Load transfer capacity (MVA)4
Knights Road | Load transfer capacity (MVA)5
Knights Road | Embedded generation capacity (MVA) Units less than 100 kVA | 16.562
Knights Road | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Lindisfarne | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Lindisfarne | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Lindisfarne | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Lindisfarne | Maximum demand (peak season) (MW) | 38.0913 | 36.8108 | 35.541 | 37.461 | 36.8504 | 36.827 | 36.8813 | 37.0462 | 37.5369 | 39.0867 | 40.3523 | 41.1941
Lindisfarne | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.49 | 2.4063 | 2.3233 | 2.4488 | 2.4089 | 2.4073 | 2.4109 | 2.4216 | 2.4537 | 2.555 | 2.6378 | 2.6928
Lindisfarne | Maximum demand (peak season) (MVA) | 38.1726 | 36.8893 | 35.6168 | 37.5409 | 36.929 | 36.9056 | 36.96 | 37.1252 | 37.617 | 39.1701 | 40.4385 | 41.282
Lindisfarne | Maximum demand (peak season) Power factor (coincident) | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787 | 0.99787
Lindisfarne | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Lindisfarne | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.00010238 | 0.00084512 | 0.00086905 | 0.00086638 | 0.00085178 | 0.00084143 | 0.00084199 | 0.00084036 | 0.0008595 | 0.00091129 | 0.00095721 | 0.00098195
Lindisfarne | Maximum demand (non-peak season) (MVA) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34894 | 0.36652 | 0.37599
Lindisfarne | Hours exceeding 95% of maximum demand | 9.5
Lindisfarne | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne | Regional Diversity Factor (Summer) | 1
Lindisfarne | Regional Diversity Factor (Winter) | 1
Lindisfarne | Load transfer capacity (MVA)1
Lindisfarne | Load transfer capacity (MVA)2
Lindisfarne | Load transfer capacity (MVA)3
Lindisfarne | Load transfer capacity (MVA)4
Lindisfarne | Load transfer capacity (MVA)5
Lindisfarne | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Lindisfarne | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Meadowbank | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
Meadowbank | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | Maximum demand (peak season) (MW) | 7.7741 | 7.8437 | 8.0658 | 8.041 | 7.9055 | 7.8095 | 7.8147 | 7.7996 | 7.9772 | 8.4578 | 8.884 | 9.1137
Meadowbank | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.768 | 2.7928 | 2.8718 | 2.863 | 2.8148 | 2.7806 | 2.7824 | 2.7771 | 2.8403 | 3.0114 | 3.1632 | 3.2449
Meadowbank | Maximum demand (peak season) (MVA) | 8.2522 | 8.3261 | 8.5618 | 8.5355 | 8.3917 | 8.2897 | 8.2952 | 8.2792 | 8.4677 | 8.9779 | 9.4303 | 9.6741
Meadowbank | Maximum demand (peak season) Power factor (coincident) | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207 | 0.94207
Meadowbank | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Meadowbank | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.00091367 | 0.0075424 | 0.0077559 | 0.0077321 | 0.0076018 | 0.0075094 | 0.0075145 | 0.0074999 | 0.0076707 | 0.0081329 | 0.0085427 | 0.0087636
Meadowbank | Maximum demand (non-peak season) (MVA) | 0.039211 | 0.32369 | 0.33285 | 0.33183 | 0.32624 | 0.32227 | 0.32249 | 0.32186 | 0.32919 | 0.34903 | 0.36662 | 0.37609
Meadowbank | Hours exceeding 95% of maximum demand | 5
Meadowbank | Hours exceeding Firm capacity (continuous rating) | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5
Meadowbank | Hours exceeding Firm capacity (short-term rating) | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5 | 8662.5
Meadowbank | Regional Diversity Factor (Summer) | 0.8769
Meadowbank | Regional Diversity Factor (Winter) | 0.55344
Meadowbank | Load transfer capacity (MVA)1 | 3.4 | [11 empty] | New Norfolk
Meadowbank | Load transfer capacity (MVA)2 | 0.5 | [11 empty] | Wayatinah Zone
Meadowbank | Load transfer capacity (MVA)3
Meadowbank | Load transfer capacity (MVA)4
Meadowbank | Load transfer capacity (MVA)5
Meadowbank | Embedded generation capacity (MVA) Units less than 100 kVA | 1.743
Meadowbank | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Mornington | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Mornington | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Mornington | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Mornington | Maximum demand (peak season) (MW) | 44.5185 | 44.523 | 42.9872 | 43.3318 | 42.6256 | 42.5985 | 42.6613 | 42.852 | 43.4196 | 45.2124 | 46.6763 | 47.65
Mornington | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.4084 | 2.4086 | 2.3255 | 2.3442 | 2.306 | 2.3045 | 2.3079 | 2.3182 | 2.3489 | 2.4459 | 2.5251 | 2.5778
Mornington | Maximum demand (peak season) (MVA) | 44.5836 | 44.5881 | 43.05 | 43.3952 | 42.6879 | 42.6608 | 42.7237 | 42.9147 | 43.4831 | 45.2785 | 46.7446 | 47.7197
Mornington | Maximum demand (peak season) Power factor (coincident) | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854 | 0.99854
Mornington | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Mornington | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0010571 | 0.0087266 | 0.0089736 | 0.008946 | 0.0087953 | 0.0086884 | 0.0086942 | 0.0086774 | 0.008875 | 0.0094097 | 0.0098839 | 0.010139
Mornington | Maximum demand (non-peak season) (MVA) | 0.039214 | 0.32372 | 0.33288 | 0.33186 | 0.32627 | 0.3223 | 0.32252 | 0.32189 | 0.32923 | 0.34906 | 0.36665 | 0.37613
Mornington | Hours exceeding 95% of maximum demand | 87.5
Mornington | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington | Regional Diversity Factor (Summer) | 1
Mornington | Regional Diversity Factor (Winter) | 0.94962
Mornington | Load transfer capacity (MVA)1
Mornington | Load transfer capacity (MVA)2
Mornington | Load transfer capacity (MVA)3
Mornington | Load transfer capacity (MVA)4
Mornington | Load transfer capacity (MVA)5
Mornington | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Mornington | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Mowbray | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Mowbray | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Mowbray | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Mowbray | Maximum demand (peak season) (MW) | 36.9918 | 38.8339 | 38.0012 | 38.3059 | 37.6815 | 37.6576 | 37.7131 | 37.8817 | 38.3835 | 39.9683 | 41.2625 | 42.1232
Mowbray | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.9304 | 4.1261 | 4.0377 | 4.07 | 4.0037 | 4.0012 | 4.0071 | 4.025 | 4.0783 | 4.2467 | 4.3842 | 4.4756
Mowbray | Maximum demand (peak season) (MVA) | 37.2 | 39.0525 | 38.2151 | 38.5215 | 37.8936 | 37.8696 | 37.9254 | 38.0949 | 38.5995 | 40.1933 | 41.4947 | 42.3603
Mowbray | Maximum demand (peak season) Power factor (coincident) | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944 | 0.9944
Mowbray | Maximum demand (non-peak season) (MW) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599
Mowbray | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.0035255 | 0.029104 | 0.029927 | 0.029836 | 0.029333 | 0.028976 | 0.028996 | 0.02894 | 0.029599 | 0.031382 | 0.032963 | 0.033816
Mowbray | Maximum demand (non-peak season) (MVA) | 0.039358 | 0.32491 | 0.3341 | 0.33308 | 0.32747 | 0.32349 | 0.3237 | 0.32308 | 0.33043 | 0.35034 | 0.368 | 0.37751
Mowbray | Hours exceeding 95% of maximum demand | 1.5
Mowbray | Hours exceeding Firm capacity (continuous rating) | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
Mowbray | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mowbray | Regional Diversity Factor (Summer) | 0.82864
Mowbray | Regional Diversity Factor (Winter) | 0.99928
Mowbray | Load transfer capacity (MVA)1 | 31.4 | [11 empty] | Trevallyn
Mowbray | Load transfer capacity (MVA)2 | 6.3 | [11 empty] | Norwood
Mowbray | Load transfer capacity (MVA)3
Mowbray | Load transfer capacity (MVA)4
Mowbray | Load transfer capacity (MVA)5
Mowbray | Embedded generation capacity (MVA) Units less than 100 kVA | 12.604
Mowbray | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
North Hobart | Substation capacity (winter and summer) (MVA) Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
North Hobart | Substation capacity (winter and summer) (MVA) Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
North Hobart | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
North Hobart | Maximum demand (peak season) (MW) | 37.008 | 34.9903 | 33.7833 | 34.0542 | 33.4991 | 33.4779 | 33.5273 | 33.6771 | 34.1232 | 35.5321 | 36.6826 | 37.4478
North Hobart | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.5077 | 2.371 | 2.2892 | 2.3075 | 2.2699 | 2.2685 | 2.2718 | 2.282 | 2.3122 | 2.4077 | 2.4856 | 2.5375
North Hobart | Maximum demand (peak season) (MVA) | 37.0928 | 35.0706 | 33.8608 | 34.1323 | 33.576 | 33.5546 | 33.6041 | 33.7543 | 34.2014 | 35.6136 | 36.7667 | 37.5337
North Hobart | Maximum demand (peak season) Power factor (coincident) | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771 | 0.99771
North Hobart | Maximum demand (non-peak season) (MW) | 6.7863 | 6.6366 | 6.4076 | 6.459 | 6.3537 | 6.3497 | 6.3591 | 6.3875 | 6.4721 | 6.7393 | 6.9575 | 7.1027
North Hobart | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.52873 | 0.51706 | 0.49922 | 0.50322 | 0.49502 | 0.49471 | 0.49544 | 0.49765 | 0.50424 | 0.52506 | 0.54206 | 0.55337
North Hobart | Maximum demand (non-peak season) (MVA) | 6.8069 | 6.6567 | 6.4271 | 6.4786 | 6.373 | 6.3689 | 6.3783 | 6.4069 | 6.4917 | 6.7597 | 6.9786 | 7.1242
North Hobart | Hours exceeding 95% of maximum demand | 2.5
North Hobart | Hours exceeding Firm capacity (continuous rating) | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5
North Hobart | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | Regional Diversity Factor (Summer) | 0.94552
North Hobart | Regional Diversity Factor (Winter) | 0.95665
North Hobart | Load transfer capacity (MVA)1
North Hobart | Load transfer capacity (MVA)2
North Hobart | Load transfer capacity (MVA)3
North Hobart | Load transfer capacity (MVA)4
North Hobart | Load transfer capacity (MVA)5
North Hobart | Embedded generation capacity (MVA) Units less than 100 kVA | 14.614
North Hobart | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.06
New Norfolk | Substation capacity (winter and summer) (MVA) Total | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Winter
New Norfolk | Substation capacity (winter and summer) (MVA) Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
New Norfolk | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
New Norfolk | Maximum demand (peak season) (MW) | 19.3862 | 17.2812 | 16.6851 | 16.8188 | 16.5447 | 16.5342 | 16.5586 | 16.6326 | 16.8529 | 17.5488 | 18.117 | 18.4949
New Norfolk | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.078902 | 0.070335 | 0.067909 | 0.068453 | 0.067338 | 0.067295 | 0.067394 | 0.067695 | 0.068592 | 0.071424 | 0.073737 | 0.075275
New Norfolk | Maximum demand (peak season) (MVA) | 19.3863 | 17.2813 | 16.6852 | 16.819 | 16.5449 | 16.5344 | 16.5587 | 16.6328 | 16.8531 | 17.5489 | 18.1171 | 18.4951
New Norfolk | Maximum demand (peak season) Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
New Norfolk | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
New Norfolk | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.90208 | 0.76035 | 0.78187 | 0.77947 | 0.76634 | 0.75703 | 0.75753 | 0.75607 | 0.77328 | 0.81988 | 0.86119 | 0.88345
New Norfolk | Maximum demand (non-peak season) (MVA) | 9.8611 | 8.3118 | 8.5471 | 8.5208 | 8.3773 | 8.2755 | 8.281 | 8.265 | 8.4532 | 8.9625 | 9.4141 | 9.6575
New Norfolk | Hours exceeding 95% of maximum demand | 19
New Norfolk | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk | Regional Diversity Factor (Summer) | 0.99575
New Norfolk | Regional Diversity Factor (Winter) | 0.9027
New Norfolk | Load transfer capacity (MVA)1 | 6.6 | [11 empty] | Meadowbank
New Norfolk | Load transfer capacity (MVA)2
New Norfolk | Load transfer capacity (MVA)3
New Norfolk | Load transfer capacity (MVA)4
New Norfolk | Load transfer capacity (MVA)5
New Norfolk | Embedded generation capacity (MVA) Units less than 100 kVA | 5.83
New Norfolk | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Newton | Substation capacity (winter and summer) (MVA) Total | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 |  | Winter
Newton | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | Maximum demand (peak season) (MW) | 4.1194 | 3.9208 | 3.7856 | 3.8159 | 3.7537 | 3.7513 | 3.7569 | 3.7736 | 3.8236 | 3.9815 | 4.1104 | 4.1962
Newton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.056735 | 0.054 | 0.052137 | 0.052555 | 0.051699 | 0.051666 | 0.051742 | 0.051973 | 0.052662 | 0.054836 | 0.056612 | 0.057793
Newton | Maximum demand (peak season) (MVA) | 4.1198 | 3.9212 | 3.7859 | 3.8163 | 3.7541 | 3.7517 | 3.7572 | 3.774 | 3.824 | 3.9819 | 4.1108 | 4.1966
Newton | Maximum demand (peak season) Power factor (coincident) | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991
Newton | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Newton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.7289 | 0.61438 | 0.63177 | 0.62983 | 0.61922 | 0.61169 | 0.6121 | 0.61092 | 0.62483 | 0.66248 | 0.69586 | 0.71385
Newton | Maximum demand (non-peak season) (MVA) | 9.8468 | 8.2997 | 8.5347 | 8.5084 | 8.3651 | 8.2634 | 8.269 | 8.253 | 8.4409 | 8.9495 | 9.4004 | 9.6435
Newton | Hours exceeding 95% of maximum demand | 1.5
Newton | Hours exceeding Firm capacity (continuous rating) | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5
Newton | Hours exceeding Firm capacity (short-term rating) | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5 | 8779.5
Newton | Regional Diversity Factor (Summer) | 0.85116
Newton | Regional Diversity Factor (Winter) | 0.88727
Newton | Load transfer capacity (MVA)1
Newton | Load transfer capacity (MVA)2
Newton | Load transfer capacity (MVA)3
Newton | Load transfer capacity (MVA)4
Newton | Load transfer capacity (MVA)5
Newton | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Newton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Norwood | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Norwood | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Norwood | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Norwood | Maximum demand (peak season) (MW) | 29.8043 | 29.8795 | 28.8489 | 29.0801 | 28.6062 | 28.588 | 28.6302 | 28.7581 | 29.139 | 30.3422 | 31.3247 | 31.9781
Norwood | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.50407 | 0.50534 | 0.48791 | 0.49182 | 0.4838 | 0.4835 | 0.48421 | 0.48637 | 0.49282 | 0.51316 | 0.52978 | 0.54083
Norwood | Maximum demand (peak season) (MVA) | 29.8086 | 29.8838 | 28.853 | 29.0843 | 28.6103 | 28.5921 | 28.6343 | 28.7622 | 29.1432 | 30.3465 | 31.3291 | 31.9826
Norwood | Maximum demand (peak season) Power factor (coincident) | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986
Norwood | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Norwood | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.070402 | 0.059341 | 0.061021 | 0.060833 | 0.059808 | 0.059081 | 0.059121 | 0.059006 | 0.06035 | 0.063986 | 0.067211 | 0.068948
Norwood | Maximum demand (non-peak season) (MVA) | 9.8201 | 8.2772 | 8.5115 | 8.4853 | 8.3424 | 8.241 | 8.2465 | 8.2305 | 8.418 | 8.9252 | 9.3749 | 9.6173
Norwood | Hours exceeding 95% of maximum demand | 25.5
Norwood | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Norwood | Regional Diversity Factor (Summer) | 0.94293
Norwood | Regional Diversity Factor (Winter) | 0.96266
Norwood | Load transfer capacity (MVA)1 | 16.2 | [11 empty] | Trevallyn
Norwood | Load transfer capacity (MVA)2 | 10.8 | [11 empty] | Mowbray
Norwood | Load transfer capacity (MVA)3 | 27 | [11 empty] | St Leonards
Norwood | Load transfer capacity (MVA)4 | 16.2 | [11 empty] | Hadspen
Norwood | Load transfer capacity (MVA)5
Norwood | Embedded generation capacity (MVA) Units less than 100 kVA | 17.898
Norwood | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.035
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Port Latta (RT) | Maximum demand (peak season) (MW) | 10.8116 | 10.7522 | 11.0566 | 11.0226 | 10.8369 | 10.7052 | 10.7124 | 10.6916 | 10.9351 | 11.594 | 12.1782 | 12.493
Port Latta (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.7834 | 3.7626 | 3.8691 | 3.8572 | 3.7922 | 3.7462 | 3.7487 | 3.7414 | 3.8266 | 4.0572 | 4.2616 | 4.3718
Port Latta (RT) | Maximum demand (peak season) (MVA) | 11.4545 | 11.3915 | 11.714 | 11.678 | 11.4813 | 11.3417 | 11.3493 | 11.3274 | 11.5853 | 12.2834 | 12.9023 | 13.2359
Port Latta (RT) | Maximum demand (peak season) Power factor (coincident) | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388 | 0.94388
Port Latta (RT) | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Port Latta (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.44596 | 0.37589 | 0.38653 | 0.38534 | 0.37885 | 0.37425 | 0.3745 | 0.37377 | 0.38229 | 0.40532 | 0.42574 | 0.43675
Port Latta (RT) | Maximum demand (non-peak season) (MVA) | 9.8299 | 8.2855 | 8.52 | 8.4938 | 8.3508 | 8.2493 | 8.2548 | 8.2388 | 8.4264 | 8.9341 | 9.3843 | 9.6269
Port Latta (RT) | Hours exceeding 95% of maximum demand | 3.5
Port Latta (RT) | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Latta (RT) | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Latta (RT) | Regional Diversity Factor (Summer) | 0.69595
Port Latta (RT) | Regional Diversity Factor (Winter) | 0.96774
Port Latta (RT) | Load transfer capacity (MVA)1 | 3.9 | [11 empty] | Burnie
Port Latta (RT) | Load transfer capacity (MVA)2 | 3.9 | [11 empty] | Smithton
Port Latta (RT) | Load transfer capacity (MVA)3
Port Latta (RT) | Load transfer capacity (MVA)4
Port Latta (RT) | Load transfer capacity (MVA)5
Port Latta (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Port Latta (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Palmerston | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
Palmerston | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Palmerston | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Palmerston | Maximum demand (peak season) (MW) | 11.885 | 13.52 | 15.7023 | 15.654 | 17.9302 | 17.7122 | 17.7241 | 17.6898 | 18.0927 | 19.1827 | 20.1493 | 20.6703
Palmerston | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.6575 | 4.1606 | 4.8322 | 4.8173 | 5.5178 | 5.4507 | 5.4544 | 5.4438 | 5.5678 | 5.9032 | 6.2007 | 6.361
Palmerston | Maximum demand (peak season) (MVA) | 12.435 | 14.1457 | 16.429 | 16.3785 | 18.76 | 18.532 | 18.5444 | 18.5085 | 18.93 | 20.0705 | 21.0819 | 21.6269
Palmerston | Maximum demand (peak season) Power factor (coincident) | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577 | 0.95577
Palmerston | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Palmerston | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.94265 | 0.79455 | 0.81704 | 0.81453 | 0.80081 | 0.79107 | 0.7916 | 0.79007 | 0.80806 | 0.85675 | 0.89992 | 0.92319
Palmerston | Maximum demand (non-peak season) (MVA) | 9.8649 | 8.315 | 8.5504 | 8.5241 | 8.3805 | 8.2786 | 8.2842 | 8.2682 | 8.4565 | 8.966 | 9.4177 | 9.6612
Palmerston | Hours exceeding 95% of maximum demand | 16
Palmerston | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palmerston | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palmerston | Regional Diversity Factor (Summer) | 0.86399
Palmerston | Regional Diversity Factor (Winter) | 0.67138
Palmerston | Load transfer capacity (MVA)1 | 2 | [11 empty] | Norwood
Palmerston | Load transfer capacity (MVA)2 | 5 | [11 empty] | Hadspen
Palmerston | Load transfer capacity (MVA)3
Palmerston | Load transfer capacity (MVA)4
Palmerston | Load transfer capacity (MVA)5
Palmerston | Embedded generation capacity (MVA) Units less than 100 kVA | 2.801
Palmerston | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Queenstown | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Queenstown | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Queenstown | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Queenstown | Maximum demand (peak season) (MW) | 6.3509 | 5.8481 | 5.6464 | 5.6917 | 5.5989 | 5.5953 | 5.6036 | 5.6286 | 5.7032 | 5.9387 | 6.131 | 6.2588
Queenstown | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.07217 | 0.066456 | 0.064163 | 0.064678 | 0.063624 | 0.063583 | 0.063677 | 0.063962 | 0.064809 | 0.067485 | 0.06967 | 0.071123
Queenstown | Maximum demand (peak season) (MVA) | 6.3513 | 5.8485 | 5.6468 | 5.692 | 5.5992 | 5.5957 | 5.6039 | 5.629 | 5.7036 | 5.939 | 6.1314 | 6.2593
Queenstown | Maximum demand (peak season) Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Queenstown | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Queenstown | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.15932 | 0.13429 | 0.13809 | 0.13766 | 0.13535 | 0.1337 | 0.13379 | 0.13353 | 0.13657 | 0.1448 | 0.1521 | 0.15603
Queenstown | Maximum demand (non-peak season) (MVA) | 9.8211 | 8.278 | 8.5124 | 8.4862 | 8.3433 | 8.2418 | 8.2474 | 8.2314 | 8.4189 | 8.9261 | 9.3759 | 9.6183
Queenstown | Hours exceeding 95% of maximum demand | 22.5
Queenstown | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queenstown | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queenstown | Regional Diversity Factor (Summer) | 0.76131
Queenstown | Regional Diversity Factor (Winter) | 0.8968
Queenstown | Load transfer capacity (MVA)1
Queenstown | Load transfer capacity (MVA)2
Queenstown | Load transfer capacity (MVA)3
Queenstown | Load transfer capacity (MVA)4
Queenstown | Load transfer capacity (MVA)5
Queenstown | Embedded generation capacity (MVA) Units less than 100 kVA | 2.329
Queenstown | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Railton | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Railton | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Railton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Railton | Maximum demand (peak season) (MW) | 48.657 | 46.2263 | 44.8277 | 45.4705 | 44.7294 | 44.701 | 44.7669 | 44.967 | 45.5626 | 47.4439 | 48.9801 | 50.0018
Railton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 9.877 | 9.3836 | 9.0997 | 9.2302 | 9.0798 | 9.074 | 9.0874 | 9.128 | 9.2489 | 9.6308 | 9.9426 | 10.15
Railton | Maximum demand (peak season) (MVA) | 49.6494 | 47.1691 | 45.742 | 46.3979 | 45.6417 | 45.6127 | 45.68 | 45.8841 | 46.4919 | 48.4115 | 49.9791 | 51.0216
Railton | Maximum demand (peak season) Power factor (coincident) | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001 | 0.98001
Railton | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Railton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 3.4318 | 2.8926 | 2.9745 | 2.9654 | 2.9154 | 2.88 | 2.8819 | 2.8763 | 2.9418 | 3.1191 | 3.2763 | 3.361
Railton | Maximum demand (non-peak season) (MVA) | 10.4022 | 8.7678 | 9.016 | 8.9883 | 8.8369 | 8.7295 | 8.7354 | 8.7185 | 8.917 | 9.4543 | 9.9307 | 10.1874
Railton | Hours exceeding 95% of maximum demand | 11.5
Railton | Hours exceeding Firm capacity (continuous rating) | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5 | 3424.5
Railton | Hours exceeding Firm capacity (short-term rating) | 868 | 868 | 868 | 868 | 868 | 868 | 868 | 868 | 868 | 868 | 868 | 868
Railton | Regional Diversity Factor (Summer) | 0.95827
Railton | Regional Diversity Factor (Winter) | 0.8359
Railton | Load transfer capacity (MVA)1 | 8.7 | [11 empty] | Devonport
Railton | Load transfer capacity (MVA)2 | 4.4 | [11 empty] | Ulverstone
Railton | Load transfer capacity (MVA)3
Railton | Load transfer capacity (MVA)4
Railton | Load transfer capacity (MVA)5
Railton | Embedded generation capacity (MVA) Units less than 100 kVA | 21.624
Railton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.042
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Total | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | Winter
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Rosebery 22kV | Maximum demand (peak season) (MW) | 2.4198 | 2.7883 | 2.6921 | 2.7137 | 2.6695 | 2.6678 | 2.6717 | 2.6837 | 2.7192 | 2.8315 | 2.9232 | 2.9842
Rosebery 22kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.54094 | 0.62334 | 0.60184 | 0.60666 | 0.59677 | 0.59639 | 0.59727 | 0.59994 | 0.60789 | 0.63299 | 0.65349 | 0.66712
Rosebery 22kV | Maximum demand (peak season) (MVA) | 2.4795 | 2.8572 | 2.7586 | 2.7807 | 2.7354 | 2.7337 | 2.7377 | 2.7499 | 2.7863 | 2.9014 | 2.9953 | 3.0578
Rosebery 22kV | Maximum demand (peak season) Power factor (coincident) | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591 | 0.97591
Rosebery 22kV | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Rosebery 22kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.4228 | 1.1993 | 1.2332 | 1.2294 | 1.2087 | 1.194 | 1.1948 | 1.1925 | 1.2197 | 1.2932 | 1.3583 | 1.3934
Rosebery 22kV | Maximum demand (non-peak season) (MVA) | 9.9223 | 8.3634 | 8.6001 | 8.5737 | 8.4293 | 8.3268 | 8.3324 | 8.3163 | 8.5057 | 9.0181 | 9.4725 | 9.7174
Rosebery 22kV | Hours exceeding 95% of maximum demand | 3
Rosebery 22kV | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV | Regional Diversity Factor (Summer) | 0.28607
Rosebery 22kV | Regional Diversity Factor (Winter) | 0.11432
Rosebery 22kV | Load transfer capacity (MVA)1
Rosebery 22kV | Load transfer capacity (MVA)2
Rosebery 22kV | Load transfer capacity (MVA)3
Rosebery 22kV | Load transfer capacity (MVA)4
Rosebery 22kV | Load transfer capacity (MVA)5
Rosebery 22kV | Embedded generation capacity (MVA) Units less than 100 kVA | 1.195
Rosebery 22kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Total | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | Winter
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Firm delivery | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Rosebery 44kV | Maximum demand (peak season) (MW) | 18.5561 | 23.3306 | 22.5258 | 22.7064 | 22.3363 | 22.3221 | 22.3551 | 22.455 | 22.7524 | 23.6918 | 24.459 | 24.9692
Rosebery 44kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 6.2775 | 7.8927 | 7.6205 | 7.6816 | 7.5564 | 7.5516 | 7.5627 | 7.5965 | 7.6971 | 8.0149 | 8.2745 | 8.4471
Rosebery 44kV | Maximum demand (peak season) (MVA) | 19.5892 | 24.6295 | 23.7799 | 23.9705 | 23.5799 | 23.5649 | 23.5996 | 23.7051 | 24.0191 | 25.0108 | 25.8207 | 26.3593
Rosebery 44kV | Maximum demand (peak season) Power factor (coincident) | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726 | 0.94726
Rosebery 44kV | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Rosebery 44kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 4.5789 | 3.8595 | 3.9687 | 3.9565 | 3.8899 | 3.8426 | 3.8452 | 3.8377 | 3.9251 | 4.1616 | 4.3713 | 4.4843
Rosebery 44kV | Maximum demand (non-peak season) (MVA) | 10.8349 | 9.1325 | 9.3911 | 9.3622 | 9.2045 | 9.0926 | 9.0987 | 9.0811 | 9.2879 | 9.8475 | 10.3437 | 10.6111
Rosebery 44kV | Hours exceeding 95% of maximum demand | 320
Rosebery 44kV | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 44kV | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 44kV | Regional Diversity Factor (Summer) | 0.99645
Rosebery 44kV | Regional Diversity Factor (Winter) | 0.94468
Rosebery 44kV | Load transfer capacity (MVA)1
Rosebery 44kV | Load transfer capacity (MVA)2
Rosebery 44kV | Load transfer capacity (MVA)3
Rosebery 44kV | Load transfer capacity (MVA)4
Rosebery 44kV | Load transfer capacity (MVA)5
Rosebery 44kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Rosebery 44kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Risdon 33kV | Substation capacity (winter and summer) (MVA) Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Winter
Risdon 33kV | Substation capacity (winter and summer) (MVA) Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Risdon 33kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Risdon 33kV | Maximum demand (peak season) (MW) | 70.4271 | 67.4446 | 65.1181 | 65.8936 | 66.4141 | 66.7818 | 66.8803 | 67.1792 | 68.069 | 70.8795 | 73.1746 | 74.701
Risdon 33kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 13.296 | 12.7329 | 12.2937 | 12.4401 | 12.5383 | 12.6078 | 12.6264 | 12.6828 | 12.8508 | 13.3814 | 13.8147 | 14.1028
Risdon 33kV | Maximum demand (peak season) (MVA) | 71.6712 | 68.636 | 66.2684 | 67.0576 | 67.5873 | 67.9615 | 68.0617 | 68.3659 | 69.2715 | 72.1316 | 74.4673 | 76.0206
Risdon 33kV | Maximum demand (peak season) Power factor (coincident) | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264 | 0.98264
Risdon 33kV | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Risdon 33kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.3465 | 1.9778 | 2.0338 | 2.0276 | 1.9934 | 1.9692 | 1.9705 | 1.9667 | 2.0115 | 2.1327 | 2.2401 | 2.298
Risdon 33kV | Maximum demand (non-peak season) (MVA) | 10.0963 | 8.51 | 8.7509 | 8.724 | 8.577 | 8.4728 | 8.4784 | 8.462 | 8.6547 | 9.1762 | 9.6386 | 9.8878
Risdon 33kV | Hours exceeding 95% of maximum demand | 188
Risdon 33kV | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon 33kV | Hours exceeding Firm capacity (short-term rating) | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251 | 1251
Risdon 33kV | Regional Diversity Factor (Summer) | 0.81236
Risdon 33kV | Regional Diversity Factor (Winter) | 0.93134
Risdon 33kV | Load transfer capacity (MVA)1
Risdon 33kV | Load transfer capacity (MVA)2
Risdon 33kV | Load transfer capacity (MVA)3
Risdon 33kV | Load transfer capacity (MVA)4
Risdon 33kV | Load transfer capacity (MVA)5
Risdon 33kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Risdon 33kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Rokeby | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Rokeby | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Rokeby | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Rokeby | Maximum demand (peak season) (MW) | 26.6898 | 26.3704 | 26.2515 | 26.462 | 26.4918 | 26.4749 | 26.514 | 26.6325 | 26.9853 | 28.0995 | 29.0093 | 29.6144
Rokeby | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.11332 | 0.11196 | 0.11146 | 0.11235 | 0.11248 | 0.11241 | 0.11257 | 0.11308 | 0.11457 | 0.11931 | 0.12317 | 0.12574
Rokeby | Maximum demand (peak season) (MVA) | 26.6901 | 26.3707 | 26.2518 | 26.4622 | 26.492 | 26.4752 | 26.5142 | 26.6327 | 26.9855 | 28.0997 | 29.0096 | 29.6147
Rokeby | Maximum demand (peak season) Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Rokeby | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Rokeby | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.29116 | 0.24541 | 0.25236 | 0.25158 | 0.24735 | 0.24434 | 0.2445 | 0.24403 | 0.24959 | 0.26462 | 0.27796 | 0.28514
Rokeby | Maximum demand (non-peak season) (MVA) | 9.8241 | 8.2806 | 8.515 | 8.4888 | 8.3458 | 8.2444 | 8.2499 | 8.2339 | 8.4215 | 8.9288 | 9.3788 | 9.6212
Rokeby | Hours exceeding 95% of maximum demand | 24.5
Rokeby | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | Regional Diversity Factor (Summer) | 1
Rokeby | Regional Diversity Factor (Winter) | 0.94399
Rokeby | Load transfer capacity (MVA)1 | 4.8 | [11 empty] | Howrah Zone
Rokeby | Load transfer capacity (MVA)2 | 4.8 | [11 empty] | Cambridge Zone
Rokeby | Load transfer capacity (MVA)3
Rokeby | Load transfer capacity (MVA)4
Rokeby | Load transfer capacity (MVA)5
Rokeby | Embedded generation capacity (MVA) Units less than 100 kVA | 20.966
Rokeby | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Scottsdale | Substation capacity (winter and summer) (MVA) Total | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | Winter
Scottsdale | Substation capacity (winter and summer) (MVA) Firm delivery | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5
Scottsdale | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
Scottsdale | Maximum demand (peak season) (MW) | 12.7525 | 13.2834 | 12.8252 | 12.928 | 12.7173 | 12.7092 | 12.728 | 12.7848 | 12.9542 | 13.4891 | 13.9258 | 14.2163
Scottsdale | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.34373 | 0.35804 | 0.34569 | 0.34846 | 0.34278 | 0.34256 | 0.34307 | 0.3446 | 0.34916 | 0.36358 | 0.37535 | 0.38318
Scottsdale | Maximum demand (peak season) (MVA) | 12.7572 | 13.2882 | 12.8298 | 12.9327 | 12.7219 | 12.7138 | 12.7326 | 12.7895 | 12.9589 | 13.494 | 13.9309 | 14.2215
Scottsdale | Maximum demand (peak season) Power factor (coincident) | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964
Scottsdale | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Scottsdale | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.5225 | 1.2833 | 1.3196 | 1.3155 | 1.2934 | 1.2776 | 1.2785 | 1.276 | 1.3051 | 1.3837 | 1.4534 | 1.491
Scottsdale | Maximum demand (non-peak season) (MVA) | 9.9371 | 8.3758 | 8.6129 | 8.5865 | 8.4418 | 8.3392 | 8.3448 | 8.3286 | 8.5183 | 9.0316 | 9.4866 | 9.7319
Scottsdale | Hours exceeding 95% of maximum demand | 8.5
Scottsdale | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scottsdale | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Scottsdale | Regional Diversity Factor (Summer) | 0.89771
Scottsdale | Regional Diversity Factor (Winter) | 0.96517
Scottsdale | Load transfer capacity (MVA)1 | 4.8 | [11 empty] | Derby
Scottsdale | Load transfer capacity (MVA)2 | 3.2 | [11 empty] | George Town
Scottsdale | Load transfer capacity (MVA)3
Scottsdale | Load transfer capacity (MVA)4
Scottsdale | Load transfer capacity (MVA)5
Scottsdale | Embedded generation capacity (MVA) Units less than 100 kVA | 9.851
Scottsdale | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Sheffield | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Sheffield | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Maximum demand (peak season) (MW) | 2.0662 | 2.1805 | 2.1053 | 2.1222 | 2.0876 | 2.0863 | 2.0893 | 2.0987 | 2.1265 | 2.2143 | 2.286 | 2.3336
Sheffield | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.18585 | 0.19613 | 0.18937 | 0.19088 | 0.18777 | 0.18765 | 0.18793 | 0.18877 | 0.19127 | 0.19917 | 0.20562 | 0.20991
Sheffield | Maximum demand (peak season) (MVA) | 2.0745 | 2.1893 | 2.1138 | 2.1307 | 2.096 | 2.0947 | 2.0978 | 2.1071 | 2.135 | 2.2232 | 2.2952 | 2.3431
Sheffield | Maximum demand (peak season) Power factor (coincident) | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598 | 0.99598
Sheffield | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Sheffield | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.1657 | 0.98258 | 1.0104 | 1.0073 | 0.99032 | 0.97828 | 0.97894 | 0.97704 | 0.99929 | 1.0595 | 1.1129 | 1.1417
Sheffield | Maximum demand (non-peak season) (MVA) | 9.8888 | 8.3351 | 8.571 | 8.5447 | 8.4007 | 8.2986 | 8.3042 | 8.2881 | 8.4769 | 8.9876 | 9.4405 | 9.6845
Sheffield | Hours exceeding 95% of maximum demand | 2
Sheffield | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Regional Diversity Factor (Summer) | 0
Sheffield | Regional Diversity Factor (Winter) | 0.84738
Sheffield | Load transfer capacity (MVA)1
Sheffield | Load transfer capacity (MVA)2
Sheffield | Load transfer capacity (MVA)3
Sheffield | Load transfer capacity (MVA)4
Sheffield | Load transfer capacity (MVA)5
Sheffield | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Sheffield | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
St Leonards | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
St Leonards | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
St Leonards | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
St Leonards | Maximum demand (peak season) (MW) | 15.2697 | 12.951 | 13.3176 | 13.2767 | 13.0531 | 12.8944 | 12.903 | 12.878 | 13.1713 | 13.9649 | 14.6686 | 15.0478
St Leonards | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.0592 | 0.8984 | 0.92383 | 0.92099 | 0.90548 | 0.89447 | 0.89507 | 0.89334 | 0.91368 | 0.96873 | 1.0175 | 1.0439
St Leonards | Maximum demand (peak season) (MVA) | 15.3064 | 12.9821 | 13.3496 | 13.3086 | 13.0844 | 12.9254 | 12.934 | 12.909 | 13.203 | 13.9985 | 14.7038 | 15.084
St Leonards | Maximum demand (peak season) Power factor (coincident) | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976 | 0.9976
St Leonards | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
St Leonards | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.19843 | 0.16725 | 0.17199 | 0.17146 | 0.16857 | 0.16652 | 0.16663 | 0.16631 | 0.1701 | 0.18035 | 0.18943 | 0.19433
St Leonards | Maximum demand (non-peak season) (MVA) | 9.8218 | 8.2786 | 8.513 | 8.4868 | 8.3439 | 8.2424 | 8.248 | 8.232 | 8.4195 | 8.9267 | 9.3766 | 9.619
St Leonards | Hours exceeding 95% of maximum demand | 2
St Leonards | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | Regional Diversity Factor (Summer) | 0.96618
St Leonards | Regional Diversity Factor (Winter) | 0.93578
St Leonards | Load transfer capacity (MVA)1 | 3 | [11 empty] | Trevallyn
St Leonards | Load transfer capacity (MVA)2 | 3 | [11 empty] | Mowbray
St Leonards | Load transfer capacity (MVA)3 | 10 | [11 empty] | Norwood
St Leonards | Load transfer capacity (MVA)4
St Leonards | Load transfer capacity (MVA)5
St Leonards | Embedded generation capacity (MVA) Units less than 100 kVA | 15.206
St Leonards | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
St Marys | Substation capacity (winter and summer) (MVA) Total | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Summer
St Marys | Substation capacity (winter and summer) (MVA) Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
St Marys | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
St Marys | Maximum demand (peak season) (MW) | 11.7755 | 10.3494 | 10.6424 | 10.6097 | 10.431 | 10.3042 | 10.3111 | 10.2911 | 10.5255 | 11.1596 | 11.722 | 12.025
St Marys | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.033224 | 0.0292 | 0.030027 | 0.029934 | 0.02943 | 0.029072 | 0.029092 | 0.029036 | 0.029697 | 0.031486 | 0.033073 | 0.033928
St Marys | Maximum demand (peak season) (MVA) | 11.7756 | 10.3494 | 10.6424 | 10.6097 | 10.431 | 10.3042 | 10.3111 | 10.2911 | 10.5255 | 11.1597 | 11.722 | 12.0251
St Marys | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
St Marys | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
St Marys | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.38774 | 0.32682 | 0.33607 | 0.33503 | 0.32939 | 0.32539 | 0.32561 | 0.32498 | 0.33238 | 0.3524 | 0.37016 | 0.37973
St Marys | Maximum demand (non-peak season) (MVA) | 9.8275 | 8.2834 | 8.5179 | 8.4917 | 8.3487 | 8.2472 | 8.2527 | 8.2367 | 8.4243 | 8.9319 | 9.3819 | 9.6245
St Marys | Hours exceeding 95% of maximum demand | 2
St Marys | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | Regional Diversity Factor (Summer) | 0.78517
St Marys | Regional Diversity Factor (Winter) | 0.98604
St Marys | Load transfer capacity (MVA)1 | 2.8 | [11 empty] | Avoca
St Marys | Load transfer capacity (MVA)2 | 4.5 | [11 empty] | Triabunna
St Marys | Load transfer capacity (MVA)3 | 4 | [11 empty] | Derby
St Marys | Load transfer capacity (MVA)4
St Marys | Load transfer capacity (MVA)5
St Marys | Embedded generation capacity (MVA) Units less than 100 kVA | 15.463
St Marys | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Sorell | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Sorell | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Sorell | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Sorell | Maximum demand (peak season) (MW) | 37.4014 | 34.421 | 33.2336 | 33.5 | 32.954 | 32.9331 | 32.9817 | 33.1291 | 33.5679 | 34.9539 | 36.0857 | 36.8384
Sorell | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sorell | Maximum demand (peak season) (MVA) | 37.4014 | 34.421 | 33.2336 | 33.5 | 32.954 | 32.9331 | 32.9817 | 33.1291 | 33.5679 | 34.9539 | 36.0857 | 36.8384
Sorell | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
Sorell | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Sorell | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sorell | Maximum demand (non-peak season) (MVA) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Sorell | Hours exceeding 95% of maximum demand | 4
Sorell | Hours exceeding Firm capacity (continuous rating) | 632 | 632 | 632 | 632 | 632 | 632 | 632 | 632 | 632 | 632 | 632 | 632
Sorell | Hours exceeding Firm capacity (short-term rating) | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5 | 88.5
Sorell | Regional Diversity Factor (Summer) | 1
Sorell | Regional Diversity Factor (Winter) | 0.91948
Sorell | Load transfer capacity (MVA)1 | 1.5 | [11 empty] | Avoca
Sorell | Load transfer capacity (MVA)2 | 1.5 | [11 empty] | Triabunna
Sorell | Load transfer capacity (MVA)3 | 1.5 | [11 empty] | Meadowbank
Sorell | Load transfer capacity (MVA)4
Sorell | Load transfer capacity (MVA)5
Sorell | Embedded generation capacity (MVA) Units less than 100 kVA | 32.257
Sorell | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.022
Savage River DL | Substation capacity (winter and summer) (MVA) Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Savage River DL | Substation capacity (winter and summer) (MVA) Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Savage River DL | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Savage River DL | Maximum demand (peak season) (MW) | 1.2171 | 1.5583 | 1.5046 | 1.5166 | 1.4919 | 1.491 | 1.4932 | 1.4998 | 1.5197 | 1.5825 | 1.6337 | 1.6678
Savage River DL | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.032683 | 0.041845 | 0.040401 | 0.040725 | 0.040061 | 0.040036 | 0.040095 | 0.040274 | 0.040808 | 0.042493 | 0.043869 | 0.044784
Savage River DL | Maximum demand (peak season) (MVA) | 1.2176 | 1.5589 | 1.5051 | 1.5172 | 1.4925 | 1.4915 | 1.4937 | 1.5004 | 1.5203 | 1.583 | 1.6343 | 1.6684
Savage River DL | Maximum demand (peak season) Power factor (coincident) | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964 | 0.99964
Savage River DL | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Savage River DL | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.63759 | 0.53742 | 0.55263 | 0.55093 | 0.54165 | 0.53507 | 0.53543 | 0.53439 | 0.54656 | 0.57949 | 0.60869 | 0.62443
Savage River DL | Maximum demand (non-peak season) (MVA) | 9.8405 | 8.2944 | 8.5292 | 8.503 | 8.3597 | 8.2581 | 8.2636 | 8.2476 | 8.4355 | 8.9437 | 9.3944 | 9.6373
Savage River DL | Hours exceeding 95% of maximum demand | 5.5
Savage River DL | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River DL | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River DL | Regional Diversity Factor (Summer) | 0.46946
Savage River DL | Regional Diversity Factor (Winter) | 0.66681
Savage River DL | Load transfer capacity (MVA)1
Savage River DL | Load transfer capacity (MVA)2
Savage River DL | Load transfer capacity (MVA)3
Savage River DL | Load transfer capacity (MVA)4
Savage River DL | Load transfer capacity (MVA)5
Savage River DL | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Savage River DL | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Smithton | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Smithton | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Smithton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Smithton | Maximum demand (peak season) (MW) | 22.4298 | 22.1401 | 21.3764 | 21.5478 | 21.1966 | 21.1831 | 21.2144 | 21.3092 | 21.5914 | 22.4829 | 23.2109 | 23.6951
Smithton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 4.4404 | 4.3831 | 4.2319 | 4.2658 | 4.1963 | 4.1936 | 4.1998 | 4.2186 | 4.2744 | 4.4509 | 4.595 | 4.6909
Smithton | Maximum demand (peak season) (MVA) | 22.8651 | 22.5698 | 21.7913 | 21.966 | 21.6079 | 21.5942 | 21.6261 | 21.7227 | 22.0105 | 22.9193 | 23.6614 | 24.1549
Smithton | Maximum demand (peak season) Power factor (coincident) | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096 | 0.98096
Smithton | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Smithton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 3.4703 | 2.9251 | 3.0079 | 2.9986 | 2.9481 | 2.9123 | 2.9142 | 2.9086 | 2.9748 | 3.1541 | 3.313 | 3.3987
Smithton | Maximum demand (non-peak season) (MVA) | 10.415 | 8.7786 | 9.0271 | 8.9994 | 8.8478 | 8.7402 | 8.7461 | 8.7292 | 8.928 | 9.4659 | 9.9428 | 10.1999
Smithton | Hours exceeding 95% of maximum demand | 0.5
Smithton | Hours exceeding Firm capacity (continuous rating) | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784
Smithton | Hours exceeding Firm capacity (short-term rating) | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784
Smithton | Regional Diversity Factor (Summer) | 0.96081
Smithton | Regional Diversity Factor (Winter) | 0.9839
Smithton | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Port Latta
Smithton | Load transfer capacity (MVA)2
Smithton | Load transfer capacity (MVA)3
Smithton | Load transfer capacity (MVA)4
Smithton | Load transfer capacity (MVA)5
Smithton | Embedded generation capacity (MVA) Units less than 100 kVA | 6.168
Smithton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Triabunna (RT) | Maximum demand (peak season) (MW) | 6.7857 | 7.1021 | 6.8571 | 6.9121 | 6.7994 | 6.7951 | 6.8051 | 6.8355 | 6.9261 | 7.2121 | 7.4456 | 7.6009
Triabunna (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.37706 | 0.39464 | 0.38103 | 0.38409 | 0.37783 | 0.37759 | 0.37814 | 0.37983 | 0.38486 | 0.40075 | 0.41373 | 0.42236
Triabunna (RT) | Maximum demand (peak season) (MVA) | 6.7962 | 7.1131 | 6.8677 | 6.9227 | 6.8099 | 6.8056 | 6.8156 | 6.8461 | 6.9368 | 7.2232 | 7.4571 | 7.6126
Triabunna (RT) | Maximum demand (peak season) Power factor (coincident) | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846
Triabunna (RT) | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Triabunna (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.27346 | 0.2305 | 0.23702 | 0.23629 | 0.23231 | 0.22949 | 0.22964 | 0.2292 | 0.23442 | 0.24854 | 0.26106 | 0.26781
Triabunna (RT) | Maximum demand (non-peak season) (MVA) | 9.8236 | 8.2801 | 8.5145 | 8.4884 | 8.3454 | 8.244 | 8.2495 | 8.2335 | 8.421 | 8.9284 | 9.3783 | 9.6207
Triabunna (RT) | Hours exceeding 95% of maximum demand | 12
Triabunna (RT) | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Triabunna (RT) | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Triabunna (RT) | Regional Diversity Factor (Summer) | 0.9129
Triabunna (RT) | Regional Diversity Factor (Winter) | 0.87448
Triabunna (RT) | Load transfer capacity (MVA)1 | 3 | [11 empty] | St Marys
Triabunna (RT) | Load transfer capacity (MVA)2 | 1.8 | [11 empty] | Sorell
Triabunna (RT) | Load transfer capacity (MVA)3
Triabunna (RT) | Load transfer capacity (MVA)4
Triabunna (RT) | Load transfer capacity (MVA)5
Triabunna (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Triabunna (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Trevallyn | Substation capacity (winter and summer) (MVA) Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Winter
Trevallyn | Substation capacity (winter and summer) (MVA) Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Trevallyn | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
Trevallyn | Maximum demand (peak season) (MW) | 71.9031 | 70.8771 | 68.4322 | 69.318 | 68.9925 | 68.9487 | 69.0504 | 69.359 | 70.2777 | 73.1794 | 75.5489 | 77.1248
Trevallyn | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.4383 | 1.4178 | 1.3689 | 1.3866 | 1.3801 | 1.3792 | 1.3813 | 1.3874 | 1.4058 | 1.4639 | 1.5113 | 1.5428
Trevallyn | Maximum demand (peak season) (MVA) | 71.9175 | 70.8913 | 68.4459 | 69.3319 | 69.0063 | 68.9625 | 69.0642 | 69.3729 | 70.2917 | 73.194 | 75.564 | 77.1403
Trevallyn | Maximum demand (peak season) Power factor (coincident) | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998
Trevallyn | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Trevallyn | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.10892 | 0.091803 | 0.094402 | 0.094112 | 0.092526 | 0.091402 | 0.091463 | 0.091286 | 0.093365 | 0.09899 | 0.10398 | 0.10667
Trevallyn | Maximum demand (non-peak season) (MVA) | 9.8204 | 8.2775 | 8.5118 | 8.4856 | 8.3427 | 8.2413 | 8.2468 | 8.2308 | 8.4183 | 8.9255 | 9.3752 | 9.6176
Trevallyn | Hours exceeding 95% of maximum demand | 2
Trevallyn | Hours exceeding Firm capacity (continuous rating) | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5 | 8783.5
Trevallyn | Hours exceeding Firm capacity (short-term rating) | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767 | 8767
Trevallyn | Regional Diversity Factor (Summer) | 0.95391
Trevallyn | Regional Diversity Factor (Winter) | 0.99922
Trevallyn | Load transfer capacity (MVA)1 | 3.6 | [11 empty] | George Town
Trevallyn | Load transfer capacity (MVA)2 | 36.1 | [11 empty] | Mowbray
Trevallyn | Load transfer capacity (MVA)3 | 21.7 | [11 empty] | Norwood
Trevallyn | Load transfer capacity (MVA)4 | 21.7 | [11 empty] | St Leonards
Trevallyn | Load transfer capacity (MVA)5 | 14.4 | [11 empty] | Hadspen
Trevallyn | Embedded generation capacity (MVA) Units less than 100 kVA | 46.227
Trevallyn | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.06
Tungatinah | Substation capacity (winter and summer) (MVA) Total | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | Winter
Tungatinah | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Maximum demand (peak season) (MW) | 1.1416 | 1.0412 | 1.0053 | 1.0133 | 0.99681 | 0.99618 | 0.99765 | 1.0021 | 1.0154 | 1.0573 | 1.0915 | 1.1143
Tungatinah | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.063521 | 0.057934 | 0.055936 | 0.056384 | 0.055465 | 0.05543 | 0.055511 | 0.05576 | 0.056498 | 0.058831 | 0.060736 | 0.062003
Tungatinah | Maximum demand (peak season) (MVA) | 1.1434 | 1.0428 | 1.0068 | 1.0149 | 0.99835 | 0.99772 | 0.99919 | 1.0037 | 1.017 | 1.0589 | 1.0932 | 1.116
Tungatinah | Maximum demand (peak season) Power factor (coincident) | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846 | 0.99846
Tungatinah | Maximum demand (non-peak season) (MW) | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617
Tungatinah | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.47241 | 0.39819 | 0.40946 | 0.4082 | 0.40132 | 0.39644 | 0.39671 | 0.39594 | 0.40496 | 0.42936 | 0.45099 | 0.46265
Tungatinah | Maximum demand (non-peak season) (MVA) | 9.8312 | 8.2865 | 8.5211 | 8.4949 | 8.3518 | 8.2503 | 8.2558 | 8.2398 | 8.4275 | 8.9352 | 9.3855 | 9.6281
Tungatinah | Hours exceeding 95% of maximum demand | 8
Tungatinah | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Regional Diversity Factor (Summer) | 0.59686
Tungatinah | Regional Diversity Factor (Winter) | 0.75049
Tungatinah | Load transfer capacity (MVA)1
Tungatinah | Load transfer capacity (MVA)2
Tungatinah | Load transfer capacity (MVA)3
Tungatinah | Load transfer capacity (MVA)4
Tungatinah | Load transfer capacity (MVA)5
Tungatinah | Embedded generation capacity (MVA) Units less than 100 kVA | 0.228
Tungatinah | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Ulverstone | Substation capacity (winter and summer) (MVA) Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Ulverstone | Substation capacity (winter and summer) (MVA) Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Ulverstone | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
Ulverstone | Maximum demand (peak season) (MW) | 32.8095 | 28.5973 | 27.6108 | 27.8322 | 27.3786 | 27.3612 | 27.4015 | 27.524 | 27.8886 | 29.0401 | 29.9804 | 30.6058
Ulverstone | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.18874 | 0.16451 | 0.15884 | 0.16011 | 0.1575 | 0.1574 | 0.15763 | 0.15834 | 0.16043 | 0.16706 | 0.17247 | 0.17606
Ulverstone | Maximum demand (peak season) (MVA) | 32.81 | 28.5978 | 27.6113 | 27.8326 | 27.379 | 27.3616 | 27.402 | 27.5245 | 27.889 | 29.0405 | 29.9809 | 30.6063
Ulverstone | Maximum demand (peak season) Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Ulverstone | Maximum demand (non-peak season) (MW) | 21.8148 | 22.8536 | 23.5005 | 23.4283 | 23.457 | 23.1719 | 23.1874 | 23.1425 | 23.6696 | 25.0956 | 26.3602 | 27.0417
Ulverstone | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.2945 | 2.4038 | 2.4718 | 2.4642 | 2.4672 | 2.4372 | 2.4389 | 2.4342 | 2.4896 | 2.6396 | 2.7726 | 2.8443
Ulverstone | Maximum demand (non-peak season) (MVA) | 21.9352 | 22.9797 | 23.6302 | 23.5576 | 23.5864 | 23.2997 | 23.3153 | 23.2702 | 23.8001 | 25.2341 | 26.5056 | 27.1909
Ulverstone | Hours exceeding 95% of maximum demand | 5
Ulverstone | Hours exceeding Firm capacity (continuous rating) | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784
Ulverstone | Hours exceeding Firm capacity (short-term rating) | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784
Ulverstone | Regional Diversity Factor (Summer) | 0.72803
Ulverstone | Regional Diversity Factor (Winter) | 1
Ulverstone | Load transfer capacity (MVA)1 | 6.8 | [11 empty] | Burnie
Ulverstone | Load transfer capacity (MVA)2 | 10.3 | [11 empty] | Devonport
Ulverstone | Load transfer capacity (MVA)3 | 3.4 | [11 empty] | Railton
Ulverstone | Load transfer capacity (MVA)4
Ulverstone | Load transfer capacity (MVA)5
Ulverstone | Embedded generation capacity (MVA) Units less than 100 kVA | 23.656
Ulverstone | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Waddamana | Substation capacity (winter and summer) (MVA) Total | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Winter
Waddamana | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Maximum demand (peak season) (MW) | 0.68766 | 0.697 | 0.67296 | 0.67835 | 0.6673 | 0.66687 | 0.66786 | 0.67084 | 0.67973 | 0.70779 | 0.73071 | 0.74595
Waddamana | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.030979 | 0.0314 | 0.030317 | 0.03056 | 0.030062 | 0.030043 | 0.030087 | 0.030222 | 0.030622 | 0.031886 | 0.032919 | 0.033605
Waddamana | Maximum demand (peak season) (MVA) | 0.68835 | 0.69771 | 0.67364 | 0.67904 | 0.66797 | 0.66755 | 0.66853 | 0.67152 | 0.68042 | 0.70851 | 0.73145 | 0.74671
Waddamana | Maximum demand (peak season) Power factor (coincident) | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899 | 0.99899
Waddamana | Maximum demand (non-peak season) (MW) | 21.8148 | 22.8536 | 23.5005 | 23.4283 | 23.457 | 23.1719 | 23.1874 | 23.1425 | 23.6696 | 25.0956 | 26.3602 | 27.0417
Waddamana | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 5.6108 | 5.878 | 6.0444 | 6.0258 | 6.0332 | 5.9598 | 5.9638 | 5.9523 | 6.0878 | 6.4546 | 6.7799 | 6.9551
Waddamana | Maximum demand (non-peak season) (MVA) | 22.5248 | 23.5974 | 24.2654 | 24.1908 | 24.2204 | 23.926 | 23.942 | 23.8957 | 24.4399 | 25.9124 | 27.2181 | 27.9218
Waddamana | Hours exceeding 95% of maximum demand | 2
Waddamana | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Regional Diversity Factor (Summer) | 0.53712
Waddamana | Regional Diversity Factor (Winter) | 0.45079
Waddamana | Load transfer capacity (MVA)1 | 0.9 | [11 empty] | Arthurs Lake
Waddamana | Load transfer capacity (MVA)2
Waddamana | Load transfer capacity (MVA)3
Waddamana | Load transfer capacity (MVA)4
Waddamana | Load transfer capacity (MVA)5
Waddamana | Embedded generation capacity (MVA) Units less than 100 kVA | 0.791
Waddamana | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Wesley Vale | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Wesley Vale | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Wesley Vale | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Wesley Vale | Maximum demand (peak season) (MW) | 11.6091 | 18.6033 | 17.9616 | 18.1056 | 17.8105 | 17.7992 | 17.8254 | 17.9051 | 18.1423 | 18.8914 | 19.5031 | 19.9099
Wesley Vale | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.28634 | 0.45886 | 0.44303 | 0.44658 | 0.4393 | 0.43902 | 0.43967 | 0.44164 | 0.44749 | 0.46596 | 0.48105 | 0.49109
Wesley Vale | Maximum demand (peak season) (MVA) | 11.6127 | 18.609 | 17.9671 | 18.1111 | 17.8159 | 17.8046 | 17.8309 | 17.9106 | 18.1478 | 18.8971 | 19.509 | 19.9159
Wesley Vale | Maximum demand (peak season) Power factor (coincident) | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997 | 0.9997
Wesley Vale | Maximum demand (non-peak season) (MW) | 21.8148 | 22.8536 | 23.5005 | 23.4283 | 23.457 | 23.1719 | 23.1874 | 23.1425 | 23.6696 | 25.0956 | 26.3602 | 27.0417
Wesley Vale | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.0329 | 2.1297 | 2.19 | 2.1833 | 2.1859 | 2.1594 | 2.1608 | 2.1566 | 2.2057 | 2.3386 | 2.4565 | 2.52
Wesley Vale | Maximum demand (non-peak season) (MVA) | 21.9094 | 22.9526 | 23.6024 | 23.5298 | 23.5586 | 23.2723 | 23.2878 | 23.2428 | 23.7721 | 25.2044 | 26.4744 | 27.1589
Wesley Vale | Hours exceeding 95% of maximum demand | 1.5
Wesley Vale | Hours exceeding Firm capacity (continuous rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wesley Vale | Hours exceeding Firm capacity (short-term rating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wesley Vale | Regional Diversity Factor (Summer) | 0.75764
Wesley Vale | Regional Diversity Factor (Winter) | 0.99276
Wesley Vale | Load transfer capacity (MVA)1
Wesley Vale | Load transfer capacity (MVA)2
Wesley Vale | Load transfer capacity (MVA)3
Wesley Vale | Load transfer capacity (MVA)4
Wesley Vale | Load transfer capacity (MVA)5
Wesley Vale | Embedded generation capacity (MVA) Units less than 100 kVA | 10.335
Wesley Vale | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.019
ZONE |  | 2023 (Actuals) | 2024 (Actuals) | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Load transfer point | Peaking season
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Bellerive | Sub-transmission lines capacityTotal (winter) | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683
Zs-Bellerive | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Bellerive | Sub-transmission lines capacityTotal (summer) | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071
Zs-Bellerive | Sub-transmission lines capacityFirm delivery (summer) | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035
Zs-Bellerive | Maximum demand forecast(peak season)Maximum demand (MVA) | 11.3973 | 9.9121 | 9.5702 | 9.6469 | 9.4897 | 9.4836 | 9.4976 | 9.5401 | 9.6664 | 10.0656 | 10.3915 | 10.6082
Zs-Bellerive | Maximum demand forecast(peak season)Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Zs-Bellerive | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 11.3973 | 9.9121 | 9.5702 | 9.6469 | 9.4897 | 9.4836 | 9.4976 | 9.5401 | 9.6664 | 10.0656 | 10.3915 | 10.6082
Zs-Bellerive | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Zs-Bellerive | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Load transfer capacity (MVA)1 | 3.1 | [11 empty] | Rokeby
Zs-Bellerive | Load transfer capacity (MVA)2 | 3.1 | [11 empty] | Howrah Zone
Zs-Bellerive | Load transfer capacity (MVA)3 | 6.2 | [11 empty] | Cambridge Zone
Zs-Bellerive | Load transfer capacity (MVA)4 | 4.1 | [11 empty] | Geilston Bay
Zs-Bellerive | Embedded generation capacity (MVA)Units less than 100 kVA | 6.108
Zs-Bellerive | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.014
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Zs-Cambridge | Sub-transmission lines capacityTotal (winter) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
Zs-Cambridge | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Sub-transmission lines capacityTotal (summer) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
Zs-Cambridge | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Maximum demand forecast(peak season)Maximum demand (MVA) | 16.2424 | 15.3721 | 14.8418 | 16.5959 | 16.3254 | 16.3151 | 16.3391 | 16.4122 | 16.6296 | 17.3162 | 17.8769 | 18.2498
Zs-Cambridge | Maximum demand forecast(peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Zs-Cambridge | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 16.2421 | 15.3718 | 14.8415 | 16.5956 | 16.3251 | 16.3148 | 16.3388 | 16.4119 | 16.6292 | 17.3158 | 17.8765 | 18.2494
Zs-Cambridge | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
Zs-Cambridge | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Load transfer capacity (MVA)1 | 7.4 | [11 empty] | Rokeby
Zs-Cambridge | Load transfer capacity (MVA)2 | 7.4 | [11 empty] | Bellerive
Zs-Cambridge | Load transfer capacity (MVA)3
Zs-Cambridge | Load transfer capacity (MVA)4
Zs-Cambridge | Embedded generation capacity (MVA)Units less than 100 kVA | 7.805
Zs-Cambridge | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-Claremont | Substation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Zs-Claremont | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Claremont | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Zs-Claremont | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-Claremont | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Claremont | Sub-transmission lines capacityTotal (summer) | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356
Zs-Claremont | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Claremont | Maximum demand forecast(peak season)Maximum demand (MVA) | 23.5187 | 22.1028 | 21.3403 | 21.5114 | 21.1608 | 21.1474 | 21.1786 | 21.2732 | 21.555 | 22.445 | 23.1717 | 23.6551
Zs-Claremont | Maximum demand forecast(peak season)Power factor (coincident) | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962 | 0.99962
Zs-Claremont | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 23.53 | 22.1134 | 21.3506 | 21.5217 | 21.171 | 21.1575 | 21.1887 | 21.2834 | 21.5653 | 22.4558 | 23.1829 | 23.6665
Zs-Claremont | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914
Zs-Claremont | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Claremont | Load transfer capacity (MVA)1
Zs-Claremont | Load transfer capacity (MVA)2
Zs-Claremont | Load transfer capacity (MVA)3
Zs-Claremont | Load transfer capacity (MVA)4
Zs-Claremont | Embedded generation capacity (MVA)Units less than 100 kVA | 11.167
Zs-Claremont | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Derwent Park | Sub-transmission lines capacityTotal (winter) | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666
Zs-Derwent Park | Sub-transmission lines capacityFirm delivery (winter) | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325
Zs-Derwent Park | Sub-transmission lines capacityTotal (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-Derwent Park | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Derwent Park | Maximum demand forecast(peak season)Maximum demand (MVA) | 20.1421 | 18.6983 | 18.0533 | 18.198 | 17.9014 | 17.8901 | 17.9164 | 17.9965 | 18.2349 | 18.9878 | 19.6026 | 20.0115
Zs-Derwent Park | Maximum demand forecast(peak season)Power factor (coincident) | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891 | 0.98891
Zs-Derwent Park | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 20.4525 | 18.9864 | 18.3315 | 18.4785 | 18.1773 | 18.1658 | 18.1925 | 18.2739 | 18.5159 | 19.2804 | 19.9047 | 20.3199
Zs-Derwent Park | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739 | 0.9739
Zs-Derwent Park | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Derwent Park | Load transfer capacity (MVA)1
Zs-Derwent Park | Load transfer capacity (MVA)2
Zs-Derwent Park | Load transfer capacity (MVA)3
Zs-Derwent Park | Load transfer capacity (MVA)4
Zs-Derwent Park | Embedded generation capacity (MVA)Units less than 100 kVA | 3.878
Zs-Derwent Park | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-East Hobart | Sub-transmission lines capacityTotal (winter) | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196
Zs-East Hobart | Sub-transmission lines capacityFirm delivery (winter) | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054
Zs-East Hobart | Sub-transmission lines capacityTotal (summer) | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196
Zs-East Hobart | Sub-transmission lines capacityFirm delivery (summer) | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054
Zs-East Hobart | Maximum demand forecast(peak season)Maximum demand (MVA) | 29.1795 | 28.0967 | 27.1275 | 27.345 | 28.5197 | 28.9182 | 28.9608 | 29.0902 | 29.4756 | 30.6926 | 31.6864 | 32.3474
Zs-East Hobart | Maximum demand forecast(peak season)Power factor (coincident) | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397 | 0.98397
Zs-East Hobart | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 29.5729 | 28.4755 | 27.4933 | 27.7137 | 28.9043 | 29.3081 | 29.3513 | 29.4825 | 29.873 | 31.1065 | 32.1137 | 32.7836
Zs-East Hobart | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088 | 0.97088
Zs-East Hobart | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Load transfer capacity (MVA)1
Zs-East Hobart | Load transfer capacity (MVA)2
Zs-East Hobart | Load transfer capacity (MVA)3
Zs-East Hobart | Load transfer capacity (MVA)4
Zs-East Hobart | Embedded generation capacity (MVA)Units less than 100 kVA | 0.491
Zs-East Hobart | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.027
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Geilston Bay | Sub-transmission lines capacityTotal (winter) | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683
Zs-Geilston Bay | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Geilston Bay | Sub-transmission lines capacityTotal (summer) | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356
Zs-Geilston Bay | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Geilston Bay | Maximum demand forecast(peak season)Maximum demand (MVA) | 19.8186 | 18.3727 | 17.7389 | 17.8811 | 17.5897 | 17.5785 | 17.6044 | 17.6831 | 17.9173 | 18.6571 | 19.2613 | 19.663
Zs-Geilston Bay | Maximum demand forecast(peak season)Power factor (coincident) | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967 | 0.99967
Zs-Geilston Bay | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 19.8125 | 18.367 | 17.7335 | 17.8756 | 17.5843 | 17.5731 | 17.599 | 17.6777 | 17.9119 | 18.6514 | 19.2554 | 19.657
Zs-Geilston Bay | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997
Zs-Geilston Bay | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Geilston Bay | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Bellerive
Zs-Geilston Bay | Load transfer capacity (MVA)2 | 5.1 | [11 empty] | Derwent Park
Zs-Geilston Bay | Load transfer capacity (MVA)3 | 3.8 | [11 empty] | East Hobart
Zs-Geilston Bay | Load transfer capacity (MVA)4
Zs-Geilston Bay | Embedded generation capacity (MVA)Units less than 100 kVA | 10.85
Zs-Geilston Bay | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Howrah | Substation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Zs-Howrah | Substation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Zs-Howrah | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
Zs-Howrah | Sub-transmission lines capacityTotal (winter) | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124
Zs-Howrah | Sub-transmission lines capacityFirm delivery (winter) | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062
Zs-Howrah | Sub-transmission lines capacityTotal (summer) | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124
Zs-Howrah | Sub-transmission lines capacityFirm delivery (summer) | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062
Zs-Howrah | Maximum demand forecast(peak season)Maximum demand (MVA) | 23.534 | 18.3139 | 17.6822 | 17.824 | 17.5334 | 17.5223 | 17.5482 | 17.6266 | 17.8601 | 18.5975 | 19.1997 | 19.6002
Zs-Howrah | Maximum demand forecast(peak season)Power factor (coincident) | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897 | 0.99897
Zs-Howrah | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 23.5728 | 18.3441 | 17.7113 | 17.8533 | 17.5623 | 17.5512 | 17.577 | 17.6556 | 17.8895 | 18.6281 | 19.2313 | 19.6324
Zs-Howrah | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733 | 0.99733
Zs-Howrah | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Howrah | Load transfer capacity (MVA)1 | 7.1 | [11 empty] | Rokeby
Zs-Howrah | Load transfer capacity (MVA)2 | 2.4 | [11 empty] | Bellerive
Zs-Howrah | Load transfer capacity (MVA)3
Zs-Howrah | Load transfer capacity (MVA)4
Zs-Howrah | Embedded generation capacity (MVA)Units less than 100 kVA | 13.516
Zs-Howrah | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-New Town | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-New Town | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-New Town | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-New Town | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-New Town | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-New Town | Sub-transmission lines capacityTotal (summer) | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662
Zs-New Town | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-New Town | Maximum demand forecast(peak season)Maximum demand (MVA) | 22.9582 | 21.2507 | 20.5176 | 20.9364 | 20.5952 | 20.5821 | 20.6125 | 20.7046 | 20.9788 | 21.845 | 22.5524 | 23.0228
Zs-New Town | Maximum demand forecast(peak season)Power factor (coincident) | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662 | 0.99662
Zs-New Town | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 22.9587 | 21.2511 | 20.518 | 20.9368 | 20.5956 | 20.5825 | 20.6129 | 20.705 | 20.9792 | 21.8455 | 22.5528 | 23.0233
Zs-New Town | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966
Zs-New Town | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-New Town | Load transfer capacity (MVA)1
Zs-New Town | Load transfer capacity (MVA)2
Zs-New Town | Load transfer capacity (MVA)3
Zs-New Town | Load transfer capacity (MVA)4
Zs-New Town | Embedded generation capacity (MVA)Units less than 100 kVA | 8.702
Zs-New Town | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.032
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Sub-transmission lines capacityTotal (winter) | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911
Zs-Rosny Park | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Sub-transmission lines capacityTotal (summer) | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911
Zs-Rosny Park | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Maximum demand forecast(peak season)Maximum demand (MVA) | 15.8065 | 15.1282 | 14.6063 | 14.7234 | 14.4835 | 14.4743 | 14.4956 | 14.5604 | 14.7533 | 15.3624 | 15.8599 | 16.1907
Zs-Rosny Park | Maximum demand forecast(peak season)Power factor (coincident) | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919
Zs-Rosny Park | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 15.797 | 15.1192 | 14.5976 | 14.7146 | 14.4748 | 14.4656 | 14.487 | 14.5517 | 14.7445 | 15.3532 | 15.8504 | 16.181
Zs-Rosny Park | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979 | 0.99979
Zs-Rosny Park | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Load transfer capacity (MVA)1
Zs-Rosny Park | Load transfer capacity (MVA)2
Zs-Rosny Park | Load transfer capacity (MVA)3
Zs-Rosny Park | Load transfer capacity (MVA)4
Zs-Rosny Park | Embedded generation capacity (MVA)Units less than 100 kVA | 7.466
Zs-Rosny Park | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-Sandy Bay | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-Sandy Bay | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Sandy Bay | Sub-transmission lines capacityTotal (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-Sandy Bay | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Sandy Bay | Maximum demand forecast(peak season)Maximum demand (MVA) | 38.6892 | 34.7075 | 33.5103 | 33.7789 | 33.2284 | 33.2073 | 33.2562 | 33.4049 | 33.8473 | 35.2449 | 36.3861 | 37.1451
Zs-Sandy Bay | Maximum demand forecast(peak season)Power factor (coincident) | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986
Zs-Sandy Bay | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 38.6839 | 34.7027 | 33.5057 | 33.7743 | 33.2238 | 33.2027 | 33.2517 | 33.4003 | 33.8427 | 35.24 | 36.3811 | 37.14
Zs-Sandy Bay | Maximum demand forecast(non-peak season)Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
Zs-Sandy Bay | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Sandy Bay | Load transfer capacity (MVA)1
Zs-Sandy Bay | Load transfer capacity (MVA)2
Zs-Sandy Bay | Load transfer capacity (MVA)3
Zs-Sandy Bay | Load transfer capacity (MVA)4
Zs-Sandy Bay | Embedded generation capacity (MVA)Units less than 100 kVA | 18.762
Zs-Sandy Bay | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.011
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Sub-transmission lines capacityTotal (winter) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
Zs-Summerleas | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Sub-transmission lines capacityTotal (summer) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
Zs-Summerleas | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Maximum demand forecast(peak season)Maximum demand (MVA) | 12.274 | 10.7118 | 10.3423 | 10.4252 | 10.2553 | 10.2488 | 10.2639 | 10.3098 | 10.4463 | 10.8776 | 11.2299 | 11.4641
Zs-Summerleas | Maximum demand forecast(peak season)Power factor (coincident) | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991
Zs-Summerleas | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 12.2802 | 10.7172 | 10.3475 | 10.4305 | 10.2605 | 10.2539 | 10.2691 | 10.315 | 10.4516 | 10.8831 | 11.2355 | 11.4699
Zs-Summerleas | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941 | 0.99941
Zs-Summerleas | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Load transfer capacity (MVA)1 | 4.9 | [11 empty] | Kingston
Zs-Summerleas | Load transfer capacity (MVA)2
Zs-Summerleas | Load transfer capacity (MVA)3
Zs-Summerleas | Load transfer capacity (MVA)4
Zs-Summerleas | Embedded generation capacity (MVA)Units less than 100 kVA | 7.197
Zs-Summerleas | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Zs-Trial Harbour | Sub-transmission lines capacityTotal (winter) | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186
Zs-Trial Harbour | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Sub-transmission lines capacityTotal (summer) | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186
Zs-Trial Harbour | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Maximum demand forecast(peak season)Maximum demand (MVA) | 2.8847 | 9.4592 | 9.1329 | 9.2061 | 9.0561 | 9.0503 | 9.0637 | 9.1042 | 9.2248 | 9.6057 | 9.9167 | 10.1236
Zs-Trial Harbour | Maximum demand forecast(peak season)Power factor (coincident) | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625 | 0.90625
Zs-Trial Harbour | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 2.8931 | 9.4866 | 9.1594 | 9.2328 | 9.0823 | 9.0766 | 9.09 | 9.1306 | 9.2515 | 9.6335 | 9.9454 | 10.1529
Zs-Trial Harbour | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363 | 0.90363
Zs-Trial Harbour | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Load transfer capacity (MVA)1
Zs-Trial Harbour | Load transfer capacity (MVA)2
Zs-Trial Harbour | Load transfer capacity (MVA)3
Zs-Trial Harbour | Load transfer capacity (MVA)4
Zs-Trial Harbour | Embedded generation capacity (MVA)Units less than 100 kVA | 0.809
Zs-Trial Harbour | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-West Hobart | Sub-transmission lines capacityTotal (winter) | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033
Zs-West Hobart | Sub-transmission lines capacityFirm delivery (winter) | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689
Zs-West Hobart | Sub-transmission lines capacityTotal (summer) | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962
Zs-West Hobart | Sub-transmission lines capacityFirm delivery (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-West Hobart | Maximum demand forecast(peak season)Maximum demand (MVA) | 38.0074 | 38.7231 | 37.3874 | 37.6871 | 37.0729 | 37.0493 | 37.104 | 37.2698 | 37.7635 | 39.3227 | 40.596 | 41.4428
Zs-West Hobart | Maximum demand forecast(peak season)Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
Zs-West Hobart | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 38.0074 | 38.7231 | 37.3874 | 37.6871 | 37.0729 | 37.0493 | 37.104 | 37.2698 | 37.7635 | 39.3227 | 40.596 | 41.4428
Zs-West Hobart | Maximum demand forecast(non-peak season)Power factor (coincident) | 1 | 1 | bar: 2025 to 2034
Zs-West Hobart | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-West Hobart | Load transfer capacity (MVA)1
Zs-West Hobart | Load transfer capacity (MVA)2
Zs-West Hobart | Load transfer capacity (MVA)3
Zs-West Hobart | Load transfer capacity (MVA)4
Zs-West Hobart | Embedded generation capacity (MVA)Units less than 100 kVA | 13.843
Zs-West Hobart | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024

## Maximum Demand Forecast
Summer | Actuals |  | Forecast | [11 empty] | Winter | Actuals |  | Forecast | [11 empty] | Hours exceeding 95% maximum demand |  | Substation firm delivery |  |  | Hours exceeding firm capacity |  |  | Load transfer capacity |  |  |  | Substation Total Capacity
Substation | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Power Factor | Diversity Factor | Substation | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Power Factor | Diversity Factor | Substation | Hours | Substation | Firm | Short-term firm | Substation | continuous rating | short-term rating | Substation |  | Load transfer point | MVA | Substation | Total (MVA)
Arthurs Lake (DL) | 0.0392 | 0.3236 | 0.33276 | 0.33174 | 0.32615 | 0.32219 | 0.3224 | 0.32178 | 0.32911 | 0.34893 | 0.36652 | 0.37599 | 0.97444 | 0.05686 | Arthurs Lake (DL) | 0.0212 | 0.0378 | 0.036496 | 0.036789 | 0.036189 | 0.036166 | 0.036219 | 0.036381 | 0.036863 | 0.038385 | 0.039628 | 0.040455 | 0.66721 | 0.44974 | Arthurs Lake (DL) | 1 | Arthurs Lake (DL) | 0 | 0 | Arthurs Lake (DL) | 8768.5 | 8768.5 | Arthurs Lake (DL) | Load transfer capacity (MVA)1 | Waddmana | 0.1 | Arthurs Lake (DL) | 25
Avoca | 9.8198 | 8.2769 | 8.5112 | 8.4851 | 8.3422 | 8.2408 | 8.2463 | 8.2303 | 8.4178 | 8.9249 | 9.3746 | 9.617 | 0.9475 | 0.58769 | Avoca | 6.7863 | 6.6366 | 6.4076 | 6.459 | 6.3537 | 6.3497 | 6.3591 | 6.3875 | 6.4721 | 6.7393 | 6.9575 | 7.1027 | 0.99978 | 0.32578 | Avoca | 0.5 | Avoca | 0 | 0 | Avoca | 8244 | 8244 | Arthurs Lake (DL) | Load transfer capacity (MVA)2 |  |  | Avoca | 17
Bridgewater | 21.8148 | 22.8536 | 23.5005 | 23.4283 | 23.457 | 23.1719 | 23.1874 | 23.1425 | 23.6696 | 25.0956 | 26.3602 | 27.0417 | 0.99986 | 1 | Bridgewater | 37.3301 | 35.704 | 34.4724 | 34.7488 | 34.5845 | 34.5626 | 34.6136 | 34.7683 | 35.2288 | 36.6834 | 37.8712 | 38.6611 | 0.99981 | 0.95489 | Bridgewater | 13.5 | Bridgewater | 35 | 42 | Bridgewater | 617 | 111 | Arthurs Lake (DL) | Load transfer capacity (MVA)3 |  |  | Bridgewater | 70
Burnie | 40.2612 | 40.5222 | 42.8822 | 42.7504 | 42.0303 | 41.5194 | 41.5472 | 41.4668 | 42.4112 | 44.9665 | 47.2323 | 48.4534 | 0.99405 | 0.90257 | Burnie | 63.5022 | 60.651 | 59.6977 | 60.1763 | 59.1955 | 59.1579 | 59.2452 | 59.51 | 60.2982 | 62.7879 | 64.8209 | 66.1731 | 0.99835 | 0.98096 | Burnie | 7 | Burnie | 60 | 72 | Burnie | 1236 | 149.5 | Arthurs Lake (DL) | Load transfer capacity (MVA)4 |  |  | Burnie | 120
Chapel Street | 22.2857 | 20.488 | 21.068 | 21.0032 | 20.6494 | 20.3984 | 20.4121 | 20.3726 | 20.8366 | 22.092 | 23.2052 | 23.8051 | 1 | 1 | Chapel Street | 43.726 | 38.5718 | 37.2413 | 37.5399 | 36.928 | 36.9046 | 36.959 | 37.1242 | 37.6159 | 39.1691 | 40.4374 | 41.2809 | 0.99999 | 0.93981 | Chapel Street | 10 | Chapel Street | 60 | 72 | Chapel Street | 0 | 0 | Arthurs Lake (DL) | Load transfer capacity (MVA)5 |  |  | Chapel Street | 120
Creek Road | 59.3115 | 48.0642 | 49.4248 | 49.2729 | 48.443 | 47.8541 | 47.8861 | 47.7935 | 48.8819 | 51.8271 | 54.4386 | 55.846 | 0.99625 | 0.98172 | Creek Road | 100.1103 | 88.7406 | 85.6795 | 86.3664 | 84.9588 | 84.9048 | 85.03 | 85.4101 | 86.5414 | 90.1146 | 93.0325 | 94.9731 | 0.99089 | 1 | Creek Road | 26 | Creek Road | 120 | 72 | Creek Road | 0 | 1921 | Avoca | Load transfer capacity (MVA)1 | St Marys | 4.6 | Creek Road | 180
Derby | 6.4486 | 6.7457 | 6.9367 | 6.9154 | 6.7989 | 6.7162 | 6.7207 | 6.7077 | 6.8605 | 7.2738 | 7.6404 | 7.8379 | 0.98426 | 0.55412 | Derby | 6.0741 | 2.7947 | 2.6983 | 2.72 | 2.6756 | 2.6739 | 2.6779 | 2.6898 | 2.7255 | 2.838 | 2.9299 | 2.991 | 0.96015 | 0.65718 | Derby | 4 | Derby | 0 | 0 | Derby | 8726.5 | 8726.5 | Avoca | Load transfer capacity (MVA)2 | Palmerston | 4.6 | Derby | 25
Derwent Bridge | 0.30421 | 0.2645 | 0.27199 | 0.27115 | 0.26659 | 0.26335 | 0.26352 | 0.26301 | 0.269 | 0.28521 | 0.29958 | 0.30733 | 0.9894 | 0.54945 | Derwent Bridge | 0.37077 | 0.3416 | 0.32981 | 0.33246 | 0.32704 | 0.32683 | 0.32731 | 0.32878 | 0.33313 | 0.34689 | 0.35812 | 0.36559 | 0.9931 | 0.90392 | Derwent Bridge | 1.5 | Derwent Bridge | 0 | 0 | Derwent Bridge | 8763 | 8763 | Avoca | Load transfer capacity (MVA)3 |  |  | Derwent Bridge | 6
Devonport | 32.906 | 34.3834 | 35.8318 | 36.7263 | 36.1077 | 35.6688 | 35.6927 | 35.6236 | 36.4349 | 38.6301 | 40.5766 | 41.6257 | 0.99235 | 0.856 | Devonport | 54.919 | 52.7679 | 51.3937 | 52.7595 | 51.8996 | 51.8667 | 51.9432 | 52.1753 | 52.8664 | 55.0492 | 56.8317 | 58.0172 | 0.99697 | 0.93495 | Devonport | 4 | Devonport | 60 | 72 | Devonport | 323 | 16.5 | Avoca | Load transfer capacity (MVA)4 |  |  | Devonport | 110
Electrona | 11.3214 | 9.9714 | 10.2537 | 10.2222 | 10.05 | 9.9278 | 9.9345 | 9.9152 | 10.141 | 10.752 | 11.2938 | 11.5858 | 0.997 | 1 | Electrona | 17.2978 | 17.4324 | 16.831 | 16.966 | 16.6894 | 16.6788 | 16.7035 | 16.7781 | 17.0003 | 17.7023 | 18.2755 | 18.6567 | 0.99914 | 0.93363 | Electrona | 14 | Electrona | 25 | 30 | Electrona | 0 | 0 | Avoca | Load transfer capacity (MVA)5 |  |  | Electrona | 50
Emu Bay (RT) | 7.04 | 7.3233 | 7.5306 | 7.5075 | 7.381 | 7.2913 | 7.2962 | 7.282 | 7.4479 | 7.8966 | 8.2945 | 8.509 | 0.96751 | 0.49385 | Emu Bay (RT) | 9.5638 | 9.0796 | 8.7664 | 8.8366 | 8.6926 | 8.6871 | 8.6999 | 8.7388 | 8.8546 | 9.2201 | 9.5187 | 9.7173 | 0.97442 | 0.81405 | Emu Bay (RT) | 11.5 | Emu Bay (RT) | 30 | 30 | Emu Bay (RT) | 0 | 0 | Bridgewater | Load transfer capacity (MVA)1 |  |  | Emu Bay (RT) | 76
George Town | 13.3119 | 11.8566 | 12.5421 | 14.2975 | 14.0567 | 13.8858 | 13.8951 | 13.8682 | 14.1841 | 15.0387 | 15.7965 | 16.2048 | 0.99765 | 0.81511 | George Town | 19.4828 | 20.5861 | 20.2044 | 22.0696 | 21.7099 | 21.6961 | 21.7281 | 21.8252 | 22.1143 | 23.0274 | 23.773 | 24.2689 | 0.99895 | 0.97224 | George Town | 3 | George Town | 48 | 48 | George Town | 0 | 0 | Bridgewater | Load transfer capacity (MVA)2 |  |  | George Town | 96
Hadspen | 34.4226 | 33.5582 | 35.3453 | 35.2367 | 36.0542 | 35.6159 | 35.6398 | 35.5708 | 36.3809 | 38.5728 | 40.5165 | 41.564 | 0.99986 | 0.97117 | Hadspen | 57.2165 | 58.1832 | 56.9622 | 57.4188 | 57.8233 | 57.7866 | 57.8719 | 58.1305 | 58.9005 | 61.3324 | 63.3184 | 64.6392 | 0.99902 | 1 | Hadspen | 4 | Hadspen | 50 | 60 | Hadspen | 1451 | 464 | Bridgewater | Load transfer capacity (MVA)3 |  |  | Hadspen | 100
Huon River | 0.57438 | 0.6402 | 0.65832 | 0.6563 | 0.64524 | 0.6374 | 0.63783 | 0.63659 | 0.65109 | 0.69032 | 0.7251 | 0.74385 | 0.59605 | 0.90316 | Huon River | 0.62104 | 0.62764 | 0.60599 | 0.61085 | 0.60089 | 0.60051 | 0.60139 | 0.60408 | 0.61208 | 0.63736 | 0.65799 | 0.67172 | 0.56163 | 0.83073 | Huon River | 4 | Huon River | 0 | 0 | Huon River | 8747.5 | 8747.5 | Bridgewater | Load transfer capacity (MVA)4 |  |  | Huon River | 25
Kermandie | 6.514 | 6.4872 | 6.6708 | 6.6503 | 6.5383 | 7.1803 | 7.1851 | 7.1712 | 7.3345 | 7.7764 | 8.1683 | 8.3795 | 0.97121 | 0.96803 | Kermandie | 9.0397 | 8.6602 | 8.3614 | 8.4285 | 8.2911 | 8.9792 | 8.9924 | 9.0326 | 9.1522 | 9.5301 | 9.8387 | 10.0439 | 0.98708 | 0.92768 | Kermandie | 11 | Kermandie | 25 | 37.5 | Kermandie | 0 | 0 | Bridgewater | Load transfer capacity (MVA)5 |  |  | Kermandie | 50
Kingston 11kV | 17.7941 | 15.6232 | 16.0655 | 16.6516 | 16.3711 | 16.1721 | 16.1829 | 16.1516 | 16.5195 | 17.5148 | 18.3973 | 18.8729 | 0.99885 | 1 | Kingston 11kV | 29.9108 | 26.6514 | 25.732 | 26.5417 | 26.1091 | 26.0925 | 26.131 | 26.2478 | 26.5954 | 27.6935 | 28.5902 | 29.1866 | 1 | 0.88817 | Kingston 11kV | 14.5 | Kingston 11kV | 35 | 42 | Kingston 11kV | 8.5 | 0 | Burnie | Load transfer capacity (MVA)1 | Port Latta | 8.8 | Kingston 11kV | 70
Kingston 33kV | 6.8357 | 6.3554 | 6.5353 | 6.5152 | 6.4055 | 6.3276 | 6.3319 | 6.3196 | 6.4635 | 6.853 | 7.1983 | 7.3844 | 1 | 1 | Kingston 33kV | 12.0349 | 10.7332 | 10.363 | 10.446 | 10.2758 | 10.2693 | 10.2844 | 10.3304 | 10.4672 | 10.8994 | 11.2523 | 11.487 | 0.99609 | 1 | Kingston 33kV | 17.5 | Kingston 33kV | 60 | 72 | Kingston 33kV | 0 | 0 | Burnie | Load transfer capacity (MVA)2 | Ulverstone | 8.8 | Kingston 33kV | 120
Knights Road | 15.079 | 14.8288 | 15.2486 | 15.2017 | 14.9457 | 17.5517 | 17.5635 | 17.5295 | 17.9287 | 19.0089 | 19.9668 | 20.483 | 0.97775 | 0.98793 | Knights Road | 20.908 | 20.1729 | 19.477 | 19.6332 | 19.3132 | 21.9799 | 22.0123 | 22.1107 | 22.4036 | 23.3286 | 24.084 | 24.5863 | 0.98922 | 0.93681 | Knights Road | 9 | Knights Road | 20 | 24 | Knights Road | 1492.5 | 261.5 | Burnie | Load transfer capacity (MVA)3 |  |  | Knights Road | 40
Lindisfarne | 23.6179 | 21.9786 | 22.6008 | 24.2536 | 23.845 | 23.5552 | 23.5709 | 23.5253 | 24.0611 | 25.5108 | 26.7962 | 27.489 | 1 | 1 | Lindisfarne | 38.0913 | 36.8108 | 35.541 | 37.461 | 36.8504 | 36.827 | 36.8813 | 37.0462 | 37.5369 | 39.0867 | 40.3523 | 41.1941 | 0.99787 | 1 | Lindisfarne | 9.5 | Lindisfarne | 60 | 78 | Lindisfarne | 0 | 0 | Burnie | Load transfer capacity (MVA)4 |  |  | Lindisfarne | 120
Meadowbank | 7.7741 | 7.8437 | 8.0658 | 8.041 | 7.9055 | 7.8095 | 7.8147 | 7.7996 | 7.9772 | 8.4578 | 8.884 | 9.1137 | 0.94207 | 0.8769 | Meadowbank | 5.4732 | 5.3121 | 5.1288 | 5.17 | 5.0857 | 5.0825 | 5.09 | 5.1127 | 5.1804 | 5.3943 | 5.569 | 5.6852 | 0.99973 | 0.55344 | Meadowbank | 5 | Meadowbank | 0 | 0 | Meadowbank | 8662.5 | 8662.5 | Burnie | Load transfer capacity (MVA)5 |  |  | Meadowbank | 25
Mornington | 26.732 | 24.9044 | 25.6094 | 25.5307 | 25.1006 | 24.7955 | 24.8121 | 24.7641 | 25.3281 | 26.8541 | 28.2073 | 28.9365 | 0.99964 | 1 | Mornington | 44.5185 | 44.523 | 42.9872 | 43.3318 | 42.6256 | 42.5985 | 42.6613 | 42.852 | 43.4196 | 45.2124 | 46.6763 | 47.65 | 0.99854 | 0.94962 | Mornington | 87.5 | Mornington | 60 | 72 | Mornington | 0 | 0 | Chapel Street | Load transfer capacity (MVA)1 |  |  | Mornington | 120
Mowbray | 20.4463 | 19.378 | 20.4664 | 20.4035 | 20.0598 | 19.816 | 19.8293 | 19.7909 | 20.2416 | 21.4612 | 22.5426 | 23.1254 | 0.99598 | 0.82864 | Mowbray | 36.9918 | 38.8339 | 38.0012 | 38.3059 | 37.6815 | 37.6576 | 37.7131 | 37.8817 | 38.3835 | 39.9683 | 41.2625 | 42.1232 | 0.9944 | 0.99928 | Mowbray | 1.5 | Mowbray | 50 | 60 | Mowbray | 15.5 | 0 | Chapel Street | Load transfer capacity (MVA)2 |  |  | Mowbray | 100
New Norfolk | 12.6495 | 12.2682 | 12.6155 | 12.5767 | 12.3649 | 12.2146 | 12.2227 | 12.1991 | 12.4769 | 13.2287 | 13.8952 | 14.2545 | 0.99581 | 0.99575 | New Norfolk | 19.3862 | 17.2812 | 16.6851 | 16.8188 | 16.5447 | 16.5342 | 16.5586 | 16.6326 | 16.8529 | 17.5488 | 18.117 | 18.4949 | 0.99999 | 0.9027 | New Norfolk | 19 | New Norfolk | 30 | 37 | New Norfolk | 0 | 0 | Chapel Street | Load transfer capacity (MVA)3 |  |  | New Norfolk | 60
Newton | 4.0509 | 3.6772 | 3.7813 | 3.7697 | 3.7062 | 3.6611 | 3.6636 | 3.6565 | 3.7398 | 3.9651 | 4.1649 | 4.2725 | 0.99726 | 0.85116 | Newton | 4.1194 | 3.9208 | 3.7856 | 3.8159 | 3.7537 | 3.7513 | 3.7569 | 3.7736 | 3.8236 | 3.9815 | 4.1104 | 4.1962 | 0.99991 | 0.88727 | Newton | 1.5 | Newton | 0 | 0 | Newton | 8779.5 | 8779.5 | Chapel Street | Load transfer capacity (MVA)4 |  |  | Newton | 22.5
North Hobart | 23.0692 | 19.6842 | 20.2414 | 20.1792 | 19.8393 | 19.5982 | 19.6113 | 19.5733 | 20.0191 | 21.2252 | 22.2948 | 22.8712 | 0.99698 | 0.94552 | North Hobart | 37.008 | 34.9903 | 33.7833 | 34.0542 | 33.4991 | 33.4779 | 33.5273 | 33.6771 | 34.1232 | 35.5321 | 36.6826 | 37.4478 | 0.99771 | 0.95665 | North Hobart | 2.5 | North Hobart | 45 | 50 | North Hobart | 35.5 | 0 | Chapel Street | Load transfer capacity (MVA)5 |  |  | North Hobart | 90
Norwood | 17.1243 | 15.9288 | 16.3797 | 16.3294 | 16.0543 | 15.8592 | 15.8698 | 15.8391 | 16.1998 | 17.1758 | 18.0413 | 18.5077 | 0.99997 | 0.94293 | Norwood | 29.8043 | 29.8795 | 28.8489 | 29.0801 | 28.6062 | 28.588 | 28.6302 | 28.7581 | 29.139 | 30.3422 | 31.3247 | 31.9781 | 0.99986 | 0.96266 | Norwood | 25.5 | Norwood | 50 | 60 | Norwood | 0 | 0 | Creek Road | Load transfer capacity (MVA)1 |  |  | Norwood | 100
Palmerston | 11.885 | 13.52 | 15.7023 | 15.654 | 17.9302 | 17.7122 | 17.7241 | 17.6898 | 18.0927 | 19.1827 | 20.1493 | 20.6703 | 0.95577 | 0.86399 | Palmerston | 9.5356 | 7.1212 | 8.5652 | 8.6339 | 10.9057 | 10.8988 | 10.9149 | 10.9637 | 11.1089 | 11.5676 | 11.9421 | 12.1912 | 0.99542 | 0.67138 | Palmerston | 16 | Palmerston | 25 | 30 | Palmerston | 0 | 0 | Creek Road | Load transfer capacity (MVA)2 |  |  | Palmerston | 50
Port Latta (RT) | 10.8116 | 10.7522 | 11.0566 | 11.0226 | 10.8369 | 10.7052 | 10.7124 | 10.6916 | 10.9351 | 11.594 | 12.1782 | 12.493 | 0.94388 | 0.69595 | Port Latta (RT) | 7.119 | 7.1438 | 6.8973 | 6.9526 | 6.8393 | 6.835 | 6.8451 | 6.8757 | 6.9667 | 7.2544 | 7.4893 | 7.6455 | 0.99897 | 0.96774 | Port Latta (RT) | 3.5 | Port Latta (RT) | 25 | 37.5 | Port Latta (RT) | 0 | 0 | Creek Road | Load transfer capacity (MVA)3 |  |  | Port Latta (RT) | 50
Queenstown | 4.8696 | 3.9578 | 4.0698 | 4.0573 | 3.989 | 3.9405 | 3.9431 | 3.9355 | 4.0251 | 4.2676 | 4.4827 | 4.5986 | 0.99987 | 0.76131 | Queenstown | 6.3509 | 5.8481 | 5.6464 | 5.6917 | 5.5989 | 5.5953 | 5.6036 | 5.6286 | 5.7032 | 5.9387 | 6.131 | 6.2588 | 0.99994 | 0.8968 | Queenstown | 22.5 | Queenstown | 25 | 30 | Queenstown | 0 | 0 | Creek Road | Load transfer capacity (MVA)4 |  |  | Queenstown | 50
Railton | 43.2732 | 45.6495 | 47.1506 | 47.3042 | 46.5074 | 45.9421 | 45.9728 | 45.8838 | 46.9288 | 49.7563 | 52.2634 | 53.6146 | 0.94401 | 0.95827 | Railton | 48.657 | 46.2263 | 44.8277 | 45.4705 | 44.7294 | 44.701 | 44.7669 | 44.967 | 45.5626 | 47.4439 | 48.9801 | 50.0018 | 0.98001 | 0.8359 | Railton | 11.5 | Railton | 50 | 60 | Railton | 3424.5 | 868 | Creek Road | Load transfer capacity (MVA)5 |  |  | Railton | 100
Risdon 33kV | 47.7681 | 46.4472 | 47.762 | 47.8822 | 48.7542 | 48.5881 | 48.6206 | 48.5266 | 49.6317 | 52.622 | 55.2736 | 56.7026 | 0.97262 | 0.81236 | Risdon 33kV | 70.4271 | 67.4446 | 65.1181 | 65.8936 | 66.4141 | 66.7818 | 66.8803 | 67.1792 | 68.069 | 70.8795 | 73.1746 | 74.701 | 0.98264 | 0.93134 | Risdon 33kV | 188 | Risdon 33kV | 100 | 60 | Risdon 33kV | 0 | 1251 | Derby | Load transfer capacity (MVA)1 | Scottsdale | 5.3 | Risdon 33kV | 150
Rokeby | 15.9404 | 15.0826 | 16.3517 | 16.3015 | 16.5123 | 16.3116 | 16.3225 | 16.2909 | 16.6619 | 17.6658 | 18.556 | 19.0357 | 0.99956 | 1 | Rokeby | 26.6898 | 26.3704 | 26.2515 | 26.462 | 26.4918 | 26.4749 | 26.514 | 26.6325 | 26.9853 | 28.0995 | 29.0093 | 29.6144 | 0.99999 | 0.94399 | Rokeby | 24.5 | Rokeby | 35 | 42 | Rokeby | 0 | 0 | Derby | Load transfer capacity (MVA)2 |  |  | Rokeby | 70
Rosebery 22kV | 1.9886 | 2.5424 | 2.6144 | 2.6064 | 2.5625 | 2.5313 | 2.533 | 2.5281 | 2.5857 | 2.7415 | 2.8796 | 2.9541 | 0.98967 | 0.28607 | Rosebery 22kV | 2.4198 | 2.7883 | 2.6921 | 2.7137 | 2.6695 | 2.6678 | 2.6717 | 2.6837 | 2.7192 | 2.8315 | 2.9232 | 2.9842 | 0.97591 | 0.11432 | Rosebery 22kV | 3 | Rosebery 22kV | 10 | 10 | Rosebery 22kV |  |  | Derby | Load transfer capacity (MVA)3 |  |  | Rosebery 22kV | 16
Rosebery 44kV | 22.2736 | 20.6717 | 21.2569 | 21.1915 | 20.8346 | 20.5813 | 20.5951 | 20.5552 | 21.0234 | 22.29 | 23.4132 | 24.0185 | 0.90631 | 0.99645 | Rosebery 44kV | 18.5561 | 23.3306 | 22.5258 | 22.7064 | 22.3363 | 22.3221 | 22.3551 | 22.455 | 22.7524 | 23.6918 | 24.459 | 24.9692 | 0.94726 | 0.94468 | Rosebery 44kV | 320 | Rosebery 44kV | 66 | 72 | Rosebery 44kV | 0 | 0 | Derby | Load transfer capacity (MVA)4 |  |  | Rosebery 44kV | 102
Savage River DL | 0.92476 | 0.95468 | 0.9817 | 0.97868 | 0.9622 | 0.9505 | 0.95114 | 0.9493 | 0.97092 | 1.0294 | 1.0813 | 1.1092 | 0.9979 | 0.46946 | Savage River DL | 1.2171 | 1.5583 | 1.5046 | 1.5166 | 1.4919 | 1.491 | 1.4932 | 1.4998 | 1.5197 | 1.5825 | 1.6337 | 1.6678 | 0.99964 | 0.66681 | Savage River DL | 5.5 | Savage River DL | 22.5 | 27 | Savage River DL | 0 | 0 | Derby | Load transfer capacity (MVA)5 |  |  | Savage River DL | 45
Scottsdale | 11.0298 | 10.547 | 10.8456 | 10.8122 | 10.6301 | 10.5009 | 10.5079 | 10.4876 | 10.7264 | 11.3727 | 11.9458 | 12.2546 | 0.98819 | 0.89771 | Scottsdale | 12.7525 | 13.2834 | 12.8252 | 12.928 | 12.7173 | 12.7092 | 12.728 | 12.7848 | 12.9542 | 13.4891 | 13.9258 | 14.2163 | 0.99964 | 0.96517 | Scottsdale | 8.5 | Scottsdale | 31.5 | 36 | Scottsdale | 0 | 0 | Derwent Bridge | Load transfer capacity (MVA)1 |  |  | Scottsdale | 63
Sheffield | 1.6022 | 4.3938 | 4.5182 | 4.5043 | 4.4284 | 4.3746 | 4.3775 | 4.3691 | 4.4686 | 4.7378 | 4.9765 | 5.1052 | 0.99303 | 0 | Sheffield | 2.0662 | 2.1805 | 2.1053 | 2.1222 | 2.0876 | 2.0863 | 2.0893 | 2.0987 | 2.1265 | 2.2143 | 2.286 | 2.3336 | 0.99598 | 0.84738 | Sheffield | 2 | Sheffield | 0 | 0 | Sheffield | 0 | 0 | Derwent Bridge | Load transfer capacity (MVA)2 |  |  | Sheffield | 25
Smithton | 22.2253 | 22.3956 | 23.0295 | 22.9587 | 22.572 | 22.2977 | 22.3126 | 22.2694 | 22.7766 | 24.1489 | 25.3657 | 26.0215 | 0.94285 | 0.96081 | Smithton | 22.4298 | 22.1401 | 21.3764 | 21.5478 | 21.1966 | 21.1831 | 21.2144 | 21.3092 | 21.5914 | 22.4829 | 23.2109 | 23.6951 | 0.98096 | 0.9839 | Smithton | 0.5 | Smithton | 35 | 42 | Smithton | 8784 | 8784 | Derwent Bridge | Load transfer capacity (MVA)3 |  |  | Smithton | 70
Sorell | 24.5727 | 24.8378 | 25.5409 | 25.4624 | 25.0335 | 24.7292 | 24.7458 | 24.6979 | 25.2604 | 26.7823 | 28.1318 | 28.8591 | 1 | 1 | Sorell | 37.4014 | 34.421 | 33.2336 | 33.5 | 32.954 | 32.9331 | 32.9817 | 33.1291 | 33.5679 | 34.9539 | 36.0857 | 36.8384 | 1 | 0.91948 | Sorell | 4 | Sorell | 60 | 78 | Sorell | 632 | 88.5 | Derwent Bridge | Load transfer capacity (MVA)4 |  |  | Sorell | 120
St Leonards | 15.2697 | 12.951 | 13.3176 | 13.2767 | 13.0531 | 12.8944 | 12.903 | 12.878 | 13.1713 | 13.9649 | 14.6686 | 15.0478 | 0.9976 | 0.96618 | St Leonards | 30.9241 | 32.1515 | 31.0424 | 31.2913 | 30.7813 | 30.7618 | 30.8071 | 30.9448 | 31.3547 | 32.6493 | 33.7065 | 34.4096 | 0.9998 | 0.93578 | St Leonards | 2 | St Leonards | 60 | 78 | St Leonards | 0 | 0 | Derwent Bridge | Load transfer capacity (MVA)5 |  |  | St Leonards | 120
St Marys | 11.7755 | 10.3494 | 10.6424 | 10.6097 | 10.431 | 10.3042 | 10.3111 | 10.2911 | 10.5255 | 11.1596 | 11.722 | 12.025 | 1 | 0.78517 | St Marys | 16.994 | 15.0283 | 14.5099 | 14.6262 | 14.3878 | 14.3787 | 14.3999 | 14.4643 | 14.6558 | 15.261 | 15.7551 | 16.0838 | 0.99922 | 0.98604 | St Marys | 2 | St Marys | 10 | 12 | St Marys | 0 | 0 | Devonport | Load transfer capacity (MVA)1 | Railton | 5.1 | St Marys | 20
Trevallyn | 39.3906 | 38.1556 | 39.2357 | 39.4703 | 39.6521 | 39.1701 | 39.1963 | 39.1205 | 40.0114 | 42.4221 | 44.5597 | 45.7117 | 0.99994 | 0.95391 | Trevallyn | 71.9031 | 70.8771 | 68.4322 | 69.318 | 68.9925 | 68.9487 | 69.0504 | 69.359 | 70.2777 | 73.1794 | 75.5489 | 77.1248 | 0.9998 | 0.99922 | Trevallyn | 2 | Trevallyn | 100 | 130 | Trevallyn | 8783.5 | 8767 | Devonport | Load transfer capacity (MVA)2 | Ulverstone | 6.3 | Trevallyn | 150
Triabunna (RT) | 5.7627 | 5.2284 | 5.3764 | 5.3599 | 5.2696 | 5.2055 | 5.209 | 5.1989 | 5.3174 | 5.6377 | 5.9218 | 6.0749 | 0.99961 | 0.9129 | Triabunna (RT) | 6.7857 | 7.1021 | 6.8571 | 6.9121 | 6.7994 | 6.7951 | 6.8051 | 6.8355 | 6.9261 | 7.2121 | 7.4456 | 7.6009 | 0.99846 | 0.87448 | Triabunna (RT) | 12 | Triabunna (RT) | 25 | 30 | Triabunna (RT) | 0 | 0 | Devonport | Load transfer capacity (MVA)3 |  |  | Triabunna (RT) | 50
Tungatinah | 0.85487 | 0.6236 | 0.64125 | 0.63928 | 0.62851 | 0.62087 | 0.62129 | 0.62009 | 0.63421 | 0.67242 | 0.7063 | 0.72456 | 0.99884 | 0.59686 | Tungatinah | 1.1416 | 1.0412 | 1.0053 | 1.0133 | 0.99681 | 0.99618 | 0.99765 | 1.0021 | 1.0154 | 1.0573 | 1.0915 | 1.1143 | 0.99846 | 0.75049 | Tungatinah | 8 | Tungatinah | 0 | 0 | Tungatinah | 0 | 0 | Devonport | Load transfer capacity (MVA)4 |  |  | Tungatinah | 13
Ulverstone | 20.5622 | 21.8366 | 22.4548 | 22.3857 | 22.0087 | 21.7412 | 21.7557 | 21.7136 | 22.2081 | 23.5461 | 24.7326 | 25.372 | 0.99451 | 0.72803 | Ulverstone | 32.8095 | 28.5973 | 27.6108 | 27.8322 | 27.3786 | 27.3612 | 27.4015 | 27.524 | 27.8886 | 29.0401 | 29.9804 | 30.6058 | 0.99998 | 1 | Ulverstone | 5 | Ulverstone | 45 | 54 | Ulverstone | 8784 | 8784 | Devonport | Load transfer capacity (MVA)5 |  |  | Ulverstone | 90
Waddamana | 0.446 | 0.493 | 0.50696 | 0.5054 | 0.49688 | 0.49085 | 0.49117 | 0.49022 | 0.50139 | 0.5316 | 0.55838 | 0.57282 | 0.96848 | 0.53712 | Waddamana | 0.68766 | 0.697 | 0.67296 | 0.67835 | 0.6673 | 0.66687 | 0.66786 | 0.67084 | 0.67973 | 0.70779 | 0.73071 | 0.74595 | 0.99899 | 0.45079 | Waddamana | 2 | Waddamana | 0 | 0 | Waddamana | 0 | 0 | Electrona | Load transfer capacity (MVA)1 | Kingston | 8 | Waddamana | 4
Wesley Vale | 7.8975 | 8.1276 | 8.3577 | 8.332 | 8.1916 | 8.0921 | 8.0975 | 8.0818 | 8.2659 | 8.7639 | 9.2055 | 9.4435 | 0.99569 | 0.75764 | Wesley Vale | 11.6091 | 18.6033 | 17.9616 | 18.1056 | 17.8105 | 17.7992 | 17.8254 | 17.9051 | 18.1423 | 18.8914 | 19.5031 | 19.9099 | 0.9997 | 0.99276 | Wesley Vale | 1.5 | Wesley Vale | 25 | 28 | Wesley Vale | 0 | 0 | Electrona | Load transfer capacity (MVA)2 | Knights Road | 3 | Wesley Vale | 50
[38 empty] | Electrona | Load transfer capacity (MVA)3
Zs-Bellerive | 9.1216 | 6.0707 | 6.2426 | 6.2234 | 6.1186 | 6.0442 | 6.0482 | 6.0365 | 6.174 | 6.546 | 6.8758 | 7.0536 | 0.99999 | 0 | Zs-Bellerive | 11.3972 | 9.912 | 9.5701 | 9.6468 | 9.4896 | 9.4836 | 9.4976 | 9.54 | 9.6664 | 10.0655 | 10.3914 | 10.6082 | 0.99999 | 0 | Zs-Bellerive | 0 | Zs-Bellerive | 22.5 | 22.9 |  |  |  | Electrona | Load transfer capacity (MVA)4 |  |  | Zs-Bellerive | 45 | Zone | Summer | Winter | Summer firm | Winter firm
Zs-Cambridge | 12.2085 | 10.4219 | 10.717 | 12.4063 | 12.1973 | 12.049 | 12.0571 | 12.0338 | 12.3078 | 13.0494 | 13.7069 | 14.0613 | 0.99996 | 0 | Zs-Cambridge | 16.2415 | 15.3712 | 14.841 | 16.595 | 16.3245 | 16.3142 | 16.3382 | 16.4113 | 16.6286 | 17.3152 | 17.8759 | 18.2488 | 0.99994 | 0 | Zs-Cambridge | 0 | Zs-Cambridge | 20 | 26 |  |  |  | Electrona | Load transfer capacity (MVA)5 |  |  | Zs-Cambridge | 40 | Zs-Bellerive | 27.2071 | 42.8683 | 13.6035 | 21.4341
Zs-Claremont | 14.5936 | 14.772 | 15.1901 | 15.1435 | 14.8884 | 14.7074 | 14.7172 | 14.6888 | 15.0233 | 15.9284 | 16.7311 | 17.1636 | 0.99914 | 0 | Zs-Claremont | 23.5098 | 22.0944 | 21.3322 | 21.5032 | 21.1528 | 21.1393 | 21.1705 | 21.2651 | 21.5468 | 22.4365 | 23.1629 | 23.6461 | 0.99962 | 0 | Zs-Claremont | 0 | Zs-Claremont | 22.5 | 30 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)1 |  |  | Zs-Claremont | 50 | Zs-Cambridge | 17.7189 | 17.7189 | 0 | 0
Zs-Derwent Park | 14.4354 | 11.3408 | 11.6618 | 11.626 | 11.4302 | 11.2912 | 11.2988 | 11.2769 | 11.5337 | 12.2286 | 12.8448 | 13.1769 | 0.9739 | 0 | Zs-Derwent Park | 19.9187 | 18.4909 | 17.853 | 17.9962 | 17.7028 | 17.6916 | 17.7177 | 17.7969 | 18.0326 | 18.7772 | 19.3852 | 19.7895 | 0.98891 | 0 | Zs-Derwent Park | 0 | Zs-Derwent Park | 22.5 | 22.9 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)2 |  |  | Zs-Derwent Park | 45 | Zs-Claremont | 27.0356 | 44.0686 | 13.4321 | 21.4341
Zs-East Hobart | 23.6183 | 25.0463 | 25.7554 | 25.6762 | 26.9223 | 27.0216 | 27.0396 | 26.9873 | 27.6019 | 29.2649 | 30.7396 | 31.5343 | 0.97088 | 0 | Zs-East Hobart | 28.7118 | 27.6464 | 26.6927 | 26.9067 | 28.0626 | 28.4547 | 28.4967 | 28.624 | 29.0032 | 30.2007 | 31.1786 | 31.829 | 0.98397 | 0 | Zs-East Hobart | 0 | Zs-East Hobart | 60 | 78 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)3 |  |  | Zs-East Hobart | 90 | Zs-Derwent Park | 26.8641 | 40.8666 | 13.4321 | 19.4325
Zs-Geilston Bay | 13.5375 | 10.5747 | 10.8741 | 10.8406 | 10.658 | 10.5285 | 10.5355 | 10.5151 | 10.7546 | 11.4026 | 11.9771 | 12.2868 | 0.99997 | 0 | Zs-Geilston Bay | 19.812 | 18.3665 | 17.733 | 17.8751 | 17.5838 | 17.5726 | 17.5986 | 17.6772 | 17.9114 | 18.6509 | 19.2548 | 19.6565 | 0.99967 | 0 | Zs-Geilston Bay | 0 | Zs-Geilston Bay | 22.5 | 22.9 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)4 |  |  | Zs-Geilston Bay | 45 | Zs-East Hobart | 42.7196 | 42.7196 | 42.7054 | 42.7054
Zs-Howrah | 14.5936 | 11.2091 | 11.5265 | 11.491 | 11.2975 | 11.1601 | 11.1676 | 11.146 | 11.3998 | 12.0867 | 12.6957 | 13.0239 | 0.99733 | 0 | Zs-Howrah | 23.5098 | 18.2951 | 17.664 | 17.8056 | 17.5154 | 17.5043 | 17.5301 | 17.6084 | 17.8417 | 18.5783 | 19.1799 | 19.58 | 0.99897 | 0 | Zs-Howrah | 0 | Zs-Howrah | 25 | 32.5 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)5 |  |  | Zs-Howrah | 50 | Zs-Geilston Bay | 27.0356 | 42.8683 | 13.4321 | 21.4341
Zs-New Town | 14.5666 | 12.17 | 12.5145 | 12.743 | 12.5283 | 12.3761 | 12.3843 | 12.3604 | 12.6419 | 13.4035 | 14.0789 | 14.4429 | 0.9966 | 0 | Zs-New Town | 22.8807 | 21.1789 | 20.4483 | 20.8657 | 20.5256 | 20.5126 | 20.5429 | 20.6347 | 20.908 | 21.7713 | 22.4762 | 22.9451 | 0.99662 | 0 | Zs-New Town | 0 | Zs-New Town | 22.5 | 22.9 |  |  |  | George Town | Load transfer capacity (MVA)1 | Scottsdale | 2.1 | Zs-New Town | 45 | Zs-Howrah | 48.0124 | 48.0124 | 24.0062 | 24.0062
Zs-Rosny Park | 10.4463 | 9.145 | 9.4038 | 9.3749 | 9.217 | 9.105 | 9.1111 | 9.0935 | 9.3006 | 9.8609 | 10.3578 | 10.6256 | 0.99979 | 0 | Zs-Rosny Park | 15.7937 | 15.116 | 14.5945 | 14.7115 | 14.4718 | 14.4626 | 14.4839 | 14.5487 | 14.7414 | 15.35 | 15.847 | 16.1776 | 0.99919 | 0 | Zs-Rosny Park | 0 | Zs-Rosny Park | 0 | 0 |  |  |  | George Town | Load transfer capacity (MVA)2 | Trevallyn | 2.1 | Zs-Rosny Park | 25 | Zs-New Town | 34.8662 | 44.0686 | 13.4321 | 21.4341
Zs-Sandy Bay | 28.1627 | 16.6946 | 17.1672 | 17.1144 | 16.8262 | 16.6216 | 16.6328 | 16.6006 | 16.9786 | 18.0016 | 18.9087 | 19.3975 | 1 | 0 | Zs-Sandy Bay | 38.6838 | 34.7027 | 33.5056 | 33.7742 | 33.2238 | 33.2027 | 33.2516 | 33.4003 | 33.8427 | 35.24 | 36.3811 | 37.14 | 0.99986 | 0 | Zs-Sandy Bay | 0 | Zs-Sandy Bay | 60 | 78 |  |  |  | George Town | Load transfer capacity (MVA)3 | Mowbray | 2.1 | Zs-Sandy Bay | 90 | Zs-Rosny Park | 20.6911 | 20.6911 | 0 | 0
Zs-Summerleas | 6.9772 | 6.3351 | 6.5144 | 6.4944 | 6.385 | 6.3074 | 6.3116 | 6.2994 | 6.4429 | 6.8311 | 7.1753 | 7.3608 | 0.99941 | 0 | Zs-Summerleas | 12.2729 | 10.7108 | 10.3414 | 10.4243 | 10.2544 | 10.2479 | 10.263 | 10.3089 | 10.4454 | 10.8767 | 11.2289 | 11.4631 | 0.99991 | 0 | Zs-Summerleas | 0 | Zs-Summerleas | 0 | 0 |  |  |  | George Town | Load transfer capacity (MVA)4 |  |  | Zs-Summerleas | 25 | Zs-Sandy Bay | 26.8641 | 44.0686 | 13.4321 | 21.4341
Zs-Trial Harbour | 6.9736 | 7.2851 | 7.4914 | 7.4683 | 7.3425 | 7.2533 | 7.2581 | 7.2441 | 7.4091 | 7.8555 | 8.2513 | 8.4646 | 0.90363 | 0 | Zs-Trial Harbour | 2.6143 | 8.5724 | 8.2767 | 8.3431 | 8.2071 | 8.2019 | 8.214 | 8.2507 | 8.36 | 8.7051 | 8.987 | 9.1745 | 0.90625 | 0 | Zs-Trial Harbour | 0 | Zs-Trial Harbour | 20 | 26 |  |  |  | George Town | Load transfer capacity (MVA)5 |  |  | Zs-Trial Harbour | 40 | Zs-Summerleas | 25.8353 | 25.8353 | 0 | 0
Zs-West Hobart | 25.4613 | 18.0818 | 18.5936 | 18.5365 | 18.2242 | 18.0027 | 18.0148 | 17.9799 | 18.3894 | 19.4973 | 20.4798 | 21.0093 | 1 | 0 | Zs-West Hobart | 38.0074 | 38.7231 | 37.3874 | 37.6871 | 37.0729 | 37.0493 | 37.104 | 37.2698 | 37.7635 | 39.3227 | 40.596 | 41.4428 | 1 | 0 | Zs-West Hobart | 0 | Zs-West Hobart | 60 | 78 |  |  |  | Gordon | Load transfer capacity (MVA)1 |  |  | Zs-West Hobart | 90 | Zs-Trial Harbour | 18.186 | 18.186 | 0 | 0
[38 empty] | Gordon | Load transfer capacity (MVA)2 |  |  |  |  | Zs-West Hobart | 40.2962 | 67.9033 | 26.8641 | 45.2689
Summer | Actuals |  | Forecast | [11 empty] | Winter | Actuals |  | Forecast | [19 empty] | Gordon | Load transfer capacity (MVA)3
Feeder | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 |  |  | Feeder | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | [10 empty] | Gordon | Load transfer capacity (MVA)4
10001 | 144.6955 | 103.9944 | 106.9383 | 106.6097 | 104.8139 | 103.5399 | 103.6091 | 103.4087 | 105.7637 | 112.136 | 117.7864 | 120.8316 |  |  | 10001 | 221.4583 | 226.8577 | 219.0323 | 220.7882 | 217.1897 | 217.0518 | 217.3719 | 218.3435 | 221.2355 | 230.3701 | 237.8296 | 242.7906 | [10 empty] | Gordon | Load transfer capacity (MVA)5
10002 | 144.0649 | 118.4944 | 121.8488 | 121.4743 | 119.4282 | 117.9765 | 118.0554 | 117.827 | 120.5104 | 127.7711 | 134.2094 | 137.6792 |  |  | 10002 | 218.11 | 225.0107 | 217.249 | 218.9907 | 215.4214 | 215.2847 | 215.6022 | 216.5658 | 219.4343 | 228.4946 | 235.8932 | 240.8139 | [10 empty] | Hadspen | Load transfer capacity (MVA)1 | Trevallyn | 26.7
10003 | 148.1841 | 109.6102 | 112.7131 | 112.3666 | 110.4739 | 109.1311 | 109.2041 | 108.9928 | 111.475 | 118.1914 | 124.1469 | 127.3565 |  |  | 10003 | 223.4236 | 227.5156 | 219.6675 | 221.4285 | 217.8195 | 217.6812 | 218.0023 | 218.9767 | 221.8771 | 231.0382 | 238.5193 | 243.4947 | [10 empty] | Hadspen | Load transfer capacity (MVA)2 | Norwood | 13.4
10007 | 127.3392 | 174.5833 | 179.5255 | 178.9737 | 175.9591 | 173.8202 | 173.9364 | 173.5999 | 177.5535 | 188.2511 | 197.7369 | 202.8491 |  |  | 10007 | 208.8296 | 196.9122 | 190.1197 | 191.6439 | 188.5203 | 188.4007 | 188.6785 | 189.5218 | 192.0321 | 199.961 | 206.4357 | 210.7419 | [10 empty] | Hadspen | Load transfer capacity (MVA)3 | Palmerston | 5.3
10008 | 111.9256 | 113.3778 | 116.5873 | 116.229 | 114.2712 | 112.8822 | 112.9577 | 112.7391 | 115.3067 | 122.2539 | 128.4142 | 131.7341 |  |  | 10008 | 233.0331 | 200.6655 | 193.7436 | 195.2968 | 192.1137 | 191.9918 | 192.275 | 193.1343 | 195.6925 | 203.7724 | 210.3706 | 214.7589 | [10 empty] | Hadspen | Load transfer capacity (MVA)4
10022 | 171.1878 | 111.4444 | 114.5992 | 114.247 | 112.3226 | 110.9573 | 111.0315 | 110.8167 | 113.3405 | 120.1692 | 126.2244 | 129.4877 |  |  | 10022 | 223.0988 | 197.4835 | 190.6714 | 192.1999 | 189.0674 | 188.9473 | 189.226 | 190.0718 | 192.5893 | 200.5412 | 207.0347 | 211.3534 | [10 empty] | Hadspen | Load transfer capacity (MVA)5
10024 | 173.6397 | 113.2667 | 116.473 | 116.1151 | 114.1592 | 112.7716 | 112.847 | 112.6287 | 115.1937 | 122.1341 | 128.2883 | 131.605 |  |  | 10024 | 230.0957 | 200.4735 | 193.5582 | 195.11 | 191.9299 | 191.8081 | 192.091 | 192.9496 | 195.5053 | 203.5775 | 210.1693 | 214.5534 | [10 empty] | Huon River | Load transfer capacity (MVA)1
10026 | 121.315 | 122.35 | 125.8135 | 125.4268 | 123.3141 | 121.8152 | 121.8966 | 121.6608 | 124.4315 | 131.9285 | 138.5763 | 142.159 |  |  | 10026 | 197.2417 | 186.0457 | 179.6281 | 181.0682 | 178.117 | 178.0039 | 178.2665 | 179.0632 | 181.435 | 188.9263 | 195.0437 | 199.1123 | [10 empty] | Huon River | Load transfer capacity (MVA)2
11004 | 137.2486 | 147.0825 | 151.2461 | 150.7813 | 148.2415 | 146.4396 | 146.5375 | 146.254 | 149.5848 | 158.5973 | 166.5889 | 170.8957 |  |  | 11004 | 169.7399 | 166.7972 | 161.0436 | 162.3346 | 159.6888 | 159.5874 | 159.8228 | 160.5372 | 162.6635 | 169.3797 | 174.8643 | 178.5119 | [10 empty] | Huon River | Load transfer capacity (MVA)3
11005 | 122.4005 | 150.0787 | 154.3271 | 153.8528 | 151.2613 | 149.4227 | 149.5226 | 149.2333 | 152.632 | 161.828 | 169.9824 | 174.377 |  |  | 11005 | 171.7295 | 160.1568 | 154.6322 | 155.8719 | 153.3314 | 153.234 | 153.46 | 154.1459 | 156.1877 | 162.6365 | 167.9027 | 171.4051 | [10 empty] | Huon River | Load transfer capacity (MVA)4
11006 | 137.5959 | 151.788 | 156.0849 | 155.6051 | 152.9841 | 151.1246 | 151.2256 | 150.933 | 154.3704 | 163.6712 | 171.9184 | 176.3631 |  |  | 11006 | 173.6464 | 161.3701 | 155.8036 | 157.0527 | 154.4929 | 154.3948 | 154.6226 | 155.3137 | 157.3709 | 163.8685 | 169.1746 | 172.7035 | [10 empty] | Huon River | Load transfer capacity (MVA)5
11021 | 133.1441 | 99.9909 | 102.8215 | 102.5055 | 100.7789 | 99.5539 | 99.6204 | 99.4277 | 101.6921 | 107.819 | 113.2519 | 116.1799 |  |  | 11021 | 175.0037 | 170.881 | 164.9865 | 166.3092 | 163.5986 | 163.4947 | 163.7358 | 164.4677 | 166.6461 | 173.5267 | 179.1456 | 182.8825 | [10 empty] | Kermandie | Load transfer capacity (MVA)1 | Knights Road | 4.4
11023 | 134.038 | 111.1152 | 114.2607 | 113.9095 | 111.9908 | 110.6296 | 110.7035 | 110.4894 | 113.0057 | 119.8142 | 125.8516 | 129.1053 |  |  | 11023 | 210.2886 | 197.8362 | 191.0118 | 192.5431 | 189.405 | 189.2847 | 189.5639 | 190.4112 | 192.9332 | 200.8993 | 207.4044 | 211.7308 | [10 empty] | Kermandie | Load transfer capacity (MVA)2
11025 | 131.5821 | 104.9667 | 107.9381 | 107.6063 | 105.7938 | 104.5079 | 104.5777 | 104.3754 | 106.7525 | 113.1843 | 118.8875 | 121.9612 |  |  | 11025 | 175.2023 | 173.2654 | 167.2886 | 168.6298 | 165.8813 | 165.776 | 166.0205 | 166.7626 | 168.9714 | 175.9481 | 181.6453 | 185.4343 | [10 empty] | Kermandie | Load transfer capacity (MVA)3
11027 | 119.2429 | 108.4635 | 111.5339 | 111.1911 | 109.3182 | 107.9894 | 108.0616 | 107.8525 | 110.3087 | 116.9549 | 122.8481 | 126.0241 |  |  | 11027 | 188.9457 | 185.4949 | 179.0963 | 180.532 | 177.5896 | 177.4769 | 177.7386 | 178.5331 | 180.8978 | 188.3669 | 194.4662 | 198.5227 | [10 empty] | Kermandie | Load transfer capacity (MVA)4
12017 | 116.2599 | 69.485 | 71.452 | 71.2324 | 70.0325 | 69.1813 | 69.2275 | 69.0936 | 70.6671 | 74.9248 | 78.7002 | 80.7349 |  |  | 12017 | 169.5196 | 156.2893 | 150.8981 | 152.1078 | 149.6287 | 149.5337 | 149.7542 | 150.4236 | 152.416 | 158.7091 | 163.8481 | 167.2659 | [10 empty] | Kermandie | Load transfer capacity (MVA)5
12018 | 99.4679 | 63.3859 | 65.1802 | 64.9799 | 63.8854 | 63.1088 | 63.151 | 63.0288 | 64.4643 | 68.3482 | 71.7922 | 73.6483 |  |  | 12018 | 158.075 | 151.9868 | 146.744 | 147.9204 | 145.5095 | 145.4171 | 145.6316 | 146.2825 | 148.2201 | 154.34 | 159.3375 | 162.6612 | [10 empty] | Kingston kV | Load transfer capacity (MVA)1 | Electrona | 7.8
12019 | 121.1366 | 88.2211 | 90.7184 | 90.4396 | 88.9162 | 87.8354 | 87.8942 | 87.7241 | 89.722 | 95.1277 | 99.9211 | 102.5044 |  |  | 12019 | 215.0868 | 187.9984 | 181.5134 | 182.9686 | 179.9864 | 179.8722 | 180.1375 | 180.9426 | 183.3393 | 190.9092 | 197.0908 | 201.2021 | [10 empty] | Kingston kV | Load transfer capacity (MVA)2 | Kermandie | 3.1
12030 | 112.7079 | 66.9561 | 68.8515 | 68.6399 | 67.4837 | 66.6635 | 66.708 | 66.579 | 68.0952 | 72.198 | 75.836 | 77.7966 |  |  | 12030 | 171.6398 | 169.3139 | 163.4735 | 164.784 | 162.0983 | 161.9954 | 162.2343 | 162.9594 | 165.1179 | 171.9354 | 177.5027 | 181.2054 | [10 empty] | Kingston kV | Load transfer capacity (MVA)3 | Kingston | 1.6
12031 | 146.4817 | 93.441 | 96.0861 | 95.7908 | 94.1773 | 93.0326 | 93.0947 | 92.9146 | 95.0307 | 100.7563 | 105.8333 | 108.5694 |  |  | 12031 | 244.6077 | 202.6335 | 195.6437 | 197.2122 | 193.9979 | 193.8747 | 194.1607 | 195.0285 | 197.6117 | 205.7709 | 212.4338 | 216.8651 | [10 empty] | Kingston kV | Load transfer capacity (MVA)4
12032 | 66.7503 | 65.6983 | 67.5581 | 67.3505 | 66.216 | 65.4112 | 65.4549 | 65.3283 | 66.8161 | 70.8417 | 74.4114 | 76.3352 |  |  | 12032 | 111.0559 | 103.7568 | 100.1777 | 100.9808 | 99.335 | 99.2719 | 99.4183 | 99.8627 | 101.1854 | 105.3632 | 108.7749 | 111.0439 | [10 empty] | Kingston kV | Load transfer capacity (MVA)5
12033 | 42.5436 | 22.5739 | 23.2129 | 23.1416 | 22.7518 | 22.4752 | 22.4902 | 22.4467 | 22.9579 | 24.3411 | 25.5677 | 26.2287 |  |  | 12033 | 67.0621 | 64.7075 | 62.4754 | 62.9763 | 61.9499 | 61.9105 | 62.0018 | 62.279 | 63.1039 | 65.7094 | 67.837 | 69.2521 | [10 empty] | Kingston kV | Load transfer capacity (MVA)1
12034 | 2.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 12034 | 2.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Kingston kV | Load transfer capacity (MVA)2
12035 | 100.5143 | 68.2735 | 70.2062 | 69.9904 | 68.8115 | 67.9751 | 68.0205 | 67.8889 | 69.435 | 73.6185 | 77.328 | 79.3272 |  |  | 12035 | 177.6698 | 174.5904 | 168.5679 | 169.9193 | 167.1499 | 167.0437 | 167.2901 | 168.0378 | 170.2636 | 177.2936 | 183.0344 | 186.8524 | [10 empty] | Kingston kV | Load transfer capacity (MVA)3
12036 | 149.766 | 138.8356 | 142.7658 | 142.3269 | 139.9296 | 138.2287 | 138.3211 | 138.0535 | 141.1976 | 149.7047 | 157.2482 | 161.3136 |  |  | 12036 | 220.5128 | 224.0597 | 216.3308 | 218.0651 | 214.5109 | 214.3747 | 214.6909 | 215.6505 | 218.5069 | 227.5288 | 234.8962 | 239.7961 | [10 empty] | Kingston kV | Load transfer capacity (MVA)4
12037 | 121.8171 | 106.3939 | 109.4057 | 109.0694 | 107.2323 | 105.9289 | 105.9997 | 105.7946 | 108.204 | 114.7233 | 120.5041 | 123.6195 |  |  | 12037 | 160.1629 | 154.8522 | 149.5106 | 150.7092 | 148.2529 | 148.1587 | 148.3773 | 149.0404 | 151.0145 | 157.2498 | 162.3416 | 165.7279 | [10 empty] | Kingston kV | Load transfer capacity (MVA)5
12038 | 106.3002 | 70.7668 | 72.7701 | 72.5464 | 71.3245 | 70.4575 | 70.5046 | 70.3682 | 71.9708 | 76.307 | 80.152 | 82.2242 |  |  | 12038 | 157.6949 | 146.3608 | 141.3121 | 142.445 | 140.1233 | 140.0344 | 140.2409 | 140.8677 | 142.7336 | 148.6269 | 153.4395 | 156.6401 | [10 empty] | Knights Road | Load transfer capacity (MVA)1 | Electrona | 1.7
12039 | 108.1286 | 107.1872 | 110.2215 | 109.8827 | 108.0319 | 106.7187 | 106.7901 | 106.5835 | 109.0108 | 115.5787 | 121.4026 | 124.5413 |  |  | 12039 | 202.9551 | 185.6811 | 179.2761 | 180.7133 | 177.7679 | 177.6551 | 177.9171 | 178.7123 | 181.0794 | 188.556 | 194.6615 | 198.722 | [10 empty] | Knights Road | Load transfer capacity (MVA)2 | Kermandie | 3.4
13043 | 45.4081 | 31.3389 | 32.226 | 32.127 | 31.5858 | 31.2019 | 31.2228 | 31.1624 | 31.8721 | 33.7924 | 35.4951 | 36.4128 |  |  | 13043 | 83.3441 | 73.1538 | 70.6304 | 71.1966 | 70.0362 | 69.9917 | 70.095 | 70.4083 | 71.3409 | 74.2864 | 76.6919 | 78.2916 | [10 empty] | Knights Road | Load transfer capacity (MVA)3 | Kingston | 1.7
13044 | 110.9798 | 173.3 | 178.2058 | 177.6581 | 174.6656 | 172.5425 | 172.6579 | 172.3238 | 176.2484 | 186.8673 | 196.2834 | 201.358 |  |  | 13044 | 181.8303 | 177.3039 | 171.1878 | 172.5602 | 169.7477 | 169.6399 | 169.8901 | 170.6495 | 172.9098 | 180.0491 | 185.8791 | 189.7564 | [10 empty] | Knights Road | Load transfer capacity (MVA)4
13045 | 146.6747 | 115.5778 | 118.8496 | 118.4843 | 116.4885 | 115.0726 | 115.1495 | 114.9267 | 117.5441 | 124.6261 | 130.9059 | 134.2903 |  |  | 13045 | 264.519 | 229.7146 | 221.7907 | 223.5687 | 219.9249 | 219.7852 | 220.1094 | 221.0932 | 224.0217 | 233.2713 | 240.8247 | 245.8482 | [10 empty] | Knights Road | Load transfer capacity (MVA)5
13046 | 53.3908 | 53.25 | 54.7574 | 54.5891 | 53.6696 | 53.0172 | 53.0527 | 52.9501 | 54.1559 | 57.4188 | 60.3121 | 61.8714 |  |  | 13046 | 66.7657 | 77.5001 | 74.8268 | 75.4266 | 74.1973 | 74.1502 | 74.2596 | 74.5915 | 75.5795 | 78.7001 | 81.2484 | 82.9432 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)1
13047 | 42.7804 | 46.3667 | 89.6723 | 89.3967 | 87.8909 | 86.8225 | 86.8806 | 86.7125 | 88.6873 | 94.0307 | 98.7688 | 101.3223 |  |  | 13047 | 77.6386 | 55.0762 | 53.1763 | 53.6026 | 52.729 | 52.6955 | 52.7732 | 53.0091 | 53.7112 | 55.9289 | 57.7399 | 58.9443 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)2
13048 | 87.4009 | 79.7833 | 124.0349 | 123.6537 | 121.5709 | 120.0931 | 120.1734 | 119.9409 | 122.6725 | 130.0635 | 136.6173 | 140.1493 |  |  | 13048 | 130.3457 | 130.9214 | 126.4053 | 127.4186 | 125.3419 | 125.2623 | 125.4471 | 126.0078 | 127.6768 | 132.9484 | 137.2533 | 140.1164 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)3
13049 | 101.1609 | 64.0056 | 107.8105 | 107.4791 | 105.6688 | 104.3843 | 104.4541 | 104.252 | 106.6263 | 113.0505 | 118.747 | 121.817 |  |  | 13049 | 159.6904 | 151.9299 | 146.6891 | 147.8651 | 145.4551 | 145.3628 | 145.5772 | 146.2278 | 148.1647 | 154.2822 | 159.2779 | 162.6004 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)4
13050 | 52.2443 | 45.2556 | 88.5297 | 88.2576 | 86.771 | 85.7163 | 85.7736 | 85.6076 | 87.5573 | 92.8326 | 97.5104 | 100.0313 |  |  | 13050 | 80.3642 | 51.6757 | 49.8931 | 50.2931 | 49.4734 | 49.442 | 49.5149 | 49.7362 | 50.395 | 52.4758 | 54.175 | 55.305 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)5
13052 | 146.0604 | 137.9389 | 141.8437 | 141.4077 | 139.0259 | 137.336 | 137.4278 | 137.1619 | 140.2856 | 148.7379 | 156.2326 | 160.2718 |  |  | 13052 | 241.1405 | 230.5289 | 222.5769 | 224.3612 | 220.7045 | 220.5643 | 220.8897 | 221.8769 | 224.8158 | 234.0982 | 241.6784 | 246.7197 | [10 empty] | Meadowbank | Load transfer capacity (MVA)1 | New Norfolk | 3.4
13053 | 95.1687 | 68.7722 | 70.719 | 70.5017 | 69.3142 | 68.4716 | 68.5174 | 68.3848 | 69.9422 | 74.1563 | 77.8929 | 79.9067 |  |  | 13053 | 150.9579 | 140.046 | 135.2151 | 136.2991 | 134.0776 | 133.9925 | 134.1901 | 134.7899 | 136.5752 | 142.2143 | 146.8192 | 149.8818 | [10 empty] | Meadowbank | Load transfer capacity (MVA)2 | Wayatinah Zone | 0.5
13054 | 59.8133 | 56.7148 | 58.3202 | 58.141 | 57.1617 | 56.4669 | 56.5046 | 56.3953 | 57.6796 | 61.1548 | 64.2364 | 65.8971 |  |  | 13054 | 80.9392 | 79.4501 | 76.7094 | 77.3244 | 76.0641 | 76.0158 | 76.128 | 76.4682 | 77.4811 | 80.6802 | 83.2926 | 85.0301 | [10 empty] | Meadowbank | Load transfer capacity (MVA)3
13055 | 147.5841 | 84.2143 | 86.5983 | 86.3321 | 84.8779 | 83.8462 | 83.9023 | 83.74 | 85.6471 | 90.8073 | 95.383 | 97.849 |  |  | 13055 | 211.8493 | 184.1565 | 177.8041 | 179.2295 | 176.3083 | 176.1964 | 176.4563 | 177.245 | 179.5926 | 187.0078 | 193.0632 | 197.0904 | [10 empty] | Meadowbank | Load transfer capacity (MVA)4
13056 | 52.4416 | 51.3401 | 52.7935 | 52.6312 | 51.7447 | 51.1157 | 51.1499 | 51.0509 | 52.2136 | 55.3594 | 58.1489 | 59.6523 |  |  | 13056 | 97.0009 | 166.3051 | 160.5684 | 161.8557 | 159.2177 | 159.1166 | 159.3513 | 160.0635 | 162.1836 | 168.88 | 174.3484 | 177.9852 | [10 empty] | Meadowbank | Load transfer capacity (MVA)5
13057 | 153.3256 | 108.2553 | 111.3198 | 110.9777 | 109.1084 | 107.7821 | 107.8542 | 107.6455 | 110.097 | 116.7304 | 122.6123 | 125.7823 |  |  | 13057 | 221.9983 | 196.8057 | 190.0169 | 191.5403 | 188.4184 | 188.2988 | 188.5765 | 189.4194 | 191.9283 | 199.8529 | 206.3241 | 210.628 | [10 empty] | Mornington | Load transfer capacity (MVA)1
13058 | 67.2172 | 4.7667 | 4.9016 | 4.8865 | 4.8042 | 4.7458 | 4.749 | 4.7398 | 4.8478 | 5.1398 | 5.3988 | 5.5384 |  |  | 13058 | 60.4773 | 5.0352 | 4.8615 | 4.9005 | 4.8206 | 4.8175 | 4.8246 | 4.8462 | 4.9104 | 5.1131 | 5.2787 | 5.3888 | [10 empty] | Mornington | Load transfer capacity (MVA)2
14060 | 92.8986 | 90.7278 | 93.2961 | 93.0094 | 91.4427 | 90.3312 | 90.3916 | 90.2167 | 92.2713 | 97.8307 | 102.7603 | 105.417 |  |  | 14060 | 122.6469 | 109.867 | 106.0771 | 106.9275 | 105.1848 | 105.118 | 105.273 | 105.7435 | 107.1442 | 111.568 | 115.1806 | 117.5833 | [10 empty] | Mornington | Load transfer capacity (MVA)3
14061 | 64.7033 | 56.8 | 58.4079 | 58.2284 | 57.2476 | 56.5517 | 56.5895 | 56.4801 | 57.7663 | 61.2468 | 64.3329 | 65.9961 |  |  | 14061 | 81.2819 | 73.0015 | 70.4834 | 71.0484 | 69.8904 | 69.846 | 69.9491 | 70.2617 | 71.1923 | 74.1318 | 76.5322 | 78.1286 | [10 empty] | Mornington | Load transfer capacity (MVA)4
14062 | 34.3333 | 28.1056 | 28.9012 | 28.8123 | 28.327 | 27.9827 | 28.0014 | 27.9472 | 28.5837 | 30.3059 | 31.833 | 32.656 |  |  | 14062 | 35.9002 | 32.6397 | 31.5138 | 31.7665 | 31.2487 | 31.2289 | 31.2749 | 31.4147 | 31.8308 | 33.1451 | 34.2183 | 34.9321 | [10 empty] | Mornington | Load transfer capacity (MVA)5
14063 | 94.2976 | 82.9278 | 85.2753 | 85.0132 | 83.5813 | 82.5653 | 82.6205 | 82.4607 | 84.3386 | 89.42 | 93.9258 | 96.3541 |  |  | 14063 | 129.6898 | 122.455 | 118.231 | 119.1788 | 117.2364 | 117.1619 | 117.3347 | 117.8592 | 119.4203 | 124.351 | 128.3775 | 131.0554 | [10 empty] | Mowbray | Load transfer capacity (MVA)1 | Trevallyn | 31.4
14064 | 8.0056 | 1.2617 | 1.2974 | 1.2934 | 1.2716 | 1.2562 | 1.257 | 1.2546 | 1.2831 | 1.3605 | 1.429 | 1.466 |  |  | 14064 | 9.3257 | 1.1714 | 1.131 | 1.14 | 1.1215 | 1.1208 | 1.1224 | 1.1274 | 1.1424 | 1.1895 | 1.228 | 1.2537 | [10 empty] | Mowbray | Load transfer capacity (MVA)2 | Norwood | 6.3
14065 | 190.6281 | 182.4 | 187.5634 | 186.9869 | 183.8373 | 181.6027 | 181.7241 | 181.3726 | 185.5032 | 196.6797 | 206.5902 | 211.9313 |  |  | 14065 | 196.8699 | 203.3947 | 196.3786 | 197.953 | 194.7266 | 194.603 | 194.89 | 195.7611 | 198.354 | 206.5439 | 213.2318 | 217.6797 | [10 empty] | Mowbray | Load transfer capacity (MVA)3
14066 | 79.7364 | 113.9611 | 117.1872 | 116.827 | 114.8591 | 113.463 | 113.5388 | 113.3192 | 115.8999 | 122.8829 | 129.0749 | 132.4119 |  |  | 14066 | 101.5481 | 95.8875 | 92.5799 | 93.3221 | 91.8011 | 91.7428 | 91.8781 | 92.2887 | 93.5112 | 97.3721 | 100.5251 | 102.622 | [10 empty] | Mowbray | Load transfer capacity (MVA)4
14067 | 60.4505 | 46.9944 | 48.3248 | 48.1762 | 47.3648 | 46.789 | 46.8203 | 46.7297 | 47.794 | 50.6736 | 53.2269 | 54.603 |  |  | 14067 | 98.9989 | 62.9611 | 60.7893 | 61.2766 | 60.2779 | 60.2396 | 60.3285 | 60.5981 | 61.4008 | 63.9359 | 66.0062 | 67.3831 | [10 empty] | Mowbray | Load transfer capacity (MVA)5
14068 | 125.4829 | 125.5444 | 129.0984 | 128.7016 | 126.5337 | 124.9957 | 125.0793 | 124.8373 | 127.6803 | 135.3731 | 142.1944 | 145.8706 |  |  | 14068 | 178.6573 | 173.7206 | 167.7282 | 169.0728 | 166.3172 | 166.2116 | 166.4567 | 167.2007 | 169.4154 | 176.4103 | 182.1225 | 185.9215 | [10 empty] | New Norfolk | Load transfer capacity (MVA)1 | Meadowbank | 6.6
14069 | 202.2456 | 124.8444 | 128.3786 | 127.984 | 125.8282 | 124.2988 | 124.3818 | 124.1412 | 126.9684 | 134.6183 | 141.4016 | 145.0573 |  |  | 14069 | 148.4557 | 133.8944 | 129.2758 | 130.3122 | 128.1883 | 128.1069 | 128.2958 | 128.8692 | 130.5762 | 135.9675 | 140.3702 | 143.2982 | [10 empty] | New Norfolk | Load transfer capacity (MVA)2
14070 | 151.2155 | 146.7 | 150.8528 | 150.3892 | 147.856 | 146.0588 | 146.1564 | 145.8737 | 149.1958 | 158.1849 | 166.1556 | 170.4513 |  |  | 14070 | 194.9709 | 180.3726 | 174.1507 | 175.5468 | 172.6856 | 172.576 | 172.8306 | 173.603 | 175.9025 | 183.1653 | 189.0962 | 193.0407 | [10 empty] | New Norfolk | Load transfer capacity (MVA)3
14071 | 163.4964 | 163.8889 | 168.5283 | 168.0103 | 165.1803 | 163.1725 | 163.2816 | 162.9657 | 166.6771 | 176.7194 | 185.6241 | 190.4232 |  |  | 14071 | 179.3901 | 172.2063 | 166.2661 | 167.599 | 164.8674 | 164.7627 | 165.0057 | 165.7432 | 167.9386 | 174.8726 | 180.535 | 184.3009 | [10 empty] | New Norfolk | Load transfer capacity (MVA)4
14072 | 22.2364 | 16.5597 | 17.0285 | 16.9762 | 16.6902 | 16.4873 | 16.4984 | 16.4664 | 16.8415 | 17.8562 | 18.7559 | 19.2408 |  |  | 14072 | 24.9291 | 19.2603 | 23.4823 | 30.7363 | 30.2353 | 30.2161 | 30.2607 | 30.3959 | 30.7985 | 32.0702 | 33.1086 | 33.7992 | [10 empty] | New Norfolk | Load transfer capacity (MVA)5
16091 | 121.9411 | 97.2944 | 100.0487 | 99.7412 | 98.0611 | 96.8692 | 96.9339 | 96.7464 | 98.9497 | 104.9114 | 110.1978 | 113.0468 |  |  | 16091 | 204.1462 | 192.6888 | 190.9285 | 199.5248 | 196.2728 | 196.1482 | 196.4375 | 197.3155 | 199.929 | 208.1839 | 214.9249 | 219.4082 | [10 empty] | Newton | Load transfer capacity (MVA)1
16092 | 93.7603 | 72.1957 | 74.2394 | 74.0112 | 96.9674 | 95.7887 | 95.8528 | 95.6673 | 97.8461 | 103.7413 | 108.9687 | 111.7859 |  |  | 16092 | 131.1657 | 124.3678 | 124.9642 | 133.0317 | 130.8634 | 130.7803 | 130.9732 | 131.5586 | 133.3012 | 138.8051 | 143.2996 | 146.2888 | [10 empty] | Newton | Load transfer capacity (MVA)2
16093 | 92.5129 | 88.5333 | 91.0396 | 90.7597 | 113.4338 | 112.055 | 112.1299 | 111.9129 | 114.4617 | 121.358 | 127.4731 | 130.7687 |  |  | 16093 | 128.6872 | 122.166 | 122.8384 | 130.8888 | 128.7555 | 128.6738 | 128.8636 | 129.4395 | 131.154 | 136.5692 | 140.9914 | 143.9324 | [10 empty] | Newton | Load transfer capacity (MVA)3
16094 | 162.1109 | 59.75 | 61.4414 | 61.2526 | 84.4236 | 83.3974 | 83.4532 | 83.2917 | 85.1886 | 90.3213 | 94.8725 | 97.3252 |  |  | 16094 | 236.6309 | 231.0786 | 223.1076 | 224.8962 | 221.2307 | 221.0903 | 221.4164 | 222.406 | 225.3519 | 234.6564 | 242.2546 | 247.308 | [10 empty] | Newton | Load transfer capacity (MVA)4
16095 | 72.1224 | 130.4889 | 134.1828 | 133.7704 | 155.72 | 153.8271 | 153.93 | 153.6322 | 157.131 | 166.5982 | 174.9929 | 179.517 |  |  | 16095 | 75 | 77.0719 | 74.4133 | 75.0098 | 73.7873 | 73.7404 | 73.8492 | 74.1793 | 75.1618 | 78.2652 | 80.7994 | 82.4848 | [10 empty] | Newton | Load transfer capacity (MVA)5
16096 | 122.9727 | 105.45 | 108.4351 | 108.1018 | 106.281 | 104.9891 | 105.0593 | 104.856 | 107.244 | 113.7055 | 119.435 | 122.5228 |  |  | 16096 | 224.0123 | 224.4705 | 216.7274 | 218.4649 | 214.9042 | 214.7678 | 215.0846 | 216.0459 | 218.9075 | 227.946 | 235.3269 | 240.2357 | [10 empty] | North Hobart | Load transfer capacity (MVA)1
16097 | 45.3333 | 42.9444 | 44.1601 | 44.0244 | 43.2829 | 42.7567 | 42.7853 | 42.7025 | 43.6751 | 46.3065 | 48.6398 | 49.8973 |  |  | 16097 | 62.9122 | 50.5532 | 48.8094 | 49.2007 | 48.3988 | 48.3681 | 48.4394 | 48.6559 | 49.3004 | 51.3359 | 52.9982 | 54.1037 | [10 empty] | North Hobart | Load transfer capacity (MVA)2
16098 | 125.2147 | 97.3889 | 100.1458 | 99.838 | 98.1563 | 96.9632 | 97.028 | 96.8403 | 99.0458 | 105.0133 | 110.3048 | 113.1565 |  |  | 16098 | 212.7631 | 205.6194 | 198.5266 | 200.1181 | 196.8565 | 196.7315 | 197.0217 | 197.9023 | 200.5236 | 208.803 | 215.564 | 220.0606 | [10 empty] | North Hobart | Load transfer capacity (MVA)3
17100 | 105.1587 | 87.0721 | 89.5369 | 89.2617 | 87.7582 | 86.6915 | 86.7494 | 86.5816 | 88.5534 | 93.8888 | 98.6197 | 101.1694 |  |  | 17100 | 128.8158 | 108.1778 | 104.4462 | 105.2835 | 103.5676 | 103.5018 | 103.6545 | 104.1178 | 105.4968 | 109.8527 | 113.4097 | 115.7754 | [10 empty] | North Hobart | Load transfer capacity (MVA)4
17101 | 91.9384 | 65.25 | 67.0971 | 66.8909 | 65.7642 | 64.9648 | 65.0082 | 64.8825 | 66.3601 | 70.3583 | 73.9036 | 75.8142 |  |  | 17101 | 123.661 | 108.5324 | 104.7886 | 105.6287 | 103.9071 | 103.8411 | 103.9943 | 104.4591 | 105.8427 | 110.2128 | 113.7816 | 116.155 | [10 empty] | North Hobart | Load transfer capacity (MVA)5
17102 | 15.7741 | 1.4778 | 1.5196 | 1.5149 | 1.4894 | 1.4713 | 1.4723 | 1.4695 | 1.5029 | 1.5935 | 1.6738 | 1.717 |  |  | 17102 | 15.2214 | 1.8533 | 1.7894 | 1.8037 | 1.7743 | 1.7732 | 1.7758 | 1.7837 | 1.8074 | 1.882 | 1.9429 | 1.9835 | [10 empty] | Norwood | Load transfer capacity (MVA)1 | Trevallyn | 16.2
17103 | 98.3907 | 90.8111 | 93.3818 | 93.0948 | 91.5267 | 90.4142 | 90.4746 | 90.2996 | 92.3561 | 97.9205 | 102.8547 | 105.5138 |  |  | 17103 | 171.4361 | 161.7816 | 156.201 | 157.4532 | 154.887 | 154.7886 | 155.0169 | 155.7098 | 157.7722 | 164.2865 | 169.6061 | 173.144 | [10 empty] | Norwood | Load transfer capacity (MVA)2 | Mowbray | 10.8
17104 | 117.6067 | 74.7556 | 76.8718 | 76.6355 | 75.3446 | 74.4288 | 74.4786 | 74.3345 | 76.0274 | 80.608 | 84.6698 | 86.8588 |  |  | 17104 | 130.2547 | 96.6181 | 93.2853 | 94.0331 | 92.5005 | 92.4418 | 92.5781 | 92.9919 | 94.2237 | 98.114 | 101.291 | 103.4039 | [10 empty] | Norwood | Load transfer capacity (MVA)3 | St Leonards | 27
17105 | 155.1789 | 127.9111 | 131.5321 | 131.1278 | 128.9191 | 127.352 | 127.4372 | 127.1906 | 130.0873 | 137.925 | 144.8749 | 148.6204 |  |  | 17105 | 219.5472 | 213.6902 | 206.319 | 207.973 | 204.5833 | 204.4535 | 204.755 | 205.6702 | 208.3944 | 216.9988 | 224.0252 | 228.6983 | [10 empty] | Norwood | Load transfer capacity (MVA)4 | Hadspen | 16.2
17106 | 166.8491 | 138.9818 | 142.9161 | 142.4768 | 140.077 | 138.3743 | 138.4668 | 138.1989 | 141.3463 | 149.8624 | 157.4138 | 161.4835 |  |  | 17106 | 199.9601 | 183.9796 | 177.6333 | 179.0573 | 176.1389 | 176.0271 | 176.2867 | 177.0746 | 179.4201 | 186.8281 | 192.8777 | 196.901 | [10 empty] | Norwood | Load transfer capacity (MVA)5
17107 | 84.385 | 82.3944 | 84.7269 | 84.4665 | 83.0437 | 82.0343 | 82.0891 | 81.9303 | 83.7962 | 88.8449 | 93.3218 | 95.7344 |  |  | 17107 | 117.9023 | 110.1093 | 106.3111 | 107.1634 | 105.4168 | 105.3499 | 105.5052 | 105.9768 | 107.3805 | 111.8141 | 115.4347 | 117.8426 | [10 empty] | Palmerston | Load transfer capacity (MVA)1 | Norwood | 2
17108 | 33.3598 | 29.9148 | 30.7616 | 30.6671 | 30.1505 | 29.784 | 29.804 | 29.7463 | 30.4237 | 32.2568 | 33.8822 | 34.7581 |  |  | 17108 | 48.6265 | 29.35 | 28.3376 | 28.5648 | 28.0992 | 28.0813 | 28.1228 | 28.2485 | 28.6226 | 29.8044 | 30.7695 | 31.4113 | [10 empty] | Palmerston | Load transfer capacity (MVA)2 | Hadspen | 5
17109 | 62.0732 | 47.1389 | 48.4733 | 48.3243 | 47.5103 | 46.9328 | 46.9642 | 46.8734 | 47.9409 | 50.8293 | 53.3905 | 54.7709 |  |  | 17109 | 84.531 | 64.8935 | 62.655 | 63.1573 | 62.1279 | 62.0885 | 62.1801 | 62.458 | 63.2853 | 65.8983 | 68.0321 | 69.4512 | [10 empty] | Palmerston | Load transfer capacity (MVA)3
20534 | 37.9309 | 30.0084 | 30.8579 | 30.7631 | 30.2449 | 29.8773 | 29.8972 | 29.8394 | 30.519 | 32.3577 | 33.9882 | 34.8669 |  |  | 20534 | 67.9438 | 59.0865 | 57.0483 | 57.5057 | 56.5684 | 56.5325 | 56.6159 | 56.8689 | 57.6222 | 60.0014 | 61.9442 | 63.2363 | [10 empty] | Palmerston | Load transfer capacity (MVA)4
20535 | 85.5568 | 69.3381 | 71.301 | 71.0818 | 69.8845 | 69.0351 | 69.0812 | 68.9476 | 70.5178 | 74.7665 | 78.5339 | 80.5643 |  |  | 20535 | 314.4447 | 157.4343 | 152.0036 | 153.2222 | 150.7249 | 150.6292 | 150.8514 | 151.5256 | 153.5326 | 159.8718 | 165.0485 | 168.4913 | [10 empty] | Palmerston | Load transfer capacity (MVA)5
20536 | 89.5253 | 71.9158 | 73.9516 | 73.7243 | 72.4825 | 71.6015 | 71.6494 | 71.5107 | 73.1393 | 77.546 | 81.4535 | 83.5593 |  |  | 20536 | 165.8201 | 151.9914 | 146.7485 | 147.925 | 145.514 | 145.4216 | 145.6361 | 146.287 | 148.2247 | 154.3447 | 159.3424 | 162.6663 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)1 | Burnie | 3.9
20537 | 72.8609 | 56.6174 | 58.2202 | 58.0412 | 57.0636 | 56.37 | 56.4077 | 56.2985 | 57.5807 | 61.0499 | 64.1262 | 65.784 |  |  | 20537 | 126.8334 | 124.655 | 120.3551 | 121.3199 | 119.3426 | 119.2668 | 119.4427 | 119.9766 | 121.5657 | 126.585 | 130.6839 | 133.4099 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)2 | Smithton | 3.9
20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)3
20539 | 26.2926 | 22.7017 | 23.3443 | 23.2726 | 22.8806 | 22.6024 | 22.6175 | 22.5738 | 23.0879 | 24.4789 | 25.7124 | 26.3772 |  |  | 20539 | 39.1628 | 34.0141 | 32.8408 | 33.104 | 32.5645 | 32.5438 | 32.5918 | 32.7375 | 33.1711 | 34.5407 | 35.6592 | 36.403 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)4
20540 | 115.3074 | 114.4294 | 117.6687 | 117.3071 | 115.3312 | 113.9293 | 114.0054 | 113.7849 | 116.3762 | 123.3879 | 129.6053 | 132.956 |  |  | 20540 | 119.7486 | 125.5257 | 121.1957 | 122.1673 | 120.1761 | 120.0998 | 120.277 | 120.8146 | 122.4148 | 127.4692 | 131.5967 | 134.3417 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)5
20541 | 142.5702 | 129.8861 | 133.563 | 133.1524 | 130.9096 | 129.3184 | 129.4048 | 129.1545 | 132.0959 | 140.0546 | 147.1119 | 150.9152 |  |  | 20541 | 239.9805 | 227.1048 | 219.2709 | 221.0287 | 217.4263 | 217.2882 | 217.6087 | 218.5813 | 221.4765 | 230.6211 | 238.0886 | 243.055 | [10 empty] | Queenstown | Load transfer capacity (MVA)1
20544 | 103.6098 | 77.8168 | 80.0197 | 79.7737 | 78.43 | 77.4767 | 77.5285 | 77.3785 | 79.1407 | 83.909 | 88.137 | 90.4157 |  |  | 20544 | 144.9676 | 138.1782 | 133.4118 | 134.4813 | 132.2895 | 132.2055 | 132.4005 | 132.9923 | 134.7538 | 140.3177 | 144.8612 | 147.8829 | [10 empty] | Queenstown | Load transfer capacity (MVA)2
20545 | 33.5161 | 27.6167 | 28.3984 | 28.3112 | 27.8343 | 27.496 | 27.5143 | 27.4611 | 28.0865 | 29.7787 | 31.2792 | 32.0879 |  |  | 20545 | 64.0616 | 54.8358 | 52.9442 | 53.3687 | 52.4988 | 52.4655 | 52.5429 | 52.7777 | 53.4768 | 55.6848 | 57.4879 | 58.6871 | [10 empty] | Queenstown | Load transfer capacity (MVA)3
20547 | 170.0343 | 137.9889 | 141.8951 | 141.459 | 139.0763 | 137.3858 | 137.4776 | 137.2116 | 140.3365 | 148.7918 | 156.2892 | 160.3298 |  |  | 20547 | 151.527 | 303.6461 | 293.1719 | 295.5222 | 290.7056 | 290.5211 | 290.9496 | 292.25 | 296.121 | 308.3475 | 318.3318 | 324.9721 | [10 empty] | Queenstown | Load transfer capacity (MVA)4
20548 | 108.656 | 88.1341 | 90.629 | 90.3504 | 88.8286 | 87.7488 | 87.8075 | 87.6376 | 89.6335 | 95.0339 | 99.8226 | 102.4033 |  |  | 20548 | 320.3896 | 156.2793 | 170.4847 | 171.8515 | 169.0505 | 168.9432 | 169.1924 | 169.9486 | 172.1997 | 179.3096 | 185.1157 | 188.9771 | [10 empty] | Queenstown | Load transfer capacity (MVA)5
20549 | 101.8624 | 82.56 | 84.8971 | 84.6362 | 83.2106 | 82.1991 | 82.2541 | 82.095 | 83.9646 | 89.0235 | 93.5093 | 95.9268 |  |  | 20549 | 178.6856 | 235.2142 | 246.6968 | 248.6745 | 244.6215 | 244.4662 | 244.8267 | 245.921 | 249.1783 | 259.4666 | 267.8682 | 273.4558 | [10 empty] | Railton | Load transfer capacity (MVA)1 | Devonport | 8.7
20551 | 40.5655 | 55.1576 | 56.719 | 56.5447 | 55.5923 | 54.9165 | 54.9532 | 54.8469 | 56.096 | 59.4758 | 62.4727 | 64.0879 |  |  | 20551 | 40.5 | 43.705 | 61.7936 | 62.289 | 61.2738 | 61.2349 | 61.3252 | 61.5993 | 62.4152 | 64.9923 | 67.0967 | 68.4964 | [10 empty] | Railton | Load transfer capacity (MVA)2 | Ulverstone | 4.4
20552 | 90.0807 | 80.8678 | 83.157 | 82.9014 | 81.505 | 80.5143 | 80.5681 | 80.4123 | 82.2436 | 87.1988 | 91.5926 | 93.9606 |  |  | 20552 | 188.7202 | 165.5414 | 179.4273 | 180.8657 | 177.9179 | 177.8049 | 178.0672 | 178.8631 | 181.2322 | 188.7151 | 194.8257 | 198.8897 | [10 empty] | Railton | Load transfer capacity (MVA)3
20553 | 98.0885 | 83.1956 | 85.5507 | 85.2877 | 83.8511 | 82.8319 | 82.8873 | 82.7269 | 84.611 | 89.7088 | 94.2291 | 96.6653 |  |  | 20553 | 174.4404 | 150.036 | 144.8605 | 146.0219 | 143.6419 | 143.5507 | 143.7624 | 144.405 | 146.3177 | 152.359 | 157.2924 | 160.5735 | [10 empty] | Railton | Load transfer capacity (MVA)4
20554 | 91.4512 | 82.4294 | 84.7629 | 84.5024 | 83.079 | 82.0692 | 82.124 | 81.9651 | 83.8318 | 88.8827 | 93.3614 | 95.7751 |  |  | 20554 | 150.8271 | 136.1962 | 131.4981 | 132.5523 | 130.3919 | 130.3091 | 130.5013 | 131.0846 | 132.8209 | 138.3049 | 142.7832 | 145.7616 | [10 empty] | Railton | Load transfer capacity (MVA)5
21081 | 107.2365 | 103.9778 | 106.9212 | 106.5926 | 104.7971 | 103.5233 | 103.5925 | 103.3921 | 105.7468 | 112.118 | 117.7675 | 120.8122 |  |  | 21081 | 173.0621 | 169.7983 | 163.9412 | 165.2554 | 162.562 | 162.4588 | 162.6984 | 163.4256 | 165.5903 | 172.4273 | 178.0105 | 181.7238 | [10 empty] | Risdon kV | Load transfer capacity (MVA)1
21082 | 27.4121 | 24.3111 | 24.9993 | 24.9225 | 24.5027 | 24.2048 | 24.221 | 24.1742 | 24.7247 | 26.2144 | 27.5353 | 28.2472 |  |  | 21082 | 47.4133 | 46.9867 | 45.3659 | 45.7295 | 44.9842 | 44.9557 | 45.022 | 45.2232 | 45.8222 | 47.7141 | 49.2591 | 50.2867 | [10 empty] | Risdon kV | Load transfer capacity (MVA)2
21083 | 180.4313 | 166.4167 | 171.1276 | 170.6017 | 167.728 | 165.6893 | 165.8 | 165.4793 | 169.2479 | 179.4451 | 188.4872 | 193.3602 |  |  | 21083 | 191.6625 | 174.9238 | 168.8898 | 170.2438 | 167.469 | 167.3627 | 167.6095 | 168.3587 | 170.5887 | 177.6321 | 183.3839 | 187.2092 | [10 empty] | Risdon kV | Load transfer capacity (MVA)3
21084 | 152.9562 | 142.6833 | 146.7224 | 146.2715 | 143.8077 | 142.0597 | 142.1546 | 141.8796 | 145.1108 | 153.8537 | 161.6063 | 165.7843 |  |  | 21084 | 180.8427 | 141.792 | 136.9009 | 137.9984 | 135.7492 | 135.663 | 135.8631 | 136.4704 | 138.278 | 143.9873 | 148.6497 | 151.7504 | [10 empty] | Risdon kV | Load transfer capacity (MVA)4
21085 | 138.5026 | 134.2444 | 138.0447 | 137.6204 | 135.3023 | 133.6577 | 133.747 | 133.4883 | 136.5283 | 144.7542 | 152.0482 | 155.9792 |  |  | 21085 | 274.5987 | 259.4834 | 250.5325 | 252.541 | 248.425 | 248.2672 | 248.6334 | 249.7447 | 253.0527 | 263.501 | 272.0332 | 277.7077 | [10 empty] | Risdon kV | Load transfer capacity (MVA)5
21086 | 74.9733 | 60.4944 | 62.2069 | 62.0157 | 60.9711 | 60.23 | 60.2703 | 60.1537 | 61.5236 | 65.2304 | 68.5173 | 70.2887 |  |  | 21086 | 140.9581 | 137.3564 | 132.6183 | 133.6815 | 131.5027 | 131.4192 | 131.613 | 132.2013 | 133.9523 | 139.4831 | 143.9996 | 147.0033 | [10 empty] | Rokeby | Load transfer capacity (MVA)1 | Howrah Zone | 4.8
21087 | 53.4906 | 47.8444 | 49.1988 | 49.0476 | 48.2215 | 47.6353 | 47.6672 | 47.5749 | 48.6584 | 51.5901 | 54.1897 | 55.5907 |  |  | 21087 | 104.1457 | 97.2151 | 93.8617 | 94.6141 | 93.0721 | 93.013 | 93.1502 | 93.5665 | 94.8058 | 98.7203 | 101.9168 | 104.0428 | [10 empty] | Rokeby | Load transfer capacity (MVA)2 | Cambridge Zone | 4.8
21088 | 32.3294 | 30.3833 | 31.2434 | 31.1474 | 30.6228 | 30.2505 | 30.2708 | 30.2122 | 30.9002 | 32.762 | 34.4128 | 35.3025 |  |  | 21088 | 61.5053 | 54.1614 | 52.2931 | 52.7123 | 51.8532 | 51.8203 | 51.8967 | 52.1287 | 52.8191 | 55 | 56.7809 | 57.9653 | [10 empty] | Rokeby | Load transfer capacity (MVA)3
21089 | 86.8468 | 84.1222 | 86.5036 | 86.2377 | 84.7851 | 83.7545 | 83.8105 | 83.6484 | 85.5534 | 90.708 | 95.2787 | 97.7419 |  |  | 21089 | 150.5987 | 151.2684 | 146.0504 | 147.2212 | 144.8217 | 144.7298 | 144.9433 | 145.5911 | 147.5195 | 153.6104 | 158.5844 | 161.8924 | [10 empty] | Rokeby | Load transfer capacity (MVA)4
22323 | 68.8897 | 56.6228 | 58.2257 | 58.0467 | 57.069 | 56.3753 | 56.413 | 56.3038 | 57.5861 | 61.0557 | 64.1322 | 65.7902 |  |  | 22323 | 104.239 | 94.0092 | 90.7664 | 91.494 | 90.0028 | 89.9456 | 90.0783 | 90.4809 | 91.6794 | 95.4647 | 98.5559 | 100.6117 | [10 empty] | Rokeby | Load transfer capacity (MVA)5
22324 | 98.6559 | 83.57 | 85.9357 | 85.6716 | 84.2285 | 83.2047 | 83.2603 | 83.0993 | 84.9918 | 90.1125 | 94.6532 | 97.1003 |  |  | 22324 | 145.9686 | 140.8127 | 135.9553 | 137.0453 | 134.8116 | 134.726 | 134.9248 | 135.5278 | 137.3229 | 142.9929 | 147.623 | 150.7023 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)1
22325 | 98.7317 | 84.9983 | 87.4045 | 87.1358 | 85.6681 | 84.6268 | 84.6834 | 84.5196 | 86.4444 | 91.6527 | 96.271 | 98.7599 |  |  | 22325 | 175.0863 | 150.7481 | 145.5481 | 146.7149 | 144.3237 | 144.232 | 144.4448 | 145.0904 | 147.0122 | 153.0821 | 158.039 | 161.3356 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)2
22326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 22326 | 56.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)3
22328 | 139.0604 | 123.5639 | 127.0618 | 126.6712 | 124.5376 | 123.0238 | 123.106 | 122.8679 | 125.6661 | 133.2375 | 139.9512 | 143.5694 |  |  | 22328 | 198.2958 | 193.5743 | 186.8969 | 188.3953 | 185.3247 | 185.207 | 185.4802 | 186.3092 | 188.777 | 196.5714 | 202.9364 | 207.1695 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)4
22329 | 120.0448 | 103.0733 | 105.9912 | 105.6654 | 103.8856 | 102.6228 | 102.6914 | 102.4927 | 104.8269 | 111.1428 | 116.7431 | 119.7613 |  |  | 22329 | 276.3709 | 187.5991 | 181.1279 | 182.58 | 179.6042 | 179.4901 | 179.7549 | 180.5583 | 182.9499 | 190.5037 | 196.6722 | 200.7747 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)5
22330 | 10.594 | 6.0505 | 6.2218 | 6.2027 | 6.0982 | 6.0241 | 6.0281 | 6.0165 | 6.1535 | 6.5242 | 6.853 | 7.0301 |  |  | 22330 | 14.5145 | 15.1273 | 14.6054 | 14.7225 | 14.4826 | 14.4734 | 14.4947 | 14.5595 | 14.7524 | 15.3615 | 15.8589 | 16.1897 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)1
22331 | 123.4277 | 124.3706 | 127.8913 | 127.4982 | 125.3506 | 123.8269 | 123.9097 | 123.67 | 126.4865 | 134.1073 | 140.8648 | 144.5067 |  |  | 22331 | 234.1418 | 200.8049 | 193.8782 | 195.4325 | 192.2472 | 192.1252 | 192.4085 | 193.2685 | 195.8284 | 203.914 | 210.5168 | 214.9081 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)2
23340 | 95.5333 | 87.4611 | 89.937 | 89.6606 | 88.1503 | 87.0788 | 87.137 | 86.9685 | 88.9491 | 94.3083 | 99.0604 | 101.6214 |  |  | 23340 | 88.5388 | 76.8314 | 74.1811 | 74.7758 | 73.5571 | 73.5104 | 73.6188 | 73.9478 | 74.9273 | 78.021 | 80.5473 | 82.2275 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)3
23341 | 82.9543 | 72.0361 | 74.0753 | 73.8477 | 72.6038 | 71.7212 | 71.7692 | 71.6303 | 73.2617 | 77.6757 | 81.5897 | 83.699 |  |  | 23341 | 129.9241 | 119.9652 | 115.8271 | 116.7556 | 114.8527 | 114.7797 | 114.949 | 115.4628 | 116.9922 | 121.8227 | 125.7673 | 128.3908 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)4
23342 | 149.3584 | 90.9044 | 93.4778 | 93.1905 | 91.6208 | 90.5071 | 90.5676 | 90.3924 | 92.451 | 98.0212 | 102.9604 | 105.6222 |  |  | 23342 | 209.9646 | 190.2306 | 183.6687 | 185.1411 | 182.1235 | 182.0079 | 182.2764 | 183.0911 | 185.5162 | 193.176 | 199.431 | 203.5911 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)5
23343 | 121.7079 | 129.8233 | 133.4984 | 133.0881 | 130.8464 | 129.2559 | 129.3423 | 129.0921 | 132.032 | 139.987 | 147.0408 | 150.8423 |  |  | 23343 | 189.9266 | 176.7934 | 170.6949 | 172.0634 | 169.259 | 169.1515 | 169.401 | 170.1582 | 172.412 | 179.5307 | 185.3439 | 189.2101 | [10 empty] | Savage River DL | Load transfer capacity (MVA)1
23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Savage River DL | Load transfer capacity (MVA)2
23347 | 81.5108 | 61.0162 | 62.7435 | 62.5506 | 61.497 | 60.7495 | 60.7901 | 60.6725 | 62.0543 | 65.7931 | 69.1083 | 70.895 |  |  | 23347 | 121.6255 | 132.6265 | 128.0515 | 129.0781 | 126.9743 | 126.8937 | 127.0808 | 127.6488 | 129.3396 | 134.6799 | 139.0409 | 141.9412 | [10 empty] | Savage River DL | Load transfer capacity (MVA)3
23348 | 92.6928 | 77.8772 | 80.0818 | 79.8357 | 78.4909 | 77.5368 | 77.5887 | 77.4386 | 79.2022 | 83.9741 | 88.2055 | 90.4859 |  |  | 23348 | 150.6928 | 149.0096 | 143.8695 | 145.0229 | 142.6592 | 142.5686 | 142.7789 | 143.4171 | 145.3167 | 151.3167 | 156.2163 | 159.475 | [10 empty] | Savage River DL | Load transfer capacity (MVA)4
24401 | 100.2288 | 95.825 | 98.5376 | 98.2348 | 96.5801 | 95.4062 | 95.4699 | 95.2852 | 97.4553 | 103.327 | 108.5335 | 111.3395 |  |  | 24401 | 179.9288 | 150.0569 | 144.8807 | 146.0422 | 143.6619 | 143.5707 | 143.7825 | 144.4251 | 146.3381 | 152.3802 | 157.3143 | 160.5959 | [10 empty] | Savage River DL | Load transfer capacity (MVA)5
24402 | 92.0456 | 78.755 | 80.9844 | 80.7355 | 79.3756 | 78.4108 | 78.4632 | 78.3114 | 80.0949 | 84.9206 | 89.1996 | 91.5058 |  |  | 24402 | 134.6321 | 129.0129 | 124.5626 | 125.5612 | 123.5147 | 123.4363 | 123.6184 | 124.1709 | 125.8156 | 131.0104 | 135.2525 | 138.0738 | [10 empty] | Scottsdale | Load transfer capacity (MVA)1 | Derby | 4.8
24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Scottsdale | Load transfer capacity (MVA)2 | George Town | 3.2
24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Scottsdale | Load transfer capacity (MVA)3
24405 | 178.6838 | 153.8267 | 158.1812 | 157.695 | 155.0388 | 153.1543 | 153.2567 | 152.9602 | 156.4437 | 165.8695 | 174.2275 | 178.7318 |  |  | 24405 | 272.9969 | 261.2746 | 252.2619 | 254.2843 | 250.1398 | 249.981 | 250.3497 | 251.4687 | 254.7995 | 265.3199 | 273.911 | 279.6247 | [10 empty] | Scottsdale | Load transfer capacity (MVA)4
24406 | 100.1859 | 95.815 | 98.5274 | 98.2245 | 96.57 | 95.3962 | 95.46 | 95.2753 | 97.4451 | 103.3162 | 108.5222 | 111.3278 |  |  | 24406 | 180.0619 | 149.7475 | 144.582 | 145.7411 | 143.3657 | 143.2747 | 143.486 | 144.1273 | 146.0364 | 152.0661 | 156.99 | 160.2647 | [10 empty] | Scottsdale | Load transfer capacity (MVA)5
25305 | 60.3766 | 48.0402 | 49.4002 | 49.2483 | 48.4188 | 47.8303 | 47.8622 | 47.7696 | 48.8576 | 51.8012 | 54.4114 | 55.8182 |  |  | 25305 | 90.1584 | 80.2913 | 77.5217 | 78.1432 | 76.8696 | 76.8208 | 76.9341 | 77.2779 | 78.3015 | 81.5345 | 84.1746 | 85.9304 | [10 empty] | Sheffield | Load transfer capacity (MVA)1
25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Sheffield | Load transfer capacity (MVA)2
25307 | 117.7657 | 89.109 | 91.6315 | 91.3499 | 89.8112 | 88.7195 | 88.7788 | 88.607 | 90.625 | 96.0852 | 100.9268 | 103.5361 |  |  | 25307 | 167.7529 | 156.1493 | 150.763 | 151.9716 | 149.4947 | 149.3998 | 149.6201 | 150.2889 | 152.2795 | 158.567 | 163.7014 | 167.1161 | [10 empty] | Sheffield | Load transfer capacity (MVA)3
25308 | 96.7784 | 86.9337 | 89.3946 | 89.1199 | 87.6187 | 86.5537 | 86.6116 | 86.444 | 88.4127 | 93.7396 | 98.463 | 101.0086 |  |  | 25308 | 164.2691 | 152.6224 | 147.3577 | 148.5391 | 146.1181 | 146.0253 | 146.2407 | 146.8943 | 148.84 | 154.9855 | 160.0039 | 163.3415 | [10 empty] | Sheffield | Load transfer capacity (MVA)4
25309 | 115.1603 | 98.4796 | 101.2673 | 100.9561 | 99.2556 | 98.0491 | 98.1147 | 97.9248 | 100.155 | 106.1893 | 111.5401 | 114.4238 |  |  | 25309 | 146.6728 | 137.9741 | 133.2147 | 134.2827 | 132.0941 | 132.0102 | 132.2049 | 132.7958 | 134.5547 | 140.1104 | 144.6472 | 147.6644 | [10 empty] | Sheffield | Load transfer capacity (MVA)5
25310 | 55.6547 | 51.1341 | 52.5816 | 52.42 | 51.5371 | 50.9106 | 50.9447 | 50.8461 | 52.0041 | 55.1373 | 57.9156 | 59.4129 |  |  | 25310 | 96.1575 | 83.9633 | 81.067 | 81.7169 | 80.385 | 80.334 | 80.4525 | 80.8121 | 81.8825 | 85.2633 | 88.0241 | 89.8603 | [10 empty] | Smithton | Load transfer capacity (MVA)1 | Port Latta | 5.1
26161 | 170.3333 | 93.0944 | 95.7298 | 95.4355 | 93.828 | 92.6875 | 92.7495 | 92.5701 | 94.6783 | 100.3826 | 105.4408 | 108.1668 |  |  | 26161 | 153.1883 | 251.9322 | 243.2418 | 245.1918 | 241.1955 | 241.0424 | 241.3979 | 242.4769 | 245.6886 | 255.8328 | 264.1167 | 269.6261 | [10 empty] | Smithton | Load transfer capacity (MVA)2
26162 | 38.0329 | 88.4778 | 90.9824 | 90.7028 | 89.175 | 88.091 | 88.1499 | 87.9794 | 89.9831 | 95.4045 | 100.2119 | 102.8027 |  |  | 26162 | 178.781 | 163.7608 | 158.1119 | 159.3795 | 156.7818 | 156.6823 | 156.9134 | 157.6147 | 159.7024 | 166.2963 | 171.681 | 175.2622 | [10 empty] | Smithton | Load transfer capacity (MVA)3
26163 | 69.5738 | 52.8222 | 54.3175 | 54.1506 | 53.2385 | 52.5913 | 52.6265 | 52.5247 | 53.7209 | 56.9576 | 59.8276 | 61.3744 |  |  | 26163 | 109.4599 | 93.5056 | 90.2802 | 91.0039 | 89.5207 | 89.4639 | 89.5958 | 89.9963 | 91.1883 | 94.9534 | 98.028 | 100.0728 | [10 empty] | Smithton | Load transfer capacity (MVA)4
26164 | 188.284 | 114.6556 | 117.9013 | 117.5389 | 115.5591 | 114.1544 | 114.2307 | 114.0097 | 116.6062 | 123.6317 | 129.8614 | 133.2188 |  |  | 26164 | 218.9563 | 223.3207 | 215.6173 | 217.3459 | 213.8034 | 213.6677 | 213.9828 | 214.9392 | 217.7862 | 226.7784 | 234.1215 | 239.0052 | [10 empty] | Smithton | Load transfer capacity (MVA)5
26165 | 102.3143 | 72.1611 | 74.2039 | 73.9758 | 72.7297 | 71.8457 | 71.8937 | 71.7546 | 73.3888 | 77.8105 | 81.7313 | 83.8443 |  |  | 26165 | 143.4032 | 111.4309 | 107.5871 | 108.4496 | 106.682 | 106.6143 | 106.7715 | 107.2488 | 108.6693 | 113.1562 | 116.8202 | 119.257 | [10 empty] | Sorell | Load transfer capacity (MVA)1 | Avoca | 1.5
26166 | 54.943 | 44.9778 | 46.251 | 46.1089 | 45.3322 | 44.7812 | 44.8111 | 44.7244 | 45.743 | 48.499 | 50.9428 | 52.2599 |  |  | 26166 | 94.6895 | 86.4149 | 83.434 | 84.1029 | 82.7322 | 82.6796 | 82.8016 | 83.1717 | 84.2733 | 87.7529 | 90.5943 | 92.4841 | [10 empty] | Sorell | Load transfer capacity (MVA)2 | Triabunna | 1.5
26167 | 139.9584 | 116.1569 | 119.4451 | 119.078 | 117.0723 | 115.6492 | 115.7265 | 115.5026 | 118.1331 | 125.2506 | 131.5619 | 134.9632 |  |  | 26167 | 233.2233 | 213.3248 | 205.9662 | 207.6174 | 204.2335 | 204.1039 | 204.4049 | 205.3185 | 208.038 | 216.6277 | 223.6421 | 228.3072 | [10 empty] | Sorell | Load transfer capacity (MVA)3 | Meadowbank | 1.5
26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Sorell | Load transfer capacity (MVA)4
27171 | 114.244 | 88.5278 | 91.0338 | 90.754 | 89.2254 | 88.1408 | 88.1998 | 88.0291 | 90.0339 | 95.4584 | 100.2685 | 102.8608 |  |  | 27171 | 191.5197 | 167.4631 | 172.8073 | 174.1927 | 171.3536 | 171.2448 | 171.4974 | 172.2639 | 174.5456 | 181.7524 | 187.6376 | 191.5516 | [10 empty] | Sorell | Load transfer capacity (MVA)5
27172 | 0 | 77.5389 | 79.7339 | 79.4888 | 78.1499 | 77.2 | 77.2516 | 77.1021 | 78.8581 | 83.6093 | 87.8222 | 90.0927 |  |  | 27172 | 0 | 0 | 11.1208 | 11.21 | 11.0273 | 11.0203 | 11.0365 | 11.0859 | 11.2327 | 11.6965 | 12.0752 | 12.3271 | [10 empty] | St Leonards | Load transfer capacity (MVA)1 | Trevallyn | 3
27173 | 29.4375 | 26.4667 | 27.2159 | 27.1322 | 26.6752 | 26.351 | 26.3686 | 26.3176 | 26.9169 | 28.5387 | 29.9767 | 30.7517 |  |  | 27173 | 46.8616 | 42.0504 | 51.7207 | 52.1353 | 51.2856 | 51.253 | 51.3286 | 51.558 | 52.2409 | 54.3979 | 56.1593 | 57.3308 | [10 empty] | St Leonards | Load transfer capacity (MVA)2 | Mowbray | 3
27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | St Leonards | Load transfer capacity (MVA)3 | Norwood | 10
27175 | 102.2178 | 71.4278 | 73.4498 | 73.224 | 71.9906 | 71.1156 | 71.1631 | 71.0254 | 72.643 | 77.0197 | 80.9007 | 82.9922 |  |  | 27175 | 160.7896 | 132.7614 | 128.1818 | 129.2094 | 127.1035 | 127.0228 | 127.2101 | 127.7787 | 129.4712 | 134.8169 | 139.1823 | 142.0856 | [10 empty] | St Leonards | Load transfer capacity (MVA)4
27176 | 61 | 52.3222 | 53.8034 | 53.638 | 52.7345 | 52.0935 | 52.1283 | 52.0275 | 53.2124 | 56.4184 | 59.2613 | 60.7934 |  |  | 27176 | 85.3378 | 83.4599 | 80.5809 | 81.2269 | 79.903 | 79.8523 | 79.9701 | 80.3275 | 81.3915 | 84.7521 | 87.4964 | 89.3215 | [10 empty] | St Leonards | Load transfer capacity (MVA)5
27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | St Marys | Load transfer capacity (MVA)1 | Avoca | 2.8
27178 | 84.6088 | 66.7278 | 68.6167 | 68.4058 | 67.2536 | 66.4361 | 66.4805 | 66.3519 | 67.863 | 71.9518 | 75.5773 | 77.5313 |  |  | 27178 | 125.2791 | 114.3457 | 110.4014 | 111.2864 | 109.4726 | 109.4031 | 109.5645 | 110.0542 | 111.5119 | 116.1161 | 119.876 | 122.3766 | [10 empty] | St Marys | Load transfer capacity (MVA)2 | Triabunna | 4.5
28221 | 109.0672 | 95.0171 | 97.7069 | 97.4066 | 95.7659 | 94.6018 | 94.665 | 94.4819 | 96.6336 | 102.4558 | 107.6185 | 110.4008 |  |  | 28221 | 141.7562 | 159.5228 | 154.0201 | 155.2548 | 152.7244 | 152.6274 | 152.8525 | 153.5357 | 155.5694 | 161.9927 | 167.238 | 170.7265 | [10 empty] | St Marys | Load transfer capacity (MVA)3 | Derby | 4
28222 | 118.6208 | 103.4766 | 106.4058 | 106.0787 | 104.292 | 103.0243 | 103.0931 | 102.8937 | 105.237 | 111.5775 | 117.1998 | 120.2298 |  |  | 28222 | 193.2413 | 160.9836 | 155.4305 | 156.6766 | 154.123 | 154.0251 | 154.2523 | 154.9418 | 156.994 | 163.4762 | 168.7695 | 172.29 | [10 empty] | St Marys | Load transfer capacity (MVA)4
28223 | 193.9001 | 119.6371 | 123.0238 | 122.6456 | 120.5798 | 119.1141 | 119.1938 | 118.9632 | 121.6724 | 129.0032 | 135.5036 | 139.0068 |  |  | 28223 | 294.1039 | 272.0964 | 262.7105 | 264.8166 | 260.5004 | 260.335 | 260.719 | 261.8843 | 265.3531 | 276.3092 | 285.2562 | 291.2065 | [10 empty] | St Marys | Load transfer capacity (MVA)5
28224 | 85.9979 | 86.8494 | 89.308 | 89.0335 | 87.5338 | 86.4698 | 86.5276 | 86.3602 | 88.327 | 93.6487 | 98.3676 | 100.9107 |  |  | 28224 | 156.3631 | 136.0628 | 131.3694 | 132.4225 | 130.2642 | 130.1815 | 130.3735 | 130.9563 | 132.6908 | 138.1695 | 142.6434 | 145.6189 | [10 empty] | Trevallyn | Load transfer capacity (MVA)1 | George Town | 3.6
28225 | 5.3219 | 3.7724 | 3.8792 | 3.8672 | 3.8021 | 3.7559 | 3.7584 | 3.7511 | 3.8365 | 4.0677 | 4.2727 | 4.3831 |  |  | 28225 | 6.2242 | 4.6109 | 4.4519 | 4.4876 | 4.4144 | 4.4116 | 4.4181 | 4.4379 | 4.4967 | 4.6823 | 4.834 | 4.9348 | [10 empty] | Trevallyn | Load transfer capacity (MVA)2 | Mowbray | 36.1
28228 | 74.3183 | 68.7773 | 70.7243 | 70.5069 | 69.3193 | 68.4767 | 68.5225 | 68.3899 | 69.9474 | 74.1618 | 77.8987 | 79.9127 |  |  | 28228 | 134.7044 | 121.6737 | 117.4766 | 118.4184 | 116.4883 | 116.4143 | 116.586 | 117.1071 | 118.6583 | 123.5575 | 127.5584 | 130.2192 | [10 empty] | Trevallyn | Load transfer capacity (MVA)3 | Norwood | 21.7
28229 | 8.6528 | 5.9061 | 6.0733 | 6.0547 | 5.9527 | 5.8803 | 5.8843 | 5.8729 | 6.0066 | 6.3685 | 6.6894 | 6.8624 |  |  | 28229 | 14.3596 | 11.0102 | 10.6304 | 10.7156 | 10.541 | 10.5343 | 10.5498 | 10.597 | 10.7373 | 11.1807 | 11.5427 | 11.7835 | [10 empty] | Trevallyn | Load transfer capacity (MVA)4 | St Leonards | 21.7
28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Trevallyn | Load transfer capacity (MVA)5 | Hadspen | 14.4
28231 | 187.7746 | 152.0661 | 156.3708 | 155.8902 | 153.2644 | 151.4014 | 151.5026 | 151.2095 | 154.6532 | 163.9711 | 172.2334 | 176.6862 |  |  | 28231 | 290.6718 | 214.2061 | 206.8171 | 208.4751 | 205.0773 | 204.9471 | 205.2494 | 206.1667 | 208.8975 | 217.5227 | 224.5661 | 229.2504 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)1 | St Marys | 3
28232 | 121.429 | 98.5913 | 101.3822 | 101.0706 | 99.3682 | 98.1603 | 98.226 | 98.0359 | 100.2686 | 106.3098 | 111.6666 | 114.5536 |  |  | 28232 | 210.4711 | 214.1777 | 206.7897 | 208.4475 | 205.0501 | 204.9199 | 205.2221 | 206.1394 | 208.8698 | 217.4938 | 224.5363 | 229.22 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)2 | Sorell | 1.8
29481 | 45.7225 | 37.0556 | 38.1045 | 37.9874 | 37.3476 | 36.8936 | 36.9183 | 36.8468 | 37.686 | 39.9566 | 41.9699 | 43.055 |  |  | 29481 | 75.8819 | 74.2167 | 71.6566 | 72.231 | 71.0538 | 71.0087 | 71.1134 | 71.4312 | 72.3774 | 75.3658 | 77.8061 | 79.4291 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)3
29482 | 41.0992 | 39.2056 | 40.3154 | 40.1915 | 39.5145 | 39.0342 | 39.0603 | 38.9847 | 39.8726 | 42.2749 | 44.4051 | 45.5531 |  |  | 29482 | 43.3054 | 40.5394 | 39.141 | 39.4548 | 38.8118 | 38.7871 | 38.8443 | 39.018 | 39.5348 | 41.1671 | 42.5001 | 43.3867 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)4
29483 | 100.5926 | 70.3644 | 72.3563 | 72.1339 | 70.9189 | 70.0569 | 70.1037 | 69.9681 | 71.5616 | 75.8731 | 79.6963 | 81.7567 |  |  | 29483 | 174.8467 | 159.766 | 154.2549 | 155.4915 | 152.9573 | 152.8601 | 153.0856 | 153.7698 | 155.8066 | 162.2397 | 167.493 | 170.9869 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)5
29485 | 107.0333 | 86.2422 | 88.6836 | 88.411 | 86.9218 | 85.8653 | 85.9227 | 85.7564 | 87.7095 | 92.994 | 97.6798 | 100.2052 |  |  | 29485 | 104.9288 | 94.4227 | 91.1656 | 91.8964 | 90.3986 | 90.3413 | 90.4745 | 90.8789 | 92.0826 | 95.8846 | 98.9894 | 101.0542 | [10 empty] | Tungatinah | Load transfer capacity (MVA)1
29486 | 46.9998 | 40.0739 | 41.2083 | 41.0817 | 40.3897 | 39.8987 | 39.9254 | 39.8482 | 40.7557 | 43.2112 | 45.3886 | 46.562 |  |  | 29486 | 48.4838 | 50.9872 | 49.2284 | 49.6231 | 48.8143 | 48.7833 | 48.8553 | 49.0736 | 49.7236 | 51.7767 | 53.4532 | 54.5682 | [10 empty] | Tungatinah | Load transfer capacity (MVA)2
29488 | 203.4826 | 179.7184 | 184.8059 | 184.2379 | 181.1346 | 178.9329 | 179.0525 | 178.7061 | 182.776 | 193.7882 | 203.553 | 208.8155 |  |  | 29488 | 236.2038 | 218.3333 | 210.8019 | 212.4919 | 209.0286 | 208.8959 | 209.204 | 210.139 | 212.9224 | 221.7138 | 228.8929 | 233.6675 | [10 empty] | Tungatinah | Load transfer capacity (MVA)3
29489 | 97.9312 | 77.5628 | 79.7584 | 79.5133 | 78.174 | 77.2238 | 77.2754 | 77.1259 | 78.8824 | 83.635 | 87.8493 | 90.1205 |  |  | 29489 | 118.2906 | 109.703 | 105.9188 | 106.768 | 105.0278 | 104.9611 | 105.1159 | 105.5857 | 106.9843 | 111.4015 | 115.0087 | 117.4078 | [10 empty] | Tungatinah | Load transfer capacity (MVA)4
29490 | 47.9016 | 36.0911 | 37.1128 | 36.9987 | 36.3755 | 35.9334 | 35.9574 | 35.8878 | 36.7051 | 38.9166 | 40.8776 | 41.9344 |  |  | 29490 | 77.9099 | 74.135 | 71.5777 | 72.1515 | 70.9756 | 70.9305 | 71.0351 | 71.3526 | 72.2977 | 75.2828 | 77.7205 | 79.3417 | [10 empty] | Tungatinah | Load transfer capacity (MVA)5
29491 | 65.7782 | 67.8089 | 69.7284 | 69.5141 | 68.3432 | 67.5125 | 67.5576 | 67.4269 | 68.9625 | 73.1175 | 76.8018 | 78.7874 |  |  | 29491 | 78.3568 | 78.9131 | 76.191 | 76.8018 | 75.55 | 75.5021 | 75.6134 | 75.9514 | 76.9574 | 80.1349 | 82.7297 | 84.4554 | [10 empty] | Ulverstone | Load transfer capacity (MVA)1 | Burnie | 6.8
29492 | 3.0738 | 2.3852 | 2.4528 | 2.4452 | 2.404 | 2.3748 | 2.3764 | 2.3718 | 2.4258 | 2.572 | 2.7016 | 2.7714 |  |  | 29492 | 3.0716 | 2.3373 | 2.2566 | 2.2747 | 2.2377 | 2.2362 | 2.2395 | 2.2495 | 2.2793 | 2.3734 | 2.4503 | 2.5014 | [10 empty] | Ulverstone | Load transfer capacity (MVA)2 | Devonport | 10.3
30603 | 175.1 | 185.03 | 190.2679 | 189.6831 | 186.4881 | 184.2213 | 184.3444 | 183.9878 | 188.1779 | 199.5156 | 209.569 | 214.9871 |  |  | 30603 | 251.8704 | 263.52 | 254.4299 | 256.4696 | 252.2895 | 252.1294 | 252.5012 | 253.6298 | 256.9892 | 267.6001 | 276.265 | 282.0278 | [10 empty] | Ulverstone | Load transfer capacity (MVA)3 | Railton | 3.4
30604 | 254.8598 | 49.98 | 51.3948 | 51.2369 | 50.3738 | 49.7615 | 49.7948 | 49.6985 | 50.8303 | 53.8928 | 56.6084 | 58.072 |  |  | 30604 | 253.5363 | 265.5515 | 256.3914 | 258.4468 | 254.2345 | 254.0731 | 254.4478 | 255.5851 | 258.9704 | 269.6631 | 278.3948 | 284.202 | [10 empty] | Ulverstone | Load transfer capacity (MVA)4
30605 | 129.5265 | 214.52 | 220.5927 | 219.9147 | 216.2104 | 213.5824 | 213.7251 | 213.3117 | 218.1696 | 231.3144 | 242.9701 | 249.2517 |  |  | 30605 | 186.5098 | 220.94 | 213.3187 | 215.0289 | 211.5242 | 211.3899 | 211.7017 | 212.6479 | 215.4645 | 224.3608 | 231.6257 | 236.4573 | [10 empty] | Ulverstone | Load transfer capacity (MVA)5
30606 | 151.5887 | 162.31 | 166.9047 | 166.3917 | 163.589 | 161.6006 | 161.7086 | 161.3957 | 165.0714 | 175.0169 | 183.8359 | 188.5886 |  |  | 30606 | 174.4706 | 276.6206 | 267.0786 | 269.2197 | 264.8318 | 264.6637 | 265.054 | 266.2387 | 269.7652 | 280.9035 | 289.9992 | 296.0485 | [10 empty] | Waddamana | Load transfer capacity (MVA)1 | Arthurs Lake | 0.9
30607 | 104 | 86.0167 | 88.4516 | 88.1798 | 86.6945 | 85.6407 | 85.6979 | 85.5322 | 87.4801 | 92.7507 | 97.4244 | 99.9431 |  |  | 30607 | 172.3114 | 162.237 | 156.6407 | 157.8965 | 155.323 | 155.2244 | 155.4533 | 156.1481 | 158.2164 | 164.749 | 170.0836 | 173.6314 | [10 empty] | Waddamana | Load transfer capacity (MVA)2
30608 | 186.9 | 168.2167 | 172.9786 | 172.4469 | 169.5422 | 167.4814 | 167.5934 | 167.2691 | 171.0785 | 181.386 | 190.5259 | 195.4516 |  |  | 30608 | 172.4349 | 162.6246 | 157.0149 | 158.2737 | 155.694 | 155.5952 | 155.8247 | 156.5211 | 158.5943 | 165.1425 | 170.4899 | 174.0462 | [10 empty] | Waddamana | Load transfer capacity (MVA)3
31002 | 111.9187 | 123.6303 | 127.1301 | 126.7393 | 124.6045 | 123.09 | 123.1722 | 122.9339 | 125.7337 | 133.3091 | 140.0264 | 143.6466 |  |  | 31002 | 120.7585 | 119.6174 | 115.4912 | 116.4171 | 114.5197 | 114.447 | 114.6158 | 115.128 | 116.653 | 121.4694 | 125.4026 | 128.0185 | [10 empty] | Waddamana | Load transfer capacity (MVA)4
31007 | 92.6143 | 87.5585 | 90.0371 | 89.7604 | 88.2484 | 87.1758 | 87.234 | 87.0653 | 89.0481 | 94.4133 | 99.1706 | 101.7345 |  |  | 31007 | 135.5033 | 126.5291 | 122.1645 | 123.1439 | 121.1368 | 121.0599 | 121.2384 | 121.7803 | 123.3934 | 128.4881 | 132.6486 | 135.4156 | [10 empty] | Waddamana | Load transfer capacity (MVA)5
31008 | 123.897 | 118.6505 | 122.0093 | 121.6343 | 119.5855 | 118.1319 | 118.2109 | 117.9822 | 120.6691 | 127.9394 | 134.3862 | 137.8605 |  |  | 31008 | 157.8333 | 148.8228 | 143.6892 | 144.8411 | 142.4804 | 142.3899 | 142.6 | 143.2373 | 145.1346 | 151.127 | 156.0205 | 159.2751 | [10 empty] | Wayatinah | Load transfer capacity (MVA)1
31010 | 64.322 | 55.0896 | 56.6491 | 56.475 | 55.5237 | 54.8488 | 54.8855 | 54.7793 | 56.0269 | 59.4025 | 62.3957 | 64.0089 |  |  | 31010 | 81.2664 | 72.0579 | 69.5723 | 70.13 | 68.987 | 68.9432 | 69.0449 | 69.3535 | 70.2721 | 73.1736 | 75.5429 | 77.1187 | [10 empty] | Wayatinah | Load transfer capacity (MVA)2
32374 | 131.7144 | 106.6611 | 109.6805 | 109.3434 | 107.5016 | 106.1949 | 106.2659 | 106.0603 | 108.4757 | 115.0114 | 120.8067 | 123.93 |  |  | 32374 | 244.2669 | 214.1523 | 206.7651 | 208.4227 | 205.0257 | 204.8956 | 205.1978 | 206.1149 | 208.845 | 217.468 | 224.5096 | 229.1928 | [10 empty] | Wayatinah | Load transfer capacity (MVA)3
32377 | 118.7085 | 119.8167 | 123.2085 | 122.8298 | 120.7608 | 119.293 | 119.3727 | 119.1418 | 121.8551 | 129.1969 | 135.707 | 139.2155 |  |  | 32377 | 167.0216 | 151.5546 | 146.3267 | 147.4998 | 145.0957 | 145.0036 | 145.2175 | 145.8666 | 147.7986 | 153.9011 | 158.8844 | 162.1987 | [10 empty] | Wayatinah | Load transfer capacity (MVA)4
32379 | 155.8666 | 128.1722 | 131.8006 | 131.3955 | 129.1822 | 127.612 | 127.6973 | 127.4503 | 130.3528 | 138.2066 | 145.1707 | 148.9238 |  |  | 32379 | 278.1166 | 247.5286 | 250.111 | 252.1161 | 248.007 | 247.8495 | 248.2151 | 249.3245 | 252.6269 | 263.0576 | 271.5754 | 277.2404 | [10 empty] | Wayatinah | Load transfer capacity (MVA)5
33271 | 109.9648 | 95.0502 | 97.7409 | 97.4404 | 95.7992 | 94.6347 | 94.698 | 94.5148 | 96.6672 | 102.4914 | 107.6559 | 110.4392 |  |  | 33271 | 183.6586 | 158.62 | 153.1484 | 154.3762 | 151.8601 | 151.7637 | 151.9875 | 152.6668 | 154.689 | 161.0759 | 166.2916 | 169.7604 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)1
33272 | 154.9824 | 115.9582 | 119.2407 | 118.8742 | 116.8719 | 115.4513 | 115.5285 | 115.305 | 117.931 | 125.0363 | 131.3368 | 134.7323 |  |  | 33272 | 250.445 | 251.7421 | 243.0583 | 245.0069 | 241.0136 | 240.8606 | 241.2159 | 242.294 | 245.5033 | 255.6398 | 263.9175 | 269.4227 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)2
33273 | 18.085 | 1.0682 | 1.0984 | 1.0951 | 1.0766 | 1.0635 | 1.0642 | 1.0622 | 1.0864 | 1.1518 | 1.2099 | 1.2411 |  |  | 33273 | 16.6384 | 0.92103 | 0.88926 | 0.89638 | 0.88177 | 0.88122 | 0.88251 | 0.88646 | 0.8982 | 0.93529 | 0.96557 | 0.98571 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)3
33274 | 180.0703 | 144.4984 | 148.5889 | 148.1322 | 145.6371 | 143.8668 | 143.963 | 143.6845 | 146.9568 | 155.8109 | 163.6621 | 167.8933 |  |  | 33274 | 263.5225 | 238.6318 | 230.4003 | 232.2473 | 228.462 | 228.317 | 228.6537 | 229.6757 | 232.7179 | 242.3265 | 250.1731 | 255.3916 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)4
33275 | 8.0821 | 24.6159 | 25.3128 | 25.235 | 24.8099 | 24.5083 | 24.5247 | 24.4773 | 25.0347 | 26.5431 | 27.8805 | 28.6013 |  |  | 33275 | 12.1884 | 8.5077 | 8.2142 | 8.2801 | 8.1451 | 8.1399 | 8.1519 | 8.1884 | 8.2968 | 8.6394 | 8.9192 | 9.1052 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)5
33276 | 165.0645 | 130.2142 | 133.9003 | 133.4887 | 131.2403 | 129.645 | 129.7317 | 129.4807 | 132.4295 | 140.4084 | 147.4834 | 151.2963 |  |  | 33276 | 240.265 | 243.2399 | 234.8494 | 236.7321 | 232.8737 | 232.7259 | 233.0691 | 234.1109 | 237.2118 | 247.006 | 255.0041 | 260.3234 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)1 | Rokeby | 3.1
33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)2 | Howrah Zone | 3.1
34251 | 99.1984 | 64.6253 | 66.4547 | 66.2504 | 65.1345 | 64.3428 | 64.3858 | 64.2612 | 65.7247 | 69.6846 | 73.196 | 75.0883 |  |  | 34251 | 141.1249 | 121.4755 | 117.2852 | 118.2255 | 116.2986 | 116.2247 | 116.3962 | 116.9164 | 118.465 | 123.3563 | 127.3506 | 130.0071 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)3 | Cambridge Zone | 6.2
34252 | 184.5964 | 141.4125 | 145.4156 | 144.9687 | 142.5268 | 140.7944 | 140.8885 | 140.6159 | 143.8183 | 152.4834 | 160.1669 | 164.3077 |  |  | 34252 | 309.9776 | 254.0096 | 245.2476 | 247.2137 | 243.1845 | 243.0301 | 243.3885 | 244.4764 | 247.7145 | 257.9424 | 266.2946 | 271.8494 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)4 | Geilston Bay | 4.1
34253 | 88.5234 | 52.3083 | 53.789 | 53.6237 | 52.7205 | 52.0796 | 52.1145 | 52.0136 | 53.1982 | 56.4034 | 59.2455 | 60.7772 |  |  | 34253 | 149.7311 | 136.9163 | 132.1934 | 133.2532 | 131.0814 | 130.9981 | 131.1914 | 131.7777 | 133.5232 | 139.0362 | 143.5382 | 146.5324 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)5
34254 | 14.0706 | 6.7783 | 6.9702 | 6.9487 | 6.8317 | 6.7487 | 6.7532 | 6.7401 | 6.8936 | 7.3089 | 7.6772 | 7.8757 |  |  | 34254 | 19.5 | 14.1217 | 13.6346 | 37.5226 | 36.9111 | 36.8876 | 36.942 | 37.1072 | 37.5987 | 39.1511 | 40.4188 | 41.2619 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)1 | Rokeby | 7.4
34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34255 | 0 | 0 | 0 | 23.7787 | 23.3912 | 23.3763 | 23.4108 | 23.5154 | 23.8269 | 24.8107 | 25.6141 | 26.1484 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)2 | Bellerive | 7.4
34256 | 99.9951 | 78.0646 | 80.2744 | 80.0277 | 78.6797 | 77.7233 | 77.7753 | 77.6248 | 79.3927 | 84.1761 | 88.4176 | 90.7035 |  |  | 34256 | 174.4023 | 145.727 | 140.7001 | 165.6068 | 162.9077 | 162.8043 | 163.0444 | 163.7731 | 165.9424 | 172.794 | 178.3891 | 182.1102 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)3
34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34257 | 0 | 240.4115 | 232.1186 | 257.7582 | 253.5571 | 253.3961 | 253.7698 | 254.9041 | 258.2804 | 268.9445 | 277.653 | 283.4447 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)4
34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34258 | 0 | 78.4376 | 75.7319 | 76.339 | 75.0948 | 75.0471 | 75.1578 | 75.4937 | 76.4937 | 79.652 | 82.2312 | 83.9465 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)5
34259 | 164.3435 | 106.5485 | 109.5647 | 109.2279 | 107.3881 | 106.0828 | 106.1537 | 105.9483 | 108.3612 | 114.89 | 120.6792 | 123.7991 |  |  | 34259 | 294.5235 | 221.3235 | 213.689 | 215.4021 | 211.8914 | 211.7569 | 212.0692 | 213.017 | 215.8385 | 224.7503 | 232.0277 | 236.8677
34260 | 74.97 | 43.8161 | 45.0564 | 44.918 | 44.1614 | 43.6246 | 43.6537 | 43.5693 | 44.5615 | 47.2464 | 49.6271 | 50.9101 |  |  | 34260 | 109.9378 | 134.6064 | 129.9632 | 131.0051 | 128.8699 | 128.7881 | 128.978 | 129.5545 | 131.2705 | 136.6905 | 141.1166 | 144.0602
34261 | 76.9418 | 82.8719 | 85.2178 | 84.9559 | 83.5249 | 82.5096 | 82.5648 | 82.4051 | 84.2818 | 89.3597 | 93.8625 | 96.2892 |  |  | 34261 | 98.6893 | 125.7349 | 121.3977 | 122.371 | 120.3765 | 120.3001 | 120.4775 | 121.016 | 122.6189 | 127.6817 | 131.816 | 134.5657
34262 | 104.0471 | 80.4834 | 82.7618 | 82.5074 | 81.1177 | 80.1317 | 80.1852 | 80.0301 | 81.8527 | 86.7843 | 91.1573 | 93.514 |  |  | 34262 | 142.2183 | 170.8265 | 164.9339 | 166.2561 | 163.5464 | 163.4425 | 163.6836 | 164.4152 | 166.5929 | 173.4714 | 179.0884 | 182.8241
34263 | 90.6633 | 70.689 | 72.6901 | 72.4667 | 71.2461 | 70.3801 | 70.4271 | 70.2909 | 71.8917 | 76.2232 | 80.064 | 82.1339 |  |  | 34263 | 154.1723 | 186.3883 | 179.9589 | 181.4016 | 178.445 | 178.3317 | 178.5947 | 179.393 | 181.7691 | 189.2742 | 195.4029 | 199.4789
34264 | 162.9071 | 112.5586 | 115.7449 | 115.3891 | 113.4455 | 112.0666 | 112.1415 | 111.9245 | 114.4735 | 121.3706 | 127.4863 | 130.7822 |  |  | 34264 | 201.1108 | 168.2277 | 162.4247 | 163.7268 | 161.0583 | 160.9561 | 161.1935 | 161.9139 | 164.0585 | 170.8323 | 176.3639 | 180.0428 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)1
36240 | 124.4027 | -3.4968 | -3.5958 | -3.5847 | -3.5243 | -3.4815 | -3.4838 | -3.4771 | -3.5563 | -3.7705 | -3.9605 | -4.0629 |  |  | 36240 | 216.7573 | 182.8778 | 176.5695 | 177.985 | 175.0841 | 174.973 | 175.231 | 176.0142 | 178.3456 | 185.7093 | 191.7226 | 195.7219 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)2
37001 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 37001 | 25.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)3
37002 | 57.0015 | 56.1201 | 57.7088 | 57.5314 | 56.5623 | 194.8784 | 195.0086 | 194.6314 | 199.0639 | 211.0575 | 221.6925 | 227.424 |  |  | 37002 | 21.5428 | 22.3845 | 21.6124 | 21.7857 | 21.4306 | 21.417 | 21.4486 | 21.5444 | 21.8298 | 22.7311 | 23.4672 | 23.9567 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)4
38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)5
38423 | 110.4 | 10.1166 | 10.403 | 10.371 | 10.1963 | 10.0724 | 10.0791 | 10.0596 | 10.2887 | 10.9086 | 11.4583 | 11.7545 |  |  | 38423 | 105.234 | 36.1624 | 34.915 | 35.1949 | 34.6213 | 34.5993 | 34.6504 | 34.8052 | 35.2662 | 36.7223 | 37.9114 | 38.7022 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)1
39010 | 46.7 | 47.7011 | 49.0514 | 48.9006 | 48.0769 | 47.4926 | 47.5243 | 47.4324 | 48.5126 | 51.4355 | 54.0273 | 55.424 |  |  | 39010 | 82.43 | 77.2668 | 74.6015 | 75.1996 | 73.974 | 73.927 | 74.036 | 74.3669 | 75.352 | 78.4632 | 81.0038 | 82.6935 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)2
39011 | 47.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 39011 | 67.4223 | 0 | 28.3918 | 28.6194 | 28.153 | 28.1351 | 28.1766 | 28.3025 | 28.6774 | 29.8614 | 30.8284 | 31.4714 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)3
39012 | 56.6675 | 39.0518 | 40.1573 | 40.0338 | 39.3595 | 38.8811 | 38.9071 | 38.8318 | 39.7162 | 42.1091 | 44.2309 | 45.3744 |  |  | 39012 | 25.3897 | 68.6956 | 66.3259 | 66.8577 | 65.768 | 65.7262 | 65.8232 | 66.1174 | 66.9931 | 69.7592 | 72.018 | 73.5203 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)4
39013 | 56.6 | 53.7068 | 55.2271 | 55.0573 | 54.13 | 53.472 | 53.5077 | 53.4042 | 54.6205 | 57.9114 | 60.8294 | 62.4021 |  |  | 39013 | 25.3897 | 87.7717 | 84.744 | 85.4234 | 84.0311 | 83.9778 | 84.1017 | 84.4775 | 85.5965 | 89.1307 | 92.0167 | 93.9362 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)5
39564 | 10.5 | 10.5 | 10.7972 | 10.7641 | 10.5827 | 10.4541 | 10.4611 | 10.4409 | 10.6786 | 11.322 | 11.8925 | 12.2 |  |  | 39564 | 10.5 | 22.2191 | 49.8444 | 50.244 | 49.4251 | 49.3937 | 49.4666 | 49.6877 | 50.3458 | 52.4246 | 54.1221 | 55.251 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)1
39565 | 44.2728 | 89.8604 | 92.4042 | 92.1202 | 90.5685 | 89.4676 | 89.5275 | 89.3543 | 91.3892 | 96.8954 | 101.7779 | 104.4092 |  |  | 39565 | 69.8026 | 146.643 | 169.9764 | 171.339 | 168.5465 | 168.4395 | 168.6879 | 169.4419 | 171.6862 | 178.7749 | 184.5637 | 188.4136 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)2
39566 | 0 | 100.8856 | 103.7415 | 103.4226 | 101.6805 | 100.4446 | 100.5117 | 100.3173 | 102.6019 | 108.7837 | 114.2652 | 117.2193 |  |  | 39566 | 0 | 77.2325 | 102.9602 | 103.7856 | 102.094 | 102.0292 | 102.1797 | 102.6364 | 103.9959 | 108.2898 | 111.7962 | 114.1282 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)3
39568 | 25.8739 | 19.1166 | 19.6577 | 19.5973 | 19.2672 | 19.033 | 19.0457 | 19.0089 | 19.4418 | 20.6132 | 21.6518 | 22.2116 |  |  | 39568 | 28.1123 | 27.1526 | 26.216 | 26.4262 | 25.9955 | 25.979 | 26.0173 | 26.1336 | 26.4797 | 27.573 | 28.4659 | 29.0597 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)4
39569 | 23.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 39569 | 3.2 | 25.577 | 24.6947 | 24.8927 | 24.487 | 24.4714 | 24.5075 | 24.617 | 24.9431 | 25.973 | 26.814 | 27.3733 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)5
39570 | 124.2161 | 26.12 | 26.8594 | 26.7768 | 26.3258 | 26.0058 | 26.0232 | 25.9728 | 26.5644 | 28.1649 | 29.5841 | 30.3489 |  |  | 39570 | 102.1686 | 23.3293 | 22.5246 | 22.7051 | 22.3351 | 22.3209 | 22.3538 | 22.4537 | 22.7511 | 23.6905 | 24.4576 | 24.9678 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)1 | Bellerive | 5.1
39571 | 116.9 | 94.3841 | 97.0559 | 96.7576 | 95.1278 | 93.9715 | 94.0344 | 93.8524 | 95.9898 | 101.7732 | 106.9015 | 109.6652 |  |  | 39571 | 88.5671 | 58.0548 | 56.0522 | 56.5016 | 55.5807 | 55.5454 | 55.6274 | 55.876 | 56.6161 | 58.9537 | 60.8626 | 62.1322 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)2 | Derwent Park | 5.1
40001 | 27.2333 | 24.4617 | 25.1541 | 25.0768 | 24.6544 | 24.3547 | 24.371 | 24.3239 | 24.8778 | 26.3767 | 27.7058 | 28.4221 |  |  | 40001 | 36.8226 | 37.6015 | 36.3044 | 36.5955 | 35.999 | 35.9761 | 36.0292 | 36.1902 | 36.6696 | 38.1836 | 39.42 | 40.2423 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)3 | East Hobart | 3.8
40002 | 94.4 | 91.1811 | 93.7623 | 93.4741 | 91.8996 | 90.7826 | 90.8433 | 90.6675 | 92.7324 | 98.3195 | 103.2737 | 105.9437 |  |  | 40002 | 122.4163 | 127.4894 | 123.0917 | 124.0785 | 122.0562 | 121.9787 | 122.1586 | 122.7046 | 124.3299 | 129.4633 | 133.6554 | 136.4434 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)4
40003 | 40.1667 | 36.8133 | 37.8555 | 37.7391 | 37.1034 | 36.6524 | 36.6769 | 36.606 | 37.4396 | 39.6954 | 41.6956 | 42.7736 |  |  | 40003 | 46.1729 | 69.2368 | 66.8485 | 67.3844 | 66.2861 | 66.2441 | 66.3418 | 66.6383 | 67.5209 | 70.3088 | 72.5854 | 74.0995 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)5
41511 | 80.3889 | 75.9745 | 78.1252 | 77.885 | 76.5731 | 75.6424 | 75.6929 | 75.5465 | 77.267 | 81.9224 | 86.0503 | 88.275 |  |  | 41511 | 135.2786 | 138.2652 | 133.4958 | 134.566 | 132.3727 | 132.2887 | 132.4838 | 133.076 | 134.8386 | 140.406 | 144.9523 | 147.976 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)1
41512 | 92.3436 | 98.4881 | 101.2761 | 100.9648 | 99.2642 | 98.0576 | 98.1232 | 97.9333 | 100.1637 | 106.1985 | 111.5498 | 114.4337 |  |  | 41512 | 140.7368 | 141.8005 | 136.9091 | 138.0067 | 135.7574 | 135.6712 | 135.8713 | 136.4786 | 138.2863 | 143.996 | 148.6586 | 151.7596 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)2
41513 | 107.9511 | 104.658 | 107.6207 | 107.2899 | 105.4827 | 104.2005 | 104.2702 | 104.0685 | 106.4385 | 112.8515 | 118.5379 | 121.6026 |  |  | 41513 | 154.3066 | 148.7919 | 143.6593 | 144.811 | 142.4508 | 142.3604 | 142.5703 | 143.2076 | 145.1044 | 151.0956 | 155.9881 | 159.242 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)3
41514 | 59.7655 | 64.2108 | 66.0285 | 65.8256 | 64.7168 | 63.9302 | 63.9729 | 63.8491 | 65.3032 | 69.2378 | 72.7266 | 74.6068 |  |  | 41514 | 74.2285 | 70.8317 | 68.3884 | 68.9366 | 67.8131 | 67.77 | 67.87 | 68.1733 | 69.0763 | 71.9284 | 74.2574 | 75.8064 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)4
41515 | 98.3201 | 63.1698 | 64.958 | 64.7584 | 63.6676 | 62.8937 | 62.9357 | 62.814 | 64.2445 | 68.1152 | 71.5475 | 73.3972 |  |  | 41515 | 144.8894 | 133.7438 | 129.1303 | 130.1655 | 128.044 | 127.9627 | 128.1515 | 128.7243 | 130.4293 | 135.8146 | 140.2123 | 143.137 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)5
41516 | 118.869 | 97.5486 | 100.3101 | 100.0018 | 98.3173 | 97.1223 | 97.1872 | 96.9992 | 99.2082 | 105.1855 | 110.4857 | 113.3422 |  |  | 41516 | 150.6998 | 152.2041 | 146.9539 | 148.132 | 145.7176 | 145.6251 | 145.8399 | 146.4917 | 148.4321 | 154.5607 | 159.5654 | 162.8939 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)1 | Rokeby | 7.1
41517 | 86.5886 | 80.8038 | 83.0912 | 82.8358 | 81.4406 | 80.4506 | 80.5044 | 80.3487 | 82.1785 | 87.1298 | 91.5202 | 93.8863 |  |  | 41517 | 124.9496 | 128.0712 | 123.6534 | 124.6447 | 122.6132 | 122.5353 | 122.716 | 123.2645 | 124.8972 | 130.0541 | 134.2653 | 137.066 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)2 | Bellerive | 2.4
41518 | 121.8409 | 81.3806 | 83.6844 | 83.4272 | 82.0219 | 81.0249 | 81.0791 | 80.9222 | 82.7652 | 87.7518 | 92.1735 | 94.5565 |  |  | 41518 | 134.8525 | 147.236 | 142.1571 | 143.2968 | 140.9612 | 140.8717 | 141.0795 | 141.7101 | 143.5871 | 149.5156 | 154.357 | 157.5768 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)3
43505 | 18.6578 | 15.9255 | 16.3763 | 16.326 | 16.051 | 15.8559 | 15.8665 | 15.8358 | 16.1964 | 17.1723 | 18.0376 | 18.5039 |  |  | 43505 | 22.0987 | 20.4094 | 19.7054 | 19.8634 | 19.5396 | 19.5272 | 19.556 | 19.6434 | 19.9036 | 20.7254 | 21.3965 | 21.8428 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)4
43506 | 50.254 | 49.3526 | 50.7497 | 50.5937 | 49.7415 | 49.1369 | 49.1697 | 49.0746 | 50.1922 | 53.2163 | 55.8979 | 57.343 |  |  | 43506 | 64.1092 | 69.7037 | 67.2993 | 67.8388 | 66.7331 | 66.6908 | 66.7891 | 67.0877 | 67.9763 | 70.7829 | 73.0749 | 74.5992 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)5
43507 | 80.0239 | 70.8675 | 72.8737 | 72.6497 | 71.426 | 70.5578 | 70.6049 | 70.4683 | 72.0732 | 76.4156 | 80.2661 | 82.3413 |  |  | 43507 | 85.8024 | 105.471 | 101.8328 | 102.6492 | 100.9761 | 100.912 | 101.0609 | 101.5126 | 102.8571 | 107.104 | 110.572 | 112.8785 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)1
45001 | 79 | 75.8989 | 78.0475 | 77.8076 | 76.497 | 75.5671 | 75.6177 | 75.4714 | 77.1902 | 81.8409 | 85.9647 | 88.1872 |  |  | 45001 | 25.903 | 30.741 | 29.6806 | 29.9186 | 29.4309 | 29.4122 | 29.4556 | 29.5873 | 29.9792 | 31.217 | 32.2278 | 32.9 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)2
45002 | 75 | 73.9619 | 76.0557 | 75.8219 | 74.5448 | 73.6387 | 73.6879 | 73.5453 | 75.2203 | 79.7523 | 83.7709 | 85.9367 |  |  | 45002 | 65 | 61.3288 | 59.2132 | 59.6879 | 58.7151 | 58.6778 | 58.7644 | 59.027 | 59.8089 | 62.2783 | 64.2949 | 65.6361 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)3
45003 | 113 | 133.4913 | 137.2702 | 136.8483 | 134.5432 | 132.9078 | 132.9967 | 132.7394 | 135.7624 | 143.9421 | 151.1952 | 155.1041 |  |  | 45003 | 77.2605 | 38.3055 | 36.9842 | 37.2807 | 36.6731 | 36.6498 | 36.7038 | 36.8679 | 37.3562 | 38.8986 | 40.1582 | 40.9958 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)4
48180 | 124.3 | 117.2939 | 120.6142 | 120.2435 | 118.2182 | 116.7812 | 116.8592 | 116.6332 | 119.2894 | 126.4766 | 132.8496 | 136.2842 |  |  | 48180 | 208.2274 | 206.533 | 199.4087 | 201.0073 | 197.7312 | 197.6056 | 197.8971 | 198.7816 | 201.4146 | 209.7308 | 216.5219 | 221.0384 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)5
48181 | 163.6949 | 99.7293 | 102.5525 | 102.2373 | 100.5152 | 99.2934 | 99.3598 | 99.1676 | 101.426 | 107.537 | 112.9556 | 115.8759 |  |  | 48181 | 184.4887 | 149.5241 | 144.3663 | 145.5236 | 143.1518 | 143.0609 | 143.2719 | 143.9123 | 145.8185 | 151.8391 | 156.7557 | 160.0256 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)1
48182 | 202.5772 | 153.6159 | 157.9645 | 157.479 | 154.8264 | 152.9444 | 153.0467 | 152.7506 | 156.2294 | 165.6422 | 173.9887 | 178.4869 |  |  | 48182 | 288.3237 | 259.0954 | 250.158 | 252.1634 | 248.0535 | 247.896 | 248.2617 | 249.3713 | 252.6743 | 263.107 | 271.6264 | 277.2924 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)2
48183 | 185.9309 | 141.071 | 145.0644 | 144.6186 | 142.1826 | 140.4544 | 140.5483 | 140.2763 | 143.471 | 152.1152 | 159.7801 | 163.9109 |  |  | 48183 | 210.2484 | 169.8464 | 163.9876 | 165.3022 | 162.608 | 162.5048 | 162.7445 | 163.4719 | 165.6371 | 172.4761 | 178.0609 | 181.7752 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)3
48184 | 145.7 | 146.7094 | 150.8625 | 150.3988 | 147.8655 | 146.0681 | 146.1658 | 145.883 | 149.2054 | 158.195 | 166.1663 | 170.4622 |  |  | 48184 | 237.8522 | 227.6337 | 219.7815 | 221.5435 | 217.9326 | 217.7943 | 218.1155 | 219.0904 | 221.9923 | 231.1582 | 238.6431 | 243.6211 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)4
48185 | 148.3 | 126.6714 | 130.2573 | 129.8569 | 127.6696 | 126.1178 | 126.2021 | 125.9579 | 128.8265 | 136.5883 | 143.4709 | 147.1801 |  |  | 48185 | 202.3419 | 199.0112 | 192.1464 | 193.6868 | 190.53 | 190.409 | 190.6898 | 191.5421 | 194.0792 | 202.0925 | 208.6363 | 212.9884 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)5
48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)1
48188 | 72.9 | 116.4254 | 119.7212 | 119.3533 | 117.3429 | 115.9166 | 115.994 | 115.7696 | 118.4062 | 125.5402 | 131.866 | 135.2752 |  |  | 48188 | 114.2934 | 109.2999 | 105.5297 | 106.3757 | 104.6419 | 104.5755 | 104.7297 | 105.1978 | 106.5912 | 110.9922 | 114.5862 | 116.9764 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)2
48189 | 64.7 | 64.5506 | 66.3779 | 152.0487 | 149.4876 | 147.6705 | 147.7693 | 147.4834 | 150.8422 | 159.9304 | 167.9892 | 172.3322 |  |  | 48189 | 110.5112 | 113.965 | 110.0338 | 110.9159 | 109.1082 | 109.0389 | 109.1997 | 109.6878 | 111.1407 | 115.7295 | 119.4769 | 121.9691 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)3
48190 | 184.3 | 169.3194 | 174.1125 | 259.4522 | 255.082 | 251.9814 | 252.1499 | 251.6621 | 257.3935 | 272.9014 | 286.6526 | 294.0636 |  |  | 48190 | 204.3616 | 183.1977 | 176.8783 | 178.2963 | 175.3904 | 175.279 | 175.5375 | 176.3221 | 178.6576 | 186.0342 | 192.058 | 196.0642 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)4
48191 | 53.4 | 47.8837 | 49.2392 | 134.9627 | 132.6894 | 131.0765 | 131.1642 | 130.9104 | 133.8918 | 141.9588 | 149.1119 | 152.967 |  |  | 48191 | 74.3083 | 68.5655 | 66.2003 | 66.7311 | 65.6434 | 65.6018 | 65.6985 | 65.9922 | 66.8663 | 69.6271 | 71.8816 | 73.3811 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)5
48192 | 140.8 | 141.1749 | 145.1713 | 230.6 | 226.7157 | 223.96 | 224.1097 | 223.6761 | 228.7701 | 242.5535 | 254.7756 | 261.3624 |  |  | 48192 | 241.7905 | 225.0046 | 217.2431 | 218.9847 | 215.4156 | 215.2788 | 215.5963 | 216.5599 | 219.4284 | 228.4883 | 235.8868 | 240.8073 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)1
48193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 48193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)2
49101 | 35 | 39.9716 | 41.1032 | 40.9768 | 40.2866 | 39.7969 | 39.8235 | 39.7465 | 40.6517 | 43.1009 | 45.2728 | 46.4432 |  |  | 49101 | 35 | 32.6333 | 31.5077 | 31.7602 | 31.2426 | 31.2228 | 31.2688 | 31.4086 | 31.8246 | 33.1386 | 34.2116 | 34.9253 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)3
49202 | 16.6212 | 12.0526 | 12.3938 | 12.3557 | 12.1476 | 11.9999 | 12.0079 | 11.9847 | 12.2577 | 12.9962 | 13.651 | 14.004 |  |  | 49202 | 18.9205 | 18.847 | 18.1969 | 18.3428 | 18.0438 | 18.0323 | 18.0589 | 18.1396 | 18.3799 | 19.1388 | 19.7585 | 20.1707 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)4
49302 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 49302 | 8.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)5
49303 | 22.4857 | 5.8411 | 6.0065 | 5.988 | 5.8871 | 5.8156 | 5.8195 | 5.8082 | 5.9405 | 6.2984 | 6.6158 | 6.7868 |  |  | 49303 | 24 | 14.2111 | 13.7209 | 13.8309 | 13.6055 | 13.5968 | 13.6169 | 13.6778 | 13.8589 | 14.4311 | 14.8984 | 15.2092 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)1 | Kingston | 4.9
49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)2
49307 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 49307 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)3
49411 | 16.9754 | 10.7678 | 11.0726 | 11.0386 | 10.8526 | 10.7207 | 10.7279 | 10.7071 | 10.951 | 11.6108 | 12.1958 | 12.5111 |  |  | 49411 | 18 | 11.6242 | 11.2233 | 11.3132 | 11.1289 | 11.1218 | 11.1382 | 11.188 | 11.3362 | 11.8042 | 12.1864 | 12.4407 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)4
49412 | 33 | 27.8286 | 28.6164 | 28.5284 | 28.0479 | 27.707 | 27.7255 | 27.6719 | 28.3021 | 30.0073 | 31.5193 | 32.3342 |  |  | 49412 | 30 | 17.4378 | 16.8363 | 16.9712 | 16.6946 | 16.684 | 16.7086 | 16.7833 | 17.0056 | 17.7078 | 18.2811 | 18.6625 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)5
49621 | 0.34614 | 0.26068 | 0.26806 | 0.26724 | 0.26274 | 0.25954 | 0.25972 | 0.25922 | 0.26512 | 0.28109 | 0.29526 | 0.30289 |  |  | 49621 | 0.41245 | 0.34369 | 0.33184 | 0.3345 | 0.32904 | 0.32884 | 0.32932 | 0.33079 | 0.33517 | 0.34901 | 0.36031 | 0.36783 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)1
49801 | 11.7503 | 5.7404 | 5.9029 | 5.8848 | 5.7856 | 5.7153 | 5.7191 | 5.7081 | 5.8381 | 6.1898 | 6.5017 | 6.6698 |  |  | 49801 | 15.5568 | 8.5152 | 8.2215 | 8.2874 | 8.1523 | 8.1471 | 8.1591 | 8.1956 | 8.3042 | 8.647 | 8.927 | 9.1132 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)2
51001 | 27.9015 | 0.19278 | 0.19824 | 0.19763 | 0.1943 | 0.19194 | 0.19207 | 0.1917 | 0.19606 | 0.20788 | 0.21835 | 0.224 |  |  | 51001 | 30.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)3
51002 | 9.2224 | 0.10942 | 0.11252 | 0.11217 | 0.11028 | 0.10894 | 0.10901 | 0.1088 | 0.11128 | 0.11798 | 0.12393 | 0.12713 |  |  | 51002 | 8.2845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)4
51003 | 272.9973 | 211.4144 | 217.3992 | 216.731 | 213.0804 | 210.4903 | 210.6311 | 210.2236 | 215.0112 | 227.9657 | 239.4526 | 245.6433 |  |  | 51003 | 206.018 | 107.1187 | 103.4236 | 104.2528 | 102.5536 | 102.4885 | 102.6396 | 103.0984 | 104.464 | 108.7772 | 112.2994 | 114.6419 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)5
51004 | 96.6002 | 198.558 | 204.1789 | 203.5513 | 200.1227 | 197.6902 | 197.8223 | 197.4396 | 201.9361 | 214.1028 | 224.8912 | 230.7054 |  |  | 51004 | 38.3974 | 83.9625 | 81.0662 | 81.7161 | 80.3843 | 80.3332 | 80.4517 | 80.8113 | 81.8817 | 85.2625 | 88.0233 | 89.8594 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)1
53001 | 90.8942 | 78.6392 | 80.8653 | 80.6168 | 79.2589 | 78.2954 | 78.3478 | 78.1962 | 79.9771 | 84.7957 | 89.0684 | 91.3712 |  |  | 53001 | 119.2912 | 113.8746 | 109.9465 | 110.828 | 109.0216 | 108.9524 | 109.1131 | 109.6008 | 111.0525 | 115.6378 | 119.3821 | 121.8724 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)2
53002 | 144.5577 | 8.6803 | 8.9261 | 8.8986 | 8.7487 | 8.6424 | 8.6482 | 8.6314 | 8.828 | 9.3599 | 9.8315 | 10.0857 |  |  | 53002 | 166.7577 | 7.2056 | 6.957 | 7.0128 | 6.8985 | 6.8941 | 6.9043 | 6.9351 | 7.027 | 7.3171 | 7.554 | 7.7116 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)3
53003 | 88.8974 | 117.3986 | 120.722 | 120.3509 | 118.3237 | 116.8855 | 116.9636 | 116.7373 | 119.3959 | 126.5895 | 132.9682 | 136.4059 |  |  | 53003 | 149.7026 | 143.9946 | 139.0275 | 140.1421 | 137.858 | 137.7705 | 137.9737 | 138.5903 | 140.426 | 146.2241 | 150.9588 | 154.1078 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)4
53004 | 43.0165 | 37.6633 | 38.7295 | 38.6105 | 37.9601 | 37.4987 | 37.5238 | 37.4512 | 38.3041 | 40.6119 | 42.6583 | 43.7612 |  |  | 53004 | 56.8138 | 55.2125 | 53.308 | 53.7353 | 52.8595 | 52.826 | 52.9039 | 53.1403 | 53.8442 | 56.0674 | 57.8829 | 59.0903 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)5
53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53006 | 0 | 0 | 0 | 31.6878 | 31.1541 | 30.7754 | 30.796 | 30.7364 | 31.4364 | 33.3304 | 35.0099 | 35.915 |  |  | 53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53007 | 0 | 0 | 0 | 31.6878 | 31.1541 | 30.7754 | 30.796 | 30.7364 | 31.4364 | 33.3304 | 35.0099 | 35.915 |  |  | 53007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53008 | 64 | 49.7031 | 51.1101 | 82.6408 | 81.2488 | 80.2612 | 80.3148 | 80.1595 | 81.985 | 86.9246 | 91.3047 | 93.6652 |  |  | 53008 | 68.7223 | 68.4755 | 66.1134 | 66.6434 | 65.5572 | 65.5156 | 65.6123 | 65.9055 | 66.7785 | 69.5357 | 71.7872 | 73.2847
53009 | 79 | 52.5744 | 54.0627 | 85.5844 | 84.1428 | 83.12 | 83.1756 | 83.0147 | 84.9053 | 90.0208 | 94.5569 | 97.0015 |  |  | 53009 | 102.3811 | 122.8423 | 118.6049 | 119.5558 | 117.6072 | 117.5325 | 117.7058 | 118.2319 | 119.798 | 124.7443 | 128.7836 | 131.4699
53010 | 187.6723 | 24.7711 | 25.4723 | 25.394 | 24.9663 | 24.6628 | 24.6793 | 24.6316 | 25.1925 | 26.7104 | 28.0563 | 28.7816 |  |  | 53010 | 242.744 | 34.3062 | 33.1228 | 33.3884 | 32.8442 | 32.8233 | 32.8717 | 33.0187 | 33.456 | 34.8374 | 35.9654 | 36.7156
54003 | 168.3333 | 168.5444 | 173.3156 | 172.7829 | 169.8726 | 167.8078 | 167.9199 | 167.5951 | 171.4119 | 181.7395 | 190.8971 | 195.8325 |  |  | 54003 | 137.0581 | 127.1276 | 122.7424 | 123.7264 | 121.7098 | 121.6326 | 121.812 | 122.3564 | 123.9771 | 129.096 | 133.2761 | 136.0562
54004 | 22.4171 | 1.1318 | 1.1638 | 1.1602 | 1.1407 | 1.1268 | 1.1276 | 1.1254 | 1.151 | 1.2204 | 1.2819 | 1.315 |  |  | 54004 | 22.388 | 1.2287 | 1.1863 | 1.1958 | 1.1763 | 1.1756 | 1.1773 | 1.1826 | 1.1982 | 1.2477 | 1.2881 | 1.315
54005 | 84.6667 | 80.6209 | 82.9031 | 82.6483 | 81.2562 | 80.2685 | 80.3221 | 80.1667 | 81.9925 | 86.9325 | 91.313 | 93.6737 |  |  | 54005 | 104.9999 | 86.4728 | 83.49 | 84.1593 | 82.7876 | 82.7351 | 82.8571 | 83.2274 | 84.3298 | 87.8117 | 90.6551 | 92.5461
54006 | 9.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 54006 | 6.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54007 | 69.5314 | 49.6833 | 51.0898 | 50.9328 | 50.0748 | 49.4662 | 49.4992 | 49.4035 | 50.5286 | 53.5729 | 56.2724 | 57.7273 |  |  | 54007 | 105.9316 | 97.8129 | 94.4389 | 95.196 | 93.6444 | 93.585 | 93.723 | 94.1419 | 95.3889 | 99.3274 | 102.5436 | 104.6826
55001 | 108.3333 | 116.1998 | 119.4892 | 119.122 | 117.1155 | 115.6919 | 115.7692 | 115.5453 | 118.1767 | 125.2969 | 131.6104 | 135.013 |  |  | 55001 | 78.466 | 36.9167 | 35.6432 | 35.929 | 35.3434 | 35.3209 | 35.373 | 35.5311 | 36.0018 | 37.4882 | 38.7021 | 39.5094
55002 | 119.3333 | 45.6461 | 46.9383 | 46.794 | 46.0058 | 45.4466 | 45.477 | 45.389 | 46.4227 | 49.2196 | 51.6998 | 53.0364 |  |  | 55002 | 115.7967 | 33.0036 | 31.8651 | 32.1206 | 31.5971 | 31.577 | 31.6236 | 31.7649 | 32.1857 | 33.5146 | 34.5998 | 35.3215
55003 | 32.3333 | 36.245 | 37.271 | 37.1564 | 36.5306 | 36.0865 | 36.1107 | 36.0408 | 36.8616 | 39.0825 | 41.0519 | 42.1132 |  |  | 55003 | 17.2372 | 16.1297 | 15.5733 | 15.6981 | 15.4423 | 15.4325 | 15.4552 | 15.5243 | 15.7299 | 16.3794 | 16.9098 | 17.2625
56001 | 10.0837 | 8.5067 | 8.7475 | 8.7206 | 8.5737 | 147.473 | 147.5716 | 147.2861 | 150.6404 | 159.7165 | 167.7645 | 172.1018 |  |  | 56001 | 8 | 0.44444 | 0.42911 | 0.43255 | 0.4255 | 0.42523 | 0.42586 | 0.42776 | 0.43343 | 0.45133 | 0.46594 | 0.47566
56002 | 0 | 0 | 0 | 0 | 0 | 139.0036 | 139.0965 | 138.8274 | 141.989 | 150.5439 | 158.1296 | 162.2178 |  |  | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56003 | 54.065 | 42.1291 | 43.3217 | 43.1885 | 42.4611 | 180.9485 | 181.0694 | 180.7191 | 184.8349 | 195.9712 | 205.846 | 211.1678 |  |  | 56003 | 55.1 | 44.3485 | 42.8187 | 43.162 | 42.4585 | 42.4316 | 42.4941 | 42.6841 | 43.2494 | 45.0352 | 46.4934 | 47.4632
56004 | 225.7164 | 184.2983 | 189.5155 | 188.933 | 185.7506 | 183.4928 | 183.6154 | 183.2602 | 187.4338 | 198.7267 | 208.7403 | 214.137 |  |  | 56004 | 135 | 130.0992 | 125.6114 | 126.6184 | 124.5547 | 124.4756 | 124.6592 | 125.2164 | 126.875 | 132.1135 | 136.3913 | 139.2364
57003 | 32.0028 | 23.1705 | 23.8264 | 23.7532 | 23.3531 | 23.0692 | 23.0846 | 23.04 | 23.5647 | 24.9844 | 26.2434 | 26.9219 |  |  | 57003 | 42.6117 | 43.9125 | 42.3977 | 42.7376 | 42.041 | 42.0143 | 42.0763 | 42.2644 | 42.8242 | 44.5924 | 46.0363 | 46.9966
57004 | 143.7525 | 114.9569 | 118.2112 | 117.8478 | 115.8628 | 114.4545 | 114.531 | 114.3094 | 116.9127 | 123.9567 | 130.2028 | 133.5689 |  |  | 57004 | 170.333 | 185.616 | 179.2132 | 180.6499 | 177.7056 | 177.5928 | 177.8547 | 178.6496 | 181.0159 | 188.4899 | 194.5932 | 198.6524
57005 | 84.1718 | 38.5408 | 39.6319 | 39.51 | 38.8445 | 38.3724 | 38.398 | 38.3237 | 39.1965 | 41.5581 | 43.6522 | 44.7807 |  |  | 57005 | 88.0837 | 38.3033 | 36.9821 | 37.2785 | 36.671 | 36.6477 | 36.7017 | 36.8658 | 37.3541 | 38.8964 | 40.1559 | 40.9935
57006 | 150.9674 | 124.7867 | 128.3192 | 127.9248 | 125.77 | 124.2412 | 124.3243 | 124.0838 | 126.9097 | 134.556 | 141.3361 | 144.9901 |  |  | 57006 | 246.5482 | 221.2574 | 213.6251 | 215.3377 | 211.828 | 211.6935 | 212.0058 | 212.9533 | 215.774 | 224.6831 | 231.9584 | 236.7969
61021 | 145.1766 | 82.9278 | 85.2753 | 85.0132 | 83.5813 | 82.5653 | 82.6205 | 82.4607 | 84.3386 | 89.42 | 93.9258 | 96.3541 |  |  | 61021 | 165.7615 | 171.9961 | 166.0631 | 167.3944 | 164.6661 | 164.5616 | 164.8043 | 165.5409 | 167.7336 | 174.6591 | 180.3146 | 184.0759
61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61023 | 89.5006 | 76.0889 | 78.2428 | 78.0023 | 76.6885 | 75.7563 | 75.807 | 75.6603 | 77.3834 | 82.0457 | 86.1799 | 88.408 |  |  | 61023 | 142.9073 | 147.1571 | 142.081 | 143.22 | 140.8857 | 140.7963 | 141.0039 | 141.6342 | 143.5102 | 149.4355 | 154.2743 | 157.4924
61024 | 130.8243 | 116.9089 | 120.2184 | 119.8489 | 117.8301 | 116.3979 | 116.4757 | 116.2504 | 118.8979 | 126.0615 | 132.4136 | 135.8369 |  |  | 61024 | 170.8388 | 173.1832 | 167.2092 | 168.5497 | 165.8026 | 165.6973 | 165.9417 | 166.6834 | 168.8912 | 175.8645 | 181.5591 | 185.3463
61025 | 82.8894 | 73.8944 | 75.9863 | 75.7527 | 74.4767 | 73.5715 | 73.6206 | 73.4782 | 75.1516 | 79.6795 | 83.6945 | 85.8583 |  |  | 61025 | 188.4667 | 242.3731 | 234.0125 | 235.8885 | 232.0438 | 231.8965 | 232.2386 | 233.2766 | 236.3664 | 246.1257 | 254.0953 | 259.3957
61026 | 112.6667 | 137.5833 | 141.4781 | 141.0432 | 138.6675 | 136.982 | 137.0735 | 136.8084 | 139.924 | 148.3545 | 155.8299 | 159.8586 |  |  | 61026 | 107.7927 | 105.8396 | 102.1887 | 103.0079 | 101.329 | 101.2647 | 101.414 | 101.8673 | 103.2166 | 107.4783 | 110.9585 | 113.273
61027 | 103.2996 | 85.9444 | 88.3774 | 88.1057 | 86.6217 | 85.5688 | 85.626 | 85.4603 | 87.4066 | 92.6729 | 97.3426 | 99.8592 |  |  | 61027 | 205.2516 | 206.3477 | 199.2297 | 200.8269 | 197.5537 | 197.4283 | 197.7195 | 198.6032 | 201.2338 | 209.5425 | 216.3276 | 220.8401
61028 | 118.9476 | 95.8667 | 98.5805 | 98.2775 | 96.6221 | 95.4476 | 95.5114 | 95.3267 | 97.4976 | 103.3719 | 108.5807 | 111.3879 |  |  | 61028 | 209.758 | 205.9434 | 198.8394 | 200.4335 | 197.1667 | 197.0415 | 197.3322 | 198.2141 | 200.8396 | 209.132 | 215.9038 | 220.4074
61029 | 58.2779 | 52.5722 | 54.0605 | 53.8943 | 52.9865 | 52.3424 | 52.3774 | 52.2761 | 53.4666 | 56.688 | 59.5445 | 61.0839 |  |  | 61029 | 115.7946 | 124.7869 | 120.4824 | 121.4483 | 119.4688 | 119.393 | 119.5691 | 120.1035 | 121.6943 | 126.719 | 130.8222 | 133.5511
61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61037 | 66.3904 | 48.9167 | 50.3014 | 50.1468 | 49.3021 | 48.7029 | 48.7354 | 48.6411 | 49.7489 | 52.7463 | 55.4041 | 56.8365 |  |  | 61037 | 88.1399 | 89.8222 | 86.7238 | 87.4191 | 85.9943 | 85.9397 | 86.0664 | 86.4511 | 87.5962 | 91.2129 | 94.1664 | 96.1307
61039 | 127.3687 | 114.1483 | 117.3797 | 117.0189 | 115.0478 | 113.6494 | 113.7254 | 113.5054 | 116.0903 | 123.0848 | 129.2869 | 132.6294 |  |  | 61039 | 162.0643 | 244.3646 | 235.9353 | 237.8267 | 233.9505 | 233.8019 | 234.1468 | 235.1933 | 238.3086 | 248.1481 | 256.1831 | 261.527
61040 | 115.8896 | 103.6 | 106.5327 | 106.2053 | 104.4164 | 103.1472 | 103.2161 | 103.0164 | 105.3626 | 111.7106 | 117.3396 | 120.3733 |  |  | 61040 | 185.6106 | 198.4119 | 191.5677 | 193.1035 | 189.9562 | 189.8356 | 190.1156 | 190.9653 | 193.4947 | 201.4839 | 208.008 | 212.347
61041 | 75.5885 | 65.9944 | 67.8626 | 67.654 | 66.5145 | 65.706 | 65.7499 | 65.6227 | 67.1172 | 71.161 | 74.7468 | 76.6792 |  |  | 61041 | 151.0027 | 155.0923 | 149.7424 | 150.9429 | 148.4827 | 148.3884 | 148.6073 | 149.2715 | 151.2487 | 157.4936 | 162.5932 | 165.9849
61043 | 126.763 | 117.5889 | 120.9176 | 120.546 | 118.5155 | 117.0749 | 117.1532 | 116.9265 | 119.5894 | 126.7947 | 133.1838 | 136.627 |  |  | 61043 | 251.9333 | 268.4599 | 259.1995 | 261.2774 | 257.019 | 256.8558 | 257.2346 | 258.3844 | 261.8068 | 272.6165 | 281.4439 | 287.3147
62004 | 111.0486 | 83.8434 | 86.2169 | 85.9519 | 84.5041 | 83.4769 | 83.5327 | 83.3711 | 85.2698 | 90.4074 | 94.9629 | 97.418 |  |  | 62004 | 204.6308 | 203.0946 | 196.0888 | 197.6609 | 194.4393 | 194.3158 | 194.6024 | 195.4722 | 198.0613 | 206.2391 | 212.9171 | 217.3585
62005 | 84.5833 | 74.3949 | 76.5009 | 76.2657 | 74.9811 | 74.0697 | 74.1192 | 73.9758 | 75.6606 | 80.2191 | 84.2613 | 86.4397 |  |  | 62005 | 149.1 | 149.1822 | 144.0362 | 145.1909 | 142.8245 | 142.7338 | 142.9443 | 143.5832 | 145.4851 | 151.492 | 156.3973 | 159.6597
62006 | 98.6586 | 71.8231 | 73.8563 | 73.6293 | 72.3891 | 71.5092 | 71.557 | 71.4185 | 73.045 | 77.446 | 81.3484 | 83.4515 |  |  | 62006 | 132.2445 | 126.6308 | 122.2627 | 123.2428 | 121.2342 | 121.1572 | 121.3359 | 121.8782 | 123.4925 | 128.5914 | 132.7552 | 135.5244
62008 | 65.5314 | 160.1278 | 164.6607 | 164.1546 | 161.3896 | 159.4279 | 159.5345 | 159.2258 | 162.852 | 172.6639 | 181.3642 | 186.0531 |  |  | 62008 | 110.2836 | 113.084 | 109.1832 | 110.0585 | 108.2647 | 108.196 | 108.3556 | 108.8399 | 110.2815 | 114.8349 | 118.5533 | 121.0263
62009 | 116.2486 | 96.2747 | 99.0001 | 98.6958 | 97.0333 | 95.8539 | 95.918 | 95.7324 | 97.9126 | 103.8119 | 109.0428 | 111.862 |  |  | 62009 | 135.4389 | 124.7059 | 120.4042 | 121.3694 | 119.3913 | 119.3155 | 119.4915 | 120.0255 | 121.6153 | 126.6367 | 130.7372 | 133.4643
62010 | 69.3183 | 89.6176 | 92.1545 | 91.8713 | 90.3238 | 89.2259 | 89.2856 | 89.1128 | 91.1423 | 96.6336 | 101.5029 | 104.1271 |  |  | 62010 | 121.4816 | 122.8104 | 118.5741 | 119.5247 | 117.5766 | 117.502 | 117.6753 | 118.2012 | 119.7669 | 124.7119 | 128.7501 | 131.4358
62013 | 140.5318 | 135.3623 | 139.1942 | 138.7664 | 136.429 | 134.7707 | 134.8608 | 134.5999 | 137.6653 | 145.9596 | 153.3144 | 157.2781 |  |  | 62013 | 192.7691 | 185.3814 | 178.9867 | 180.4216 | 177.481 | 177.3683 | 177.6299 | 178.4239 | 180.7872 | 188.2517 | 194.3473 | 198.4013
65060 | 9 | 9.2048 | 9.4654 | 9.4363 | 9.2774 | 9.1646 | 9.1707 | 9.153 | 9.3614 | 9.9254 | 10.4256 | 10.6951 |  |  | 65060 | 8.0092 | 9 | 8.6895 | 8.7592 | 8.6164 | 8.611 | 8.6237 | 8.6622 | 8.777 | 9.1393 | 9.4353 | 9.6321
65061 | 116 | 119 | 122.3687 | 121.9926 | 119.9377 | 118.4799 | 118.5591 | 118.3297 | 121.0246 | 128.3163 | 134.782 | 138.2666 |  |  | 65061 | 107.0726 | 106 | 102.3435 | 103.164 | 101.4826 | 101.4182 | 101.5677 | 102.0217 | 103.373 | 107.6412 | 111.1266 | 113.4447
65062 | 0 | 70.1869 | 72.1738 | 71.9519 | 70.74 | 69.8801 | 69.9268 | 69.7915 | 71.381 | 75.6817 | 79.4952 | 81.5504 |  |  | 65062 | 0 | 133.8903 | 129.2717 | 130.3081 | 128.1842 | 128.1029 | 128.2918 | 128.8652 | 130.5721 | 135.9633 | 140.3658 | 143.2938
65063 | 0 | 26.024 | 26.7607 | 26.6784 | 26.2291 | 25.9103 | 25.9276 | 25.8774 | 26.4667 | 28.0614 | 29.4754 | 30.2374 |  |  | 65063 | 0 | 54.0918 | 52.2259 | 52.6446 | 51.7866 | 51.7537 | 51.83 | 52.0617 | 52.7512 | 54.9293 | 56.7079 | 57.8908
65064 | 0 | 40.2561 | 41.3957 | 41.2685 | 40.5733 | 40.0802 | 40.1069 | 40.0294 | 40.941 | 43.4077 | 45.595 | 46.7737 |  |  | 65064 | 0 | 97.2758 | 93.9203 | 94.6732 | 93.1302 | 93.071 | 93.2083 | 93.6249 | 94.865 | 98.7819 | 101.9805 | 104.1078
65065 | 143.5679 | 56.4978 | 58.0972 | 57.9186 | 56.943 | 56.2509 | 56.2885 | 56.1796 | 57.459 | 60.9209 | 63.9907 | 65.6451 |  |  | 65065 | 196.5653 | 180.9538 | 174.7119 | 176.1125 | 173.2421 | 173.1321 | 173.3875 | 174.1624 | 176.4693 | 183.7555 | 189.7056 | 193.6627
65066 | 92.2046 | 103.5581 | 106.4896 | 106.1623 | 104.3741 | 103.1054 | 103.1744 | 102.9748 | 105.3199 | 111.6655 | 117.2922 | 120.3246 |  |  | 65066 | 143.2829 | 117.8757 | 113.8096 | 114.722 | 112.8522 | 112.7806 | 112.9469 | 113.4517 | 114.9545 | 119.7008 | 123.5767 | 126.1545
65067 | 55.5077 | 49.7448 | 51.153 | 50.9958 | 50.1368 | 49.5274 | 49.5605 | 49.4646 | 50.5911 | 53.6393 | 56.3421 | 57.7987 |  |  | 65067 | 72.0058 | 70.0091 | 67.5942 | 68.136 | 67.0255 | 66.983 | 67.0818 | 67.3816 | 68.2741 | 71.0931 | 73.3951 | 74.9261
66101 | 33 | 28.155 | 28.952 | 28.863 | 28.3769 | 28.0319 | 28.0507 | 27.9964 | 28.634 | 30.3592 | 31.889 | 32.7134 |  |  | 66101 | 58.6284 | 56.4271 | 54.4807 | 54.9174 | 54.0223 | 53.988 | 54.0677 | 54.3093 | 55.0287 | 57.3008 | 59.1562 | 60.3901
66102 | 133.7086 | 59.885 | 61.5802 | 61.391 | 60.3569 | 59.6232 | 59.6631 | 59.5477 | 60.9038 | 64.5733 | 67.8271 | 69.5806 |  |  | 66102 | 178.4312 | 193.5394 | 186.8633 | 188.3614 | 185.2914 | 185.1737 | 185.4468 | 186.2757 | 188.743 | 196.536 | 202.8999 | 207.1323
66103 | 109.7493 | 76.065 | 78.2183 | 77.9779 | 76.6644 | 75.7325 | 75.7832 | 75.6365 | 77.3591 | 82.02 | 86.1529 | 88.3802 |  |  | 66103 | 198.4505 | 217.9372 | 210.4194 | 212.1063 | 208.6493 | 208.5168 | 208.8244 | 209.7577 | 212.5361 | 221.3115 | 228.4776 | 233.2435
66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66105 | 84.585 | 49.2417 | 50.6356 | 50.48 | 49.6297 | 49.0264 | 49.0592 | 48.9643 | 50.0794 | 53.0967 | 55.7722 | 57.2141 |  |  | 66105 | 106.3183 | 108.0227 | 104.2965 | 105.1326 | 103.4191 | 103.3534 | 103.5058 | 103.9685 | 105.3456 | 109.6952 | 113.2471 | 115.6094
66106 | 129.8307 | 72.155 | 74.1976 | 73.9695 | 72.7236 | 71.8396 | 71.8876 | 71.7486 | 73.3826 | 77.8039 | 81.7243 | 83.8372 |  |  | 66106 | 180.4526 | 221.6678 | 214.0214 | 215.7372 | 212.221 | 212.0863 | 212.3991 | 213.3484 | 216.1743 | 225.0999 | 232.3887 | 237.2362
66107 | 87.3569 | 34.2183 | 35.187 | 35.0788 | 34.488 | 34.0688 | 34.0915 | 34.0256 | 34.8005 | 36.8972 | 38.7564 | 39.7584 |  |  | 66107 | 101.2602 | 151.3017 | 146.0826 | 147.2537 | 144.8537 | 144.7617 | 144.9752 | 145.6232 | 147.552 | 153.6443 | 158.6193 | 161.9281
66108 | 3.8224 | 0.5693 | 0.58542 | 0.58362 | 0.57379 | 0.56682 | 0.56719 | 0.5661 | 0.57899 | 0.61387 | 0.64481 | 0.66148 |  |  | 66108 | 4.6163 | 0.75667 | 0.73057 | 0.73642 | 0.72442 | 0.72396 | 0.72503 | 0.72827 | 0.73791 | 0.76838 | 0.79326 | 0.80981
66109 | 30.2947 | 23.3233 | 23.9836 | 23.9099 | 23.5071 | 23.2214 | 23.2369 | 23.192 | 23.7201 | 25.1493 | 26.4165 | 27.0995 |  |  | 66109 | 58.4896 | 60.4677 | 58.3819 | 58.8499 | 57.8907 | 57.854 | 57.9393 | 58.1983 | 58.9691 | 61.4039 | 63.3922 | 64.7145
66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67081 | 96.3604 | 71.5175 | 73.542 | 73.316 | 72.0811 | 71.2049 | 71.2525 | 71.1147 | 72.7342 | 77.1165 | 81.0023 | 83.0965 |  |  | 67081 | 132.3497 | 136.9945 | 132.2689 | 133.3292 | 131.1562 | 131.0729 | 131.2662 | 131.8529 | 133.5994 | 139.1156 | 143.6201 | 146.616
67082 | 131 | 119.7542 | 123.1442 | 122.7657 | 120.6979 | 119.2308 | 119.3105 | 119.0797 | 121.7916 | 129.1295 | 135.6362 | 139.1429 |  |  | 67082 | 131.3579 | 144.0218 | 139.0538 | 140.1685 | 137.884 | 137.7964 | 137.9997 | 138.6165 | 140.4525 | 146.2517 | 150.9873 | 154.1368
67083 | 138.3715 | 112.9247 | 116.1214 | 115.7645 | 113.8146 | 112.4311 | 112.5063 | 112.2886 | 114.8459 | 121.7654 | 127.901 | 131.2077 |  |  | 67083 | 141.0807 | 237.4912 | 229.299 | 231.1373 | 227.3701 | 227.2257 | 227.5608 | 228.5779 | 231.6056 | 241.1683 | 248.9774 | 254.1709
67084 | 172.0287 | 172.2769 | 177.1538 | 176.6093 | 173.6345 | 171.5239 | 171.6386 | 171.3065 | 175.2079 | 185.7642 | 195.1246 | 200.1693 |  |  | 67084 | 172.7152 | 138.5577 | 133.7782 | 134.8506 | 132.6528 | 132.5685 | 132.7641 | 133.3575 | 135.1238 | 140.703 | 145.2589 | 148.289
67085 | 70.2029 | 65.2019 | 67.0477 | 66.8416 | 65.7157 | 64.917 | 64.9603 | 64.8347 | 66.3112 | 70.3065 | 73.8492 | 75.7584 |  |  | 67085 | 115.3128 | 114.3402 | 110.3961 | 111.2811 | 109.4674 | 109.3979 | 109.5592 | 110.0489 | 111.5066 | 116.1106 | 119.8702 | 122.3707
67086 | 96.4917 | 91.2825 | 93.8665 | 93.578 | 92.0018 | 90.8835 | 90.9443 | 90.7683 | 92.8355 | 98.4288 | 103.3886 | 106.0615 |  |  | 67086 | 175.7695 | 182.4601 | 176.1661 | 177.5784 | 174.6841 | 174.5732 | 174.8307 | 175.6121 | 177.9382 | 185.2851 | 191.2846 | 195.2748
67087 | 182 | 80.2208 | 82.4917 | 82.2382 | 80.853 | 79.8702 | 79.9236 | 79.769 | 81.5856 | 86.5012 | 90.8599 | 93.2089 |  |  | 67087 | 211.3447 | 230.2388 | 222.2967 | 224.0789 | 220.4267 | 220.2867 | 220.6117 | 221.5977 | 224.5328 | 233.8036 | 241.3742 | 246.4091
67088 | 47.4435 | 42.5008 | 43.704 | 43.5696 | 42.8357 | 42.3151 | 42.3434 | 42.2614 | 43.2239 | 45.8281 | 48.1374 | 49.3819 |  |  | 67088 | 99.5241 | 205.3757 | 198.2913 | 199.881 | 196.6232 | 196.4984 | 196.7882 | 197.6678 | 200.286 | 208.5556 | 215.3086 | 219.7999
67089 | 55.3855 | 50.4819 | 51.911 | 51.7514 | 50.8797 | 50.2613 | 50.2949 | 50.1976 | 51.3408 | 54.4341 | 57.177 | 58.6552 |  |  | 67089 | 109.3138 | 109.9003 | 106.1093 | 106.96 | 105.2167 | 105.1499 | 105.305 | 105.7756 | 107.1767 | 111.6019 | 115.2156 | 117.6189
67090 | 167.4959 | 141.4987 | 145.5043 | 145.0571 | 142.6138 | 140.8803 | 140.9744 | 140.7017 | 143.9061 | 152.5764 | 160.2646 | 164.408 |  |  | 67090 | 264.604 | 248.2771 | 239.7128 | 241.6346 | 237.6963 | 237.5453 | 237.8957 | 238.959 | 242.1241 | 252.1212 | 260.2849 | 265.7143
67091 | 79.6207 | 59.0483 | 60.7199 | 60.5332 | 59.5136 | 58.7902 | 58.8295 | 58.7157 | 60.0529 | 63.6711 | 66.8794 | 68.6085 |  |  | 67091 | 133.9512 | 139.9172 | 135.0907 | 136.1737 | 133.9543 | 133.8693 | 134.0667 | 134.6659 | 136.4496 | 142.0835 | 146.6842 | 149.744
80001 | 83.0228 | 61.0933 | 62.8228 | 62.6297 | 61.5748 | 60.8263 | 60.867 | 60.7492 | 62.1327 | 65.8762 | 69.1957 | 70.9846 |  |  | 80001 | 91.2981 | 211.6362 | 204.3358 | 205.9739 | 202.6169 | 202.4882 | 202.7869 | 203.6932 | 206.3912 | 214.9129 | 221.8718 | 226.5
80002 | 153.1936 | 155.9333 | 160.3475 | 159.8547 | 157.1621 | 155.2518 | 155.3555 | 155.055 | 158.5862 | 168.1411 | 176.6135 | 181.1796 |  |  | 80002 | 131.2303 | 119.2733 | 115.159 | 116.0822 | 114.1903 | 114.1178 | 114.2861 | 114.7969 | 116.3174 | 121.12 | 125.0419 | 127.6503
80003 | 169.6102 | 150.7133 | 154.9798 | 154.5034 | 151.901 | 150.0546 | 150.1549 | 149.8644 | 153.2774 | 162.5124 | 170.7012 | 175.1144 |  |  | 80003 | 181.5924 | 174.0794 | 168.0746 | 169.422 | 166.6606 | 166.5548 | 166.8005 | 167.546 | 169.7652 | 176.7747 | 182.4987 | 186.3055
80004 | 56.4746 | 92.1867 | 94.7963 | 94.5049 | 92.9131 | 91.7837 | 91.8451 | 91.6674 | 93.755 | 99.4038 | 104.4126 | 107.1121 |  |  | 80004 | 99.6264 | 98.8582 | 95.4481 | 96.2133 | 94.6452 | 94.5851 | 94.7246 | 95.148 | 96.4082 | 100.3888 | 103.6394 | 105.8013
80005 | 103.2 | 67.52 | 69.4314 | 69.218 | 68.0521 | 67.2249 | 67.2698 | 67.1397 | 68.6687 | 72.806 | 76.4746 | 78.4518 |  |  | 80005 | 250.1773 | 206.8292 | 199.6946 | 201.2956 | 198.0147 | 197.889 | 198.1809 | 199.0667 | 201.7034 | 210.0315 | 216.8324 | 221.3554
80006 | 205.8314 | 115.16 | 118.42 | 118.056 | 116.0675 | 114.6566 | 114.7333 | 114.5113 | 117.1192 | 124.1757 | 130.4327 | 133.8049 |  |  | 80006 | 116.3897 | 280.6336 | 270.9532 | 273.1254 | 268.6738 | 268.5032 | 268.8993 | 270.1011 | 273.6787 | 284.9786 | 294.2063 | 300.3433
80007 | 91.308 | 103.7467 | 106.6836 | 106.3557 | 104.5642 | 103.2932 | 103.3622 | 103.1623 | 105.5117 | 111.8688 | 117.5058 | 120.5437 |  |  | 80007 | 160.9115 | 142.7917 | 137.8661 | 138.9713 | 136.7063 | 136.6195 | 136.821 | 137.4325 | 139.2529 | 145.0025 | 149.6977 | 152.8203
80008 | 163.4687 | 72.4533 | 74.5044 | 74.2754 | 73.0243 | 72.1366 | 72.1849 | 72.0452 | 73.686 | 78.1256 | 82.0622 | 84.1838 |  |  | 80008 | 236.5933 | 144.2572 | 139.2811 | 140.3977 | 138.1094 | 138.0217 | 138.2253 | 138.8431 | 140.6821 | 146.4908 | 151.2342 | 154.3888
80009 | 83.6755 | 77.6867 | 79.8858 | 79.6403 | 78.2988 | 77.3471 | 77.3988 | 77.2491 | 79.0084 | 83.7686 | 87.9896 | 90.2645 |  |  | 80009 | 146.7103 | 170.6146 | 164.7293 | 166.0499 | 163.3435 | 163.2398 | 163.4806 | 164.2113 | 166.3863 | 173.2563 | 178.8663 | 182.5974
80010 | 105.5043 | 73.4667 | 75.5464 | 75.3142 | 74.0456 | 73.1456 | 73.1944 | 73.0528 | 74.7166 | 79.2182 | 83.21 | 85.3612 |  |  | 80010 | 182 | 186.0459 | 179.6283 | 181.0683 | 178.1172 | 178.0041 | 178.2666 | 179.0634 | 181.4352 | 188.9264 | 195.0439 | 199.1124
80011 | 92.0007 | 88.5067 | 91.0121 | 90.7324 | 89.2041 | 88.1198 | 88.1787 | 88.0081 | 90.0124 | 95.4357 | 100.2446 | 102.8363 |  |  | 80011 | 156 | 156.3725 | 150.9785 | 152.1889 | 149.7084 | 149.6133 | 149.834 | 150.5037 | 152.4972 | 158.7936 | 163.9354 | 167.355
81001 | 36 | 31.32 | 32.2066 | 32.1076 | 31.5668 | 31.1831 | 31.2039 | 31.1436 | 31.8528 | 33.772 | 35.4737 | 36.3908 |  |  | 81001 | 47.2 | 201.8057 | 194.8444 | 196.4064 | 193.2053 | 193.0826 | 193.3674 | 194.2317 | 196.8044 | 204.9302 | 211.5659 | 215.9791
81002 | 64.7525 | 53.9257 | 55.4522 | 55.2818 | 54.3506 | 53.69 | 53.7259 | 53.6219 | 54.8431 | 58.1474 | 61.0774 | 62.6565 |  |  | 81002 | 70.2212 | 63.7495 | 61.5504 | 62.0439 | 61.0326 | 60.9939 | 61.0839 | 61.3569 | 62.1696 | 64.7365 | 66.8327 | 68.2268
81003 | 120.1386 | 104.5543 | 107.5141 | 107.1836 | 105.3782 | 104.0973 | 104.1669 | 103.9654 | 106.3331 | 112.7397 | 118.4205 | 121.4821 |  |  | 81003 | 207.1816 | 180.8676 | 174.6286 | 176.0285 | 173.1595 | 173.0496 | 173.3048 | 174.0794 | 176.3852 | 183.6679 | 189.6152 | 193.5704
82001 | 118.9 | 94.2665 | 96.935 | 96.6371 | 95.0093 | 93.8544 | 93.9172 | 93.7355 | 95.8702 | 101.6464 | 106.7683 | 109.5286 |  |  | 82001 | 92.7773 | 78.4962 | 75.7885 | 76.3961 | 75.151 | 75.1033 | 75.214 | 75.5502 | 76.5509 | 79.7116 | 82.2927 | 84.0093
82002 | 161.3905 | 72.1073 | 74.1486 | 73.9207 | 72.6755 | 71.7922 | 71.8402 | 71.7012 | 73.3341 | 77.7525 | 81.6703 | 83.7818 |  |  | 82002 | 176.6632 | 152.3864 | 147.1298 | 148.3093 | 145.8921 | 145.7995 | 146.0145 | 146.6671 | 148.6098 | 154.7458 | 159.7565 | 163.0889
82003 | 121.6848 | 90.9937 | 93.5695 | 93.2819 | 91.7107 | 90.5959 | 90.6565 | 90.4811 | 92.5417 | 98.1174 | 103.0614 | 105.7259 |  |  | 82003 | 200.7833 | 182.1558 | 175.8724 | 177.2823 | 174.3929 | 174.2822 | 174.5392 | 175.3193 | 177.6415 | 184.9761 | 190.9657 | 194.9492
82004 | 58.6 | 58.8839 | 60.5508 | 60.3647 | 59.3479 | 94.6006 | 94.6639 | 94.4807 | 96.6324 | 102.4546 | 107.6171 | 110.3994 |  |  | 82004 | 0 | 48.4938 | 46.821 | 47.1963 | 46.4271 | 46.3976 | 46.4661 | 46.6738 | 47.292 | 49.2446 | 50.8392 | 51.8996
82005 | 87.1851 | 0 | 0 | 0 | 0 | 35.9741 | 35.9982 | 35.9285 | 36.7468 | 38.9608 | 40.924 | 41.982 |  |  | 82005 | 165.0258 | 152.1494 | 146.9011 | 148.0787 | 145.6653 | 145.5728 | 145.7875 | 146.4391 | 148.3787 | 154.5052 | 159.5081 | 162.8353
82006 | 122.9859 | 135.6109 | 139.4498 | 139.0212 | 136.6795 | 170.9923 | 171.1066 | 170.7756 | 174.6648 | 185.1884 | 194.5198 | 199.5488 |  |  | 82006 | 117 | 84.3578 | 81.4479 | 82.1008 | 80.7627 | 80.7114 | 80.8305 | 81.1918 | 82.2672 | 85.6639 | 88.4377 | 90.2825
82007 | 42.5 | 86.86 | 89.3188 | 89.0443 | 87.5444 | 122.4544 | 122.5363 | 122.2992 | 125.0845 | 132.6208 | 139.3034 | 142.9049 |  |  | 82007 | 68.7586 | 35.4419 | 34.2193 | 34.4936 | 33.9314 | 33.9099 | 33.9599 | 34.1117 | 34.5635 | 35.9906 | 37.156 | 37.931
82008 | 113.2031 | 96.2005 | 98.9238 | 98.6197 | 96.9586 | 95.78 | 95.844 | 95.6586 | 97.8371 | 103.7318 | 108.9588 | 111.7757 |  |  | 82008 | 182.2266 | 169.324 | 163.4832 | 164.7939 | 162.108 | 162.005 | 162.244 | 162.9691 | 165.1277 | 171.9457 | 177.5133 | 181.2162
84121 | 39.6 | 36.0643 | 37.0853 | 36.9713 | 36.3485 | 35.9067 | 35.9307 | 35.8612 | 36.6779 | 38.8878 | 40.8473 | 41.9033 |  |  | 84121 | 51.3942 | 50.1063 | 48.3779 | 48.7658 | 47.9709 | 47.9405 | 48.0112 | 48.2258 | 48.8646 | 50.8821 | 52.5297 | 53.6254
84122 | 27.9515 | 5.4045 | 5.5575 | 5.5404 | 5.4471 | 5.3809 | 5.3845 | 5.3741 | 5.4965 | 5.8276 | 6.1213 | 6.2795 |  |  | 84122 | 28.2734 | 8.6789 | 8.3795 | 8.4467 | 8.309 | 8.3037 | 8.316 | 8.3532 | 8.4638 | 8.8133 | 9.0986 | 9.2884
85001 | 153.3534 | 118.2426 | 121.5898 | 121.2161 | 119.1743 | 117.7257 | 117.8044 | 117.5765 | 120.2542 | 127.4995 | 133.9241 | 137.3865 |  |  | 85001 | 179.8661 | 144.4339 | 139.4517 | 140.5696 | 138.2785 | 138.1907 | 138.3946 | 139.0131 | 140.8544 | 146.6701 | 151.4194 | 154.5779
85002 | 170.9 | 214.3134 | 220.3803 | 219.7029 | 216.0023 | 213.3767 | 213.5193 | 213.1063 | 217.9596 | 231.0916 | 242.7361 | 249.0117 |  |  | 85002 | 176.2466 | 222.5181 | 214.8424 | 216.5648 | 213.0351 | 212.8998 | 213.2138 | 214.1668 | 217.0035 | 225.9634 | 233.2801 | 238.1462
85003 | 86.8 | 82.6738 | 85.0141 | 84.7528 | 83.3253 | 82.3124 | 82.3674 | 82.2081 | 84.0803 | 89.1462 | 93.6381 | 96.059 |  |  | 85003 | 106.7432 | 43.8028 | 42.2918 | 42.6309 | 41.936 | 41.9094 | 41.9712 | 42.1588 | 42.7172 | 44.481 | 45.9213 | 46.8792
85004 | 106.3 | 115.4497 | 118.7179 | 118.353 | 116.3595 | 114.9451 | 115.0219 | 114.7994 | 117.4138 | 124.488 | 130.7609 | 134.1415 |  |  | 85004 | 67.9 | 100.9144 | 97.4334 | 98.2145 | 96.6137 | 96.5524 | 96.6948 | 97.127 | 98.4135 | 102.4769 | 105.7951 | 108.0019
85005 | 317.6631 | 292.1797 | 300.4508 | 299.5274 | 294.4822 | 290.9027 | 291.0971 | 290.534 | 297.1506 | 315.0539 | 330.9292 | 339.4848 |  |  | 85005 | 338.2496 | 286.5577 | 276.6729 | 278.891 | 274.3454 | 274.1713 | 274.5757 | 275.8029 | 279.456 | 290.9945 | 300.4169 | 306.6835
85006 | 247.6 | 229.5292 | 236.0268 | 235.3013 | 231.3379 | 228.526 | 228.6787 | 228.2363 | 233.4342 | 247.4986 | 259.9698 | 266.6909 |  |  | 85006 | 185.3413 | 188.6007 | 182.0949 | 183.5548 | 180.5631 | 180.4484 | 180.7146 | 181.5223 | 183.9267 | 191.5208 | 197.7223 | 201.8467
85007 | 516.9818 | 382.5371 | 393.366 | 392.157 | 385.5515 | 380.8651 | 381.1196 | 380.3823 | 389.0452 | 412.4852 | 433.2699 | 444.4714 |  |  | 85007 | 534.7612 | 317.3158 | 306.3701 | 308.8262 | 303.7928 | 303.5999 | 304.0477 | 305.4066 | 309.4519 | 322.2288 | 332.6627 | 339.6019
85008 | 110.7393 | 99.7532 | 102.577 | 102.2618 | 100.5393 | 99.3172 | 99.3836 | 99.1913 | 101.4503 | 107.5627 | 112.9827 | 115.9037 |  |  | 85008 | 178.4351 | 162.4409 | 156.8375 | 158.0949 | 155.5182 | 155.4194 | 155.6487 | 156.3443 | 158.4152 | 164.956 | 170.2973 | 173.8496
90019 | 408.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 90019 | 401.7503 | 0.24 | 0.23172 | 0.23358 | 0.22977 | 0.22963 | 0.22996 | 0.23099 | 0.23405 | 0.24372 | 0.25161 | 0.25686
90020 | 98.4862 | 71.4733 | 73.4966 | 73.2707 | 72.0366 | 71.1609 | 71.2085 | 71.0707 | 72.6893 | 77.0688 | 80.9523 | 83.0452 |  |  | 90020 | 122.6979 | 96.671 | 93.3364 | 94.0846 | 92.5512 | 92.4924 | 92.6288 | 93.0429 | 94.2752 | 98.1678 | 101.3465 | 103.4605
90021 | 67.5481 | 0.575 | 0.59128 | 0.58946 | 0.57953 | 0.57249 | 0.57287 | 0.57176 | 0.58478 | 0.62002 | 0.65126 | 0.66809 |  |  | 90021 | 88.3617 | 78.8733 | 76.1526 | 76.7631 | 75.512 | 75.464 | 75.5753 | 75.9131 | 76.9186 | 80.0945 | 82.688 | 84.4128
90023 | 86.3185 | 65.725 | 67.5856 | 67.3778 | 66.2429 | 65.4377 | 65.4815 | 65.3548 | 66.8432 | 70.8705 | 74.4416 | 76.3661 |  |  | 90023 | 136.561 | 121.3834 | 117.1963 | 118.1359 | 116.2104 | 116.1366 | 116.3079 | 116.8278 | 118.3752 | 123.2628 | 127.2541 | 129.9085
90024 | 78.9189 | 44.135 | 45.3844 | 45.2449 | 44.4828 | 43.9421 | 43.9715 | 43.8864 | 44.8859 | 47.5902 | 49.9883 | 51.2806 |  |  | 90024 | 122.879 | 121.0229 | 116.8482 | 117.785 | 115.8652 | 115.7917 | 115.9624 | 116.4807 | 118.0236 | 122.8967 | 126.8761 | 129.5227
91001 | 163.4182 | 145.0754 | 149.1822 | 148.7237 | 146.2186 | 144.4413 | 144.5378 | 144.2582 | 147.5435 | 156.433 | 164.3155 | 168.5637 |  |  | 91001 | 150 | 162.2796 | 156.6818 | 157.9379 | 155.3637 | 155.2651 | 155.4941 | 156.1891 | 158.2579 | 164.7922 | 170.1282 | 173.677
91002 | 79 | 78.15 | 80.3623 | 80.1153 | 78.7658 | 77.8084 | 77.8604 | 77.7098 | 79.4796 | 84.2682 | 88.5144 | 90.8028 |  |  | 91002 | 81.0636 | 57.0314 | 55.0641 | 55.5056 | 54.6009 | 54.5662 | 54.6467 | 54.891 | 55.618 | 57.9144 | 59.7897 | 61.0369
91003 | 154.5534 | 158.7124 | 163.2053 | 162.7037 | 159.9631 | 158.0187 | 158.1243 | 157.8184 | 161.4126 | 171.1377 | 179.7612 | 184.4086 |  |  | 91003 | 235.0999 | 211.4367 | 204.1433 | 205.7798 | 202.4259 | 202.2974 | 202.5958 | 203.5013 | 206.1967 | 214.7104 | 221.6628 | 226.2866
91004 | 152.6667 | 166.2 | 170.9048 | 170.3795 | 167.5097 | 165.4736 | 165.5842 | 165.2638 | 169.0276 | 179.2115 | 188.2418 | 193.1084 |  |  | 91004 | 162 | 159.8944 | 154.3789 | 155.6165 | 153.0802 | 152.983 | 153.2087 | 153.8934 | 155.9318 | 162.3701 | 167.6277 | 171.1243
91005 | 98.1754 | 50.6611 | 52.0952 | 51.9351 | 51.0603 | 50.4397 | 50.4734 | 50.3757 | 51.523 | 54.6273 | 57.3799 | 58.8633 |  |  | 91005 | 108.5406 | 151.5625 | 146.3343 | 147.5075 | 145.1033 | 145.0112 | 145.2251 | 145.8742 | 147.8063 | 153.9091 | 158.8927 | 162.2071
91006 | 166.911 | 150.6125 | 154.8761 | 154.4 | 151.7993 | 149.9542 | 150.0544 | 149.7641 | 153.1749 | 162.4036 | 170.587 | 174.9972 |  |  | 91006 | 249.9722 | 248.0385 | 239.4825 | 241.4023 | 237.4678 | 237.3171 | 237.6671 | 238.7294 | 241.8914 | 251.8789 | 260.0348 | 265.459
91007 | 57.8539 | 87.8869 | 90.3748 | 90.097 | 88.5794 | 87.5027 | 87.5612 | 87.3918 | 89.3821 | 94.7674 | 99.5426 | 102.1161 |  |  | 91007 | 109.2243 | 219.5818 | 212.0074 | 213.707 | 210.2239 | 210.0904 | 210.4003 | 211.3407 | 214.14 | 222.9816 | 230.2018 | 235.0037
91008 | 130.6683 | 70.5944 | 72.5928 | 72.3697 | 71.1507 | 70.2859 | 70.3329 | 70.1968 | 71.7955 | 76.1211 | 79.9568 | 82.024 |  |  | 91008 | 245.7037 | 238.9476 | 230.7051 | 232.5546 | 228.7643 | 228.6191 | 228.9563 | 229.9796 | 233.0258 | 242.6472 | 250.5041 | 255.7296
91009 | 96.3747 | 115.8833 | 119.1638 | 118.7975 | 116.7965 | 115.3768 | 115.4539 | 115.2306 | 117.8549 | 124.9556 | 131.252 | 134.6453 |  |  | 91009 | 183.3222 | 178.0739 | 171.9313 | 173.3096 | 170.4849 | 170.3767 | 170.6279 | 171.3906 | 173.6607 | 180.831 | 186.6863 | 190.5805
91010 | 126.753 | 78.9202 | 81.1543 | 80.9049 | 79.5421 | 78.5753 | 78.6278 | 78.4757 | 80.2629 | 85.0988 | 89.3868 | 91.6977 |  |  | 91010 | 217.3396 | 219.1958 | 211.6347 | 213.3313 | 209.8544 | 209.7211 | 210.0304 | 210.9692 | 213.7636 | 222.5896 | 229.7971 | 234.5906
91011 | 96 | 189.4598 | 194.8231 | 194.2243 | 190.9528 | 188.6317 | 188.7578 | 188.3926 | 192.6831 | 204.2922 | 214.5863 | 220.1341 |  |  | 91011 | 81 | 107.9083 | 104.186 | 105.0212 | 103.3095 | 103.2439 | 103.3962 | 103.8584 | 105.234 | 109.579 | 113.1272 | 115.487
91012 | 97.6667 | 82.1444 | 84.4698 | 84.2102 | 82.7918 | 81.7854 | 81.8401 | 81.6817 | 83.542 | 88.5754 | 93.0386 | 95.444 |  |  | 91012 | 69.0022 | 74.7028 | 72.1259 | 72.7042 | 71.5192 | 71.4738 | 71.5792 | 71.8991 | 72.8515 | 75.8594 | 78.3158 | 79.9494
93001 | 134.456 | 134.051 | 137.8458 | 137.4221 | 135.1074 | 133.4651 | 133.5543 | 133.296 | 136.3317 | 144.5456 | 151.8291 | 155.7544 |  |  | 93001 | 127.8758 | 143.138 | 138.2005 | 139.3084 | 137.0379 | 136.9508 | 137.1528 | 137.7659 | 139.5906 | 145.3542 | 150.0608 | 153.191
93002 | 183.207 | 189.5093 | 194.8739 | 194.275 | 191.0026 | 188.6809 | 188.8071 | 188.4418 | 192.7334 | 204.3456 | 214.6423 | 220.1916 |  |  | 93002 | 120.3792 | 120.3089 | 116.1589 | 117.0901 | 115.1817 | 115.1086 | 115.2784 | 115.7936 | 117.3273 | 122.1717 | 126.1276 | 128.7586
93003 | 142.1124 | 131.2339 | 134.9489 | 134.5341 | 132.268 | 130.6603 | 130.7476 | 130.4947 | 133.4666 | 141.5079 | 148.6384 | 152.4812 |  |  | 93003 | 132.4247 | 116.5196 | 112.5003 | 113.4022 | 111.5539 | 111.4831 | 111.6475 | 112.1465 | 113.6319 | 118.3237 | 122.155 | 124.7031
93004 | 104.3774 | 98.4385 | 101.2251 | 100.914 | 99.2142 | 98.0083 | 98.0738 | 97.884 | 100.1133 | 106.1451 | 111.4936 | 114.3761 |  |  | 93004 | 120.6386 | 115.6568 | 111.6672 | 112.5625 | 110.7279 | 110.6576 | 110.8208 | 111.3161 | 112.7905 | 117.4475 | 121.2505 | 123.7797
93005 | 101.651 | 94.9673 | 97.6557 | 97.3555 | 95.7156 | 94.5522 | 94.6154 | 94.4324 | 96.583 | 102.4021 | 107.562 | 110.3429 |  |  | 93005 | 131.2911 | 128.1538 | 123.7331 | 124.7251 | 122.6922 | 122.6143 | 122.7952 | 123.344 | 124.9778 | 130.138 | 134.3519 | 137.1544
93006 | 69.2202 | 83.3132 | 85.6717 | 85.4084 | 83.9697 | 82.9491 | 83.0045 | 82.8439 | 84.7306 | 89.8357 | 94.3624 | 96.802 |  |  | 93006 | 63.2045 | 63.6133 | 61.419 | 61.9114 | 60.9023 | 60.8637 | 60.9534 | 61.2259 | 62.0368 | 64.5983 | 66.69 | 68.0811
94001 | 114.8 | 108.5933 | 111.6674 | 111.3242 | 109.4491 | 108.1187 | 108.191 | 107.9816 | 110.4408 | 117.0949 | 122.9952 | 126.175 |  |  | 94001 | 66.9709 | 59.8386 | 57.7745 | 58.2377 | 57.2885 | 57.2521 | 57.3365 | 57.5928 | 58.3556 | 60.7651 | 62.7327 | 64.0413
94002 | 190 | 197.2966 | 202.8817 | 202.2581 | 198.8513 | 196.4342 | 196.5655 | 196.1852 | 200.6532 | 212.7425 | 223.4624 | 229.2397 |  |  | 94002 | 130.8172 | 176.6174 | 170.525 | 171.8921 | 169.0905 | 168.9831 | 169.2324 | 169.9888 | 172.2403 | 179.352 | 185.1594 | 189.0218
95001 | 25.0935 | 22.3968 | 23.0308 | 22.96 | 22.5733 | 22.2989 | 22.3138 | 22.2706 | 22.7778 | 24.1502 | 25.3671 | 26.0229 |  |  | 95001 | 33.2275 | 32.2834 | 31.1698 | 31.4197 | 30.9076 | 30.888 | 30.9335 | 31.0718 | 31.4834 | 32.7833 | 33.8448 | 34.5508
96202 | 110.4845 | 95.3895 | 98.0898 | 97.7883 | 96.1412 | 94.9725 | 95.036 | 94.8522 | 97.0124 | 102.8574 | 108.0402 | 110.8334 |  |  | 96202 | 115.8333 | 103.7322 | 100.154 | 100.9569 | 99.3115 | 99.2484 | 99.3948 | 99.839 | 101.1615 | 105.3383 | 108.7492 | 111.0176
97001 | 28.0568 | 17.7701 | 18.2732 | 18.217 | 17.9102 | 17.6925 | 17.7043 | 17.67 | 18.0725 | 19.1613 | 20.1268 | 20.6472 |  |  | 97001 | 35.2223 | 33.2627 | 32.1153 | 32.3727 | 31.8451 | 31.8249 | 31.8718 | 32.0143 | 32.4383 | 33.7777 | 34.8714 | 35.5988
97002 | 29.3522 | 22.2818 | 22.9125 | 22.8421 | 22.4574 | 22.1844 | 22.1992 | 22.1563 | 22.6609 | 24.0262 | 25.2368 | 25.8893 |  |  | 97002 | 38.5929 | 36.0322 | 34.7893 | 35.0682 | 34.4966 | 34.4747 | 34.5256 | 34.6799 | 35.1393 | 36.5901 | 37.7749 | 38.5629
97013 | 0 | 50.8498 | 52.2893 | 52.1286 | 51.2505 | 50.6275 | 50.6614 | 50.5634 | 51.7149 | 54.8307 | 57.5936 | 59.0826 |  |  | 97013 | 0 | 123.7236 | 119.4558 | 120.4135 | 118.4509 | 118.3757 | 118.5503 | 119.0802 | 120.6574 | 125.6393 | 129.7075 | 132.4131
97014 | 0 | 33.6942 | 34.648 | 34.5415 | 33.9597 | 33.5469 | 33.5693 | 33.5044 | 34.2674 | 36.332 | 38.1628 | 39.1494 |  |  | 97014 | 0 | 243.0285 | 234.6453 | 236.5264 | 232.6714 | 232.5236 | 232.8666 | 233.9074 | 237.0056 | 246.7913 | 254.7825 | 260.0971
98001 | 52.2644 | 41.5856 | 42.7628 | 42.6314 | 41.9133 | 41.4038 | 41.4315 | 41.3514 | 42.2931 | 44.8413 | 47.1008 | 48.3185 |  |  | 98001 | 59.1292 | 58.8448 | 56.8149 | 57.2704 | 56.337 | 56.3012 | 56.3842 | 56.6362 | 57.3864 | 59.7558 | 61.6907 | 62.9776
98002 | 49.1613 | 39.1032 | 40.2101 | 40.0865 | 39.4113 | 38.9322 | 38.9583 | 38.8829 | 39.7684 | 42.1645 | 44.2891 | 45.4341 |  |  | 98002 | 67.5717 | 65.1368 | 62.89 | 63.3941 | 62.3609 | 62.3213 | 62.4132 | 62.6922 | 63.5226 | 66.1454 | 68.2872 | 69.7116
98003 | 30.0487 | 22.7359 | 23.3795 | 23.3076 | 22.915 | 22.6365 | 22.6516 | 22.6078 | 23.1227 | 24.5158 | 25.7511 | 26.4169 |  |  | 98003 | 46.5093 | 40.4536 | 39.0582 | 39.3713 | 38.7296 | 38.705 | 38.7621 | 38.9353 | 39.4511 | 41.08 | 42.4101 | 43.2948
99981 | 35.9056 | 26.9092 | 27.6709 | 27.5859 | 27.1212 | 26.7916 | 26.8095 | 26.7576 | 27.367 | 29.0159 | 30.4779 | 31.2659 |  |  | 99981 | 52.7418 | 48.5295 | 46.8555 | 47.2311 | 46.4613 | 46.4318 | 46.5003 | 46.7082 | 47.3268 | 49.2809 | 50.8766 | 51.9379
99982 | 202.8644 | 198.4722 | 204.0906 | 203.4633 | 200.0362 | 197.6047 | 197.7368 | 197.3543 | 201.8488 | 214.0102 | 224.794 | 230.6057 |  |  | 99982 | 60.3333 | 207.7778 | 200.6105 | 202.2188 | 198.9229 | 198.7966 | 199.0898 | 199.9797 | 202.6285 | 210.9948 | 217.8268 | 222.3706
99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18131A | 158 | 95.0518 | 97.7426 | 97.4422 | 95.8009 | 94.6364 | 94.6996 | 94.5164 | 96.669 | 102.4933 | 107.6578 | 110.4411 |  |  | 18131A | 178.5728 | 158.3843 | 152.9208 | 154.1468 | 151.6344 | 151.5381 | 151.7616 | 152.4399 | 154.4591 | 160.8365 | 166.0445 | 169.5081
18131B | 173.0051 | 153.6593 | 158.0092 | 157.5235 | 154.8702 | 152.9877 | 153.09 | 152.7938 | 156.2735 | 165.689 | 174.0379 | 178.5374 |  |  | 18131B | 206.7787 | 174.4993 | 168.48 | 169.8306 | 167.0626 | 166.9566 | 167.2028 | 167.9501 | 170.1747 | 177.2011 | 182.9389 | 186.7549
18132A | 0 | 50.3939 | 51.8204 | 51.6611 | 50.791 | 50.1736 | 50.2071 | 50.11 | 51.2512 | 54.3391 | 57.0772 | 58.5528 |  |  | 18132A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18132B | 49.8 | 41.654 | 42.8332 | 42.7015 | 41.9823 | 41.472 | 41.4997 | 41.4194 | 42.3627 | 44.915 | 47.1783 | 48.398 |  |  | 18132B | 50.9551 | 38.6877 | 37.3531 | 37.6526 | 37.0389 | 37.0154 | 37.07 | 37.2357 | 37.7289 | 39.2867 | 40.5588 | 41.4048
18133A | 45 | 74.5461 | 76.6564 | 76.4207 | 75.1335 | 74.2203 | 74.2699 | 74.1262 | 75.8143 | 80.3822 | 84.4325 | 86.6154 |  |  | 18133A | 45.0664 | 37.2622 | 35.9768 | 36.2653 | 35.6742 | 35.6515 | 35.7041 | 35.8637 | 36.3387 | 37.8391 | 39.0644 | 39.8792
18133B | 35.8984 | 23.4107 | 24.0734 | 23.9994 | 23.5951 | 23.3083 | 23.3239 | 23.2788 | 23.809 | 25.2434 | 26.5154 | 27.2009 |  |  | 18133B | 56.7327 | 42.4236 | 40.9602 | 41.2886 | 40.6156 | 40.5898 | 40.6497 | 40.8314 | 41.3722 | 43.0804 | 44.4754 | 45.4031
18134A | 42.0111 | 35.7668 | 36.7792 | 36.6662 | 36.0486 | 35.6104 | 35.6342 | 35.5653 | 36.3753 | 38.5669 | 40.5102 | 41.5575 |  |  | 18134A | 66.1345 | 60.4675 | 58.3817 | 58.8497 | 57.8905 | 57.8538 | 57.9391 | 58.1981 | 58.9689 | 61.4037 | 63.392 | 64.7143
18134B | 30.1878 | 17.5474 | 18.0442 | 17.9887 | 17.6857 | 17.4707 | 17.4824 | 17.4486 | 17.846 | 18.9212 | 19.8746 | 20.3884 |  |  | 18134B | 51.9148 | 42.2833 | 40.8247 | 41.152 | 40.4813 | 40.4556 | 40.5152 | 40.6963 | 41.2354 | 42.9379 | 44.3283 | 45.2529
18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18135B | 76.9883 | 70.0551 | 72.0382 | 71.8168 | 70.6071 | 69.7489 | 69.7955 | 69.6604 | 71.2469 | 75.5395 | 79.3459 | 81.3973 |  |  | 18135B | 128.6887 | 98.127 | 94.7421 | 95.5017 | 93.9451 | 93.8855 | 94.0239 | 94.4442 | 95.6951 | 99.6463 | 102.8729 | 105.0187
18136A | 62.9714 | 40.2243 | 41.363 | 41.2359 | 40.5413 | 40.0485 | 40.0753 | 39.9977 | 40.9086 | 43.3734 | 45.5589 | 46.7368 |  |  | 18136A | 114.4323 | 108.4125 | 104.6728 | 105.512 | 137.2082 | 137.1211 | 137.3234 | 137.9372 | 139.7642 | 145.5349 | 150.2474 | 153.3815
18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18136B | 0 | 0 | 0 | 0 | 33.416 | 33.3947 | 33.444 | 33.5935 | 34.0384 | 35.4439 | 36.5915 | 37.3548
18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18141A | 0 | 0 | 0 | 0 | 33.416 | 33.3947 | 33.444 | 33.5935 | 34.0384 | 35.4439 | 36.5915 | 37.3548
18141B | 136.3688 | 139.1014 | 143.0392 | 142.5995 | 140.1976 | 138.4934 | 138.586 | 138.3179 | 141.468 | 149.9914 | 157.5493 | 161.6225 |  |  | 18141B | 184.2653 | 181.8268 | 175.5547 | 176.9621 | 207.4938 | 207.3621 | 207.6679 | 208.5961 | 211.359 | 220.0858 | 227.2123 | 231.9518
18142A | 20.3704 | 15.1184 | 15.5464 | 15.4986 | 15.2375 | 15.0523 | 15.0624 | 15.0332 | 15.3756 | 16.302 | 17.1234 | 17.5661 |  |  | 18142A | 33.9027 | 29.4033 | 28.389 | 28.6166 | 28.1502 | 28.1323 | 28.1738 | 28.2998 | 28.6746 | 29.8585 | 30.8254 | 31.4684
18142B | 32.0712 | 27.17 | 27.9392 | 27.8533 | 27.3841 | 27.0513 | 27.0694 | 27.017 | 27.6323 | 29.2971 | 30.7734 | 31.569 |  |  | 18142B | 43.7114 | 37.1042 | 35.8243 | 36.1115 | 35.5229 | 35.5003 | 35.5527 | 35.7116 | 36.1846 | 37.6786 | 38.8987 | 39.7101
18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18143B | 148.2572 | 94.1795 | 96.8455 | 96.5479 | 94.9216 | 93.7678 | 93.8305 | 93.649 | 95.7818 | 101.5526 | 106.6697 | 109.4275 |  |  | 18143B | 263.2392 | 229.0104 | 221.1108 | 222.8834 | 219.2507 | 219.1115 | 219.4347 | 220.4154 | 223.3349 | 232.5562 | 240.0864 | 245.0945
18144A | 64.3699 | 37.6158 | 38.6807 | 38.5618 | 37.9123 | 37.4514 | 37.4765 | 37.404 | 38.2558 | 40.5607 | 42.6045 | 43.706 |  |  | 18144A | 118.1078 | 106.47 | 102.7974 | 103.6215 | 101.9326 | 101.8679 | 102.0181 | 102.4741 | 103.8314 | 108.1185 | 111.6194 | 113.9477
18144B | 87.2078 | 70.9893 | 72.9989 | 72.7745 | 71.5487 | 70.679 | 70.7263 | 70.5895 | 72.1971 | 76.547 | 80.4041 | 82.4828 |  |  | 18144B | 207.6075 | 147.6451 | 142.5521 | 143.6949 | 141.3529 | 141.2632 | 141.4715 | 142.1039 | 143.9861 | 149.9311 | 154.7859 | 158.0147
18145A | 49.9983 | 34.5626 | 35.541 | 35.4318 | 34.835 | 34.4115 | 34.4345 | 34.3679 | 35.1506 | 37.2685 | 39.1464 | 40.1584 |  |  | 18145A | 66.6123 | 57.1594 | 55.1877 | 55.6301 | 54.7234 | 54.6887 | 54.7693 | 55.0141 | 55.7428 | 58.0444 | 59.9239 | 61.1738
18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18146A | 117.3616 | 77.4322 | 79.6242 | 79.3794 | 78.0424 | 77.0937 | 77.1453 | 76.996 | 78.7496 | 83.4942 | 87.7014 | 89.9688 |  |  | 18146A | 188.6115 | 178.656 | 172.4933 | 173.8761 | 171.0422 | 170.9336 | 171.1857 | 171.9508 | 174.2284 | 181.4221 | 187.2966 | 191.2035
18146B | 172.376 | 112.1189 | 115.2928 | 114.9384 | 113.0024 | 111.6289 | 111.7035 | 111.4874 | 114.0264 | 120.8965 | 126.9883 | 130.2714 |  |  | 18146B | 346.9505 | 284.748 | 274.9257 | 277.1297 | 272.6129 | 272.4398 | 272.8416 | 274.0611 | 277.6912 | 289.1567 | 298.5197 | 304.7467
Substation Load profile data
Winter percentage change
Season | Substation | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Summer | Arthurs Lake (DL) | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Avoca | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Bridgewater | 0.028308 | -0.0030736 | 0.0012243 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Burnie | 0.05824 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Chapel Street | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Creek Road | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Derby | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Derwent Bridge | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Devonport | 0.042125 | 0.024964 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Electrona | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Emu Bay (RT) | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | George Town | 0.057813 | 0.13997 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Hadspen | 0.053254 | -0.0030736 | 0.0232 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Huon River | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Kermandie | 0.028308 | -0.0030736 | -0.016844 | 0.09819 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Kingston 11kV | 0.028308 | 0.036484 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Kingston 33kV | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Knights Road | 0.028308 | -0.0030736 | -0.016844 | 0.17437 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Lindisfarne | 0.028308 | 0.073129 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Meadowbank | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Mornington | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Mowbray | 0.056168 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | New Norfolk | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Newton (Henty Goldmine) | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | North Hobart | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Norwood | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Palmerston | 0.16141 | -0.0030736 | 0.14541 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Port Latta (RT) | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Queenstown | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Railton | 0.032881 | 0.0032577 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Risdon 33kV | 0.028308 | 0.0025155 | 0.018212 | -0.0034067 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Rokeby | 0.084146 | -0.0030736 | 0.012932 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Rosebery 22kV | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Rosebery 44kV | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Savage River DL | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Scottsdale | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Sheffield | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Smithton | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Sorell | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | St Leonards | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | St Marys | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Trevallyn | 0.028308 | 0.0059797 | 0.0046055 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Triabunna (RT) | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Tungatinah | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Ulverstone | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Waddamana | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Summer | Wesley Vale | 0.028308 | -0.0030736 | -0.016844 | -0.012155 | 0.00066847 | -0.0019346 | 0.022774 | 0.06025 | 0.050389 | 0.025853
Winter | Arthurs Lake (DL) | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Avoca | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Bridgewater | -0.034495 | 0.0080168 | -0.0047269 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Burnie | -0.015718 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Chapel Street | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Creek Road | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Derby | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Derwent Bridge | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Devonport | -0.026042 | 0.026575 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Electrona | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Emu Bay (RT) | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | George Town | -0.018539 | 0.092314 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Hadspen | -0.020985 | 0.0080168 | 0.0070446 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Huon River | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Kermandie | -0.034495 | 0.0080168 | -0.016299 | 0.082987 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Kingston 11kV | -0.034495 | 0.031464 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Kingston 33kV | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Knights Road | -0.034495 | 0.0080168 | -0.016299 | 0.13808 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Lindisfarne | -0.034495 | 0.054022 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Meadowbank | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Mornington | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Mowbray | -0.021442 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | New Norfolk | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Newton (Henty Goldmine) | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | North Hobart | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Norwood | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Palmerston | 0.20277 | 0.0080168 | 0.26314 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Port Latta (RT) | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Queenstown | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Railton | -0.030255 | 0.014339 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Risdon 33kV | -0.034495 | 0.011909 | 0.007899 | 0.0055367 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Rokeby | -0.0045086 | 0.0080168 | 0.0011255 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Rosebery 22kV | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Rosebery 44kV | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Savage River DL | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Scottsdale | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Sheffield | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Smithton | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Sorell | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | St Leonards | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | St Marys | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Trevallyn | -0.034495 | 0.012945 | -0.004697 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Triabunna (RT) | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Tungatinah | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Ulverstone | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Waddamana | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Winter | Wesley Vale | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
|  | -0.034495 | 0.0080168 | -0.016299 | -0.00063489 | 0.001475 | 0.0044696 | 0.013245 | 0.041289 | 0.03238 | 0.02086
Substation
Feeder
Growth
Zone
Additional Information