## Disclaimer
TasNetworks – Annual Planning Report 2026 – Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2025.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Assumptions + methodology
Tx-Dx connection points | Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Appendix A.3.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix C of this APR.
Distribution line max. demand |  | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Appendix A.3.2 of this APR.
Updated 27 October 2026

## Tx-Dx connection points
|  |  |  | Planning area |  |  |  | Greater Hobart
| Transmission-distribution connection point: |  |  | Supplying |  |  |  | Distribution lines
| North Hobart |  |  | Voltage |  |  |  | 110/11 kV
|  |  |  | Number of transformers |  |  |  | 2
|  |  |  | Peaking season |  |  |  | Winter
Forecast | Parameter |  | 2025 (Actuals) | 2026 (Actuals) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
| Firm delivery | Substation capacity (winter and summer) (MVA) Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Maximum demand forecast | Maximum demand (MW) | Maximum demand (peak season) (MW) | 36.7547 | 36.9917 | 36.9843 | 37.4552 | 38.1265 | 38.9247 | 39.6203 | 40.1468 | 40.3974 | 40.6112 | 40.752 | 41.1377
| Reactive power (coincident) (MVAr) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9572 | 1.9698 | 1.9694 | 1.9945 | 2.0302 | 2.0727 | 2.1098 | 2.1378 | 2.1511 | 2.1625 | 2.17 | 2.1905
(Winter peak) | Maximum demand (MVA) | Maximum demand (peak season) (MVA) | 36.8068 | 37.0442 | 37.0367 | 37.5082 | 38.1805 | 38.9799 | 39.6764 | 40.2037 | 40.4547 | 40.6688 | 40.8097 | 41.1959
| Power factor (coincident) | Maximum demand (peak season) Power factor (coincident) | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859
|  | Maximum demand (non-peak season) (MW) | 16.7929 | 17.6608 | 17.9392 | 18.4044 | 18.9493 | 19.565 | 20.0868 | 20.6895 | 20.9622 | 21.23 | 21.4289 | 21.598
Maximum demand forecast | Maximum demand (MW) | Maximum demand (peak season) (MW) | 16.7929 | 17.6608 | 17.9392 | 18.4044 | 18.9493 | 19.565 | 20.0868 | 20.6895 | 20.9622 | 21.23 | 21.4289 | 21.598
(Summer) | Reactive power (coincident) (MVAr) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9783 | 2.0805 | 2.1133 | 2.1681 | 2.2323 | 2.3048 | 2.3663 | 2.4373 | 2.4694 | 2.501 | 2.5244 | 2.5443
| Maximum demand (MVA) | Maximum demand (peak season) (MVA) | 16.909 | 17.7829 | 18.0633 | 18.5316 | 19.0803 | 19.7003 | 20.2257 | 20.8325 | 21.1071 | 21.3768 | 21.5771 | 21.7474
| Power factor (coincident) | Maximum demand (Summer) Power factor (coincident) | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313 | 0.99313
Hours exceeding | 95% of maximum demand | Hours exceeding 95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Regional diversity factor | Summer | Regional Diversity Factor (Summer) | 0.88363
| Winter | Regional Diversity Factor (Winter) | 1
Load transfer capacity (MVA) |  | Load transfer capacity (MVA)1
Load transfer capacity (MVA)2
Load transfer capacity (MVA)3
Load transfer capacity (MVA)4
Load transfer capacity (MVA)5
Embedded generation capacity | Units less than 100 kVA | Embedded generation capacity (MVA) Units less than 100 kVA | 14.614
| Units greater than 100 kVA | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.06
| DER generation contribution (MW) | Embedded generation forecast capacity (MVA) | 3.1704 | 3.8227 | 4.4114 | 4.959 | 5.4283 | 6.5693 | 7.7365 | 8.8146 | 9.7769 | 10.6262 | 11.4531 | 12.2613
| Notes | TRUE
TRUE
TRUE
#VALUE!
[13 empty] | 2035 | 2036
[13 empty] | 45 | 45
[13 empty] | 50 | 50
[13 empty] | 40.8097 | 41.1959
TRUE
TRUE
TRUE
xxc

## Zone subs & sub-trans lines
|  |  |  | Planning area |  |  |  | Greater Hobart
| Zone substation: |  |  | Supplying |  |  |  | Distribution lines
| Zs-Cambridge |  |  | Voltage |  |  |  | 33/11 kV
|  |  |  | Number of transformers |  |  |  | 2
|  |  |  | Peaking season |  |  |  | Winter
|  |  |  | Subtransmission lines |  |  |  | 29481,29482,29483,29485,29486,29488,29489,29490,29491,29492
|  |  |  | Source Substation |  |  |  | Mornington, Lindisfarne
Forecast | Parameter |  | 2025 (Actuals) | 2026 (Actuals) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Firm delivery | Substation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Short-term firm delivery | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Sub-transmission line capacity (MVA) | Total (winter) | Sub-transmission lines capacityTotal (winter) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
| Firm delivery (winter) | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total (summer) | Sub-transmission lines capacityTotal (summer) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
| Firm delivery (summer) | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub-transmission line capacity (MVA) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(peak season)Maximum demand (MVA) | 7.2936 | 7.3407 | 7.3392 | 7.4326 | 7.5658 | 7.7242 | 7.8623 | 7.9668 | 8.0165 | 8.0589 | 8.0868 | 8.1634
(Winter) | Power factor (coincident) | Maximum demand forecast(peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 3.7738 | 3.9689 | 4.0314 | 4.136 | 4.2584 | 4.3968 | 4.514 | 4.6495 | 4.7108 | 4.7709 | 4.8157 | 4.8537
(Summer) | Power factor (coincident) | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Hours exceeding | 95% of maximum demand | Hours exceeding95% of maximum demand | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Load transfer capacity (MVA) | Rokeby | Load transfer capacity (MVA)1 | 7.4
| Bellerive | Load transfer capacity (MVA)2 | 7.4
Load transfer capacity (MVA)3
Load transfer capacity (MVA)4
|  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA)Units less than 100 kVA | 7.805
| Units greater than 100 kVA | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
DER Capacity (MW) | Embedded Generation |  | 1.3197 | 1.57 | 1.805 | 2.0038 | 2.1857 | 2.6288 | 3.0811 | 3.497 | 3.8641 | 4.1826 | 4.4855 | 4.7723
Notes

## Distribution feeder max. demand
|  |  | Summer (Amps) | [11 empty] | Winter (Amps) | [11 empty] | Feeder DER forecast (kVA) | [11 empty] | Embedded Generation (MVA)
Substation |  | Feeder | 2025 (Actual) | 2026 (Actual) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2025 (Actual) | 2026 (Actual) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Substation | <100kVA | >100kVA
Arthurs Lake (DL) |  | 49101 | 28.5997 | 30.078 | 30.5521 | 31.3443 | 32.2723 | 33.321 | 34.2096 | 35.236 | 35.7005 | 36.1566 | 36.4954 | 36.7834 | 31.3796 | 31.5819 | 31.5755 | 31.9775 | 32.5507 | 33.2322 | 33.826 | 34.2756 | 34.4895 | 34.6721 | 34.7922 | 35.1215 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752 | Arthurs Lake (DL) | 0.012 | 0
Avoca |  | 56001 | 10.9863 | 11.5542 | 11.7363 | 12.0406 | 12.3971 | 12.8 | 13.1413 | 13.5356 | 13.714 | 13.8892 | 14.0194 | 14.13 | 8.7278 | 8.784 | 8.7823 | 8.8941 | 9.0535 | 9.243 | 9.4082 | 9.5332 | 9.5927 | 9.6435 | 9.6769 | 9.7685 | 8.6 | 8.6 | 8.6 | 11.7142 | 16.6279 | 28.4426 | 40.4017 | 51.326 | 60.9545 | 69.3228 | 77.3194 | 84.9573 | Avoca | 3.267 | 0
Avoca |  | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 1.02 | 1.8666 | 4.3972 | 9.025 | 21.9627 | 37.1594 | 53.1527 | 69.1683 | 84.637 | 100.581 | 112.5889 | Bridgewater | 21.781 | 0.012
Avoca |  | 56003 | 34.8986 | 36.7024 | 37.281 | 38.2477 | 39.38 | 40.6597 | 41.744 | 42.9965 | 43.5632 | 44.1198 | 44.5332 | 44.8846 | 46.207 | 46.5049 | 46.4955 | 47.0875 | 47.9315 | 48.935 | 49.8095 | 50.4714 | 50.7865 | 51.0553 | 51.2322 | 51.7171 | 60.6007 | 64.1868 | 66.4644 | 87.6891 | 111.8686 | 170.1053 | 228.8581 | 282.0503 | 328.299 | 367.8568 | 405.1008 | 440.3642 | Burnie | 32.961 | 0.003
Avoca |  | 56004 | 202.7049 | 213.1821 | 216.5427 | 222.1575 | 228.7349 | 236.1674 | 242.4657 | 249.7407 | 253.0324 | 256.2655 | 258.6667 | 260.7078 | 142.6258 | 143.5455 | 143.5165 | 145.3438 | 147.9489 | 151.0464 | 153.7455 | 155.7887 | 156.7612 | 157.5909 | 158.137 | 159.6337 | 217.2836 | 233.1907 | 258.0153 | 325.8749 | 428.5504 | 686.3504 | 958.2859 | 1216.4902 | 1452.6481 | 1665.6054 | 1876.9879 | 2087.1187 | Chapel Street | 20.875 | 0
Bridgewater |  | 48180 | 100.388 | 105.5767 | 107.241 | 110.0217 | 113.2791 | 116.96 | 120.0792 | 123.6821 | 125.3123 | 126.9134 | 128.1026 | 129.1134 | 247.2749 | 248.8694 | 248.8191 | 251.9871 | 256.5037 | 261.8739 | 266.5535 | 270.0958 | 271.7818 | 273.2203 | 274.1671 | 276.7619 | 660.4669 | 747.5639 | 847.6685 | 903.4352 | 962.5945 | 1105.8939 | 1251.5968 | 1385.0979 | 1503.3169 | 1607.1916 | 1708.7088 | 1809.6217 | Creek Road | 0 | 0
Bridgewater |  | 48181 | 114.7471 | 120.678 | 122.5803 | 125.7588 | 129.4821 | 133.6895 | 137.2548 | 141.3731 | 143.2365 | 145.0666 | 146.4259 | 147.5813 | 147.3407 | 148.2908 | 148.2608 | 150.1485 | 152.8397 | 156.0396 | 158.828 | 160.9387 | 161.9434 | 162.8004 | 163.3646 | 164.9108 | 0 | 0 | 0 | 5.884 | 15.7816 | 41.3761 | 69.3631 | 96.9498 | 123.0133 | 147.0251 | 171.0089 | 194.5868 | Derby | 2.841 | 0.012
Bridgewater |  | 48182 | 80.5989 | 84.7648 | 86.101 | 88.3336 | 90.9489 | 93.9042 | 96.4084 | 99.3011 | 100.61 | 101.8955 | 102.8503 | 103.6618 | 138.7082 | 139.6027 | 139.5744 | 141.3515 | 143.8851 | 146.8975 | 149.5225 | 151.5095 | 152.4553 | 153.2622 | 153.7933 | 155.2489 | 331.5008 | 381.5806 | 437.1033 | 468.4699 | 500.7511 | 578.0154 | 655.7406 | 726.3027 | 789.4496 | 845.8678 | 902.0635 | 958.7247 | Derwent Bridge | 0.055 | 0
Bridgewater |  | 48183 | 108.0736 | 113.6596 | 115.4513 | 118.4449 | 121.9517 | 125.9144 | 129.2724 | 133.1511 | 134.9061 | 136.6298 | 137.9101 | 138.9983 | 172.8288 | 173.9433 | 173.9081 | 176.1223 | 179.2791 | 183.0325 | 186.3032 | 188.7791 | 189.9575 | 190.9629 | 191.6247 | 193.4383 | 234.026 | 259.0423 | 285.6377 | 324.8051 | 377.0488 | 506.4273 | 641.1517 | 767.1954 | 880.2958 | 979.6949 | 1075.0379 | 1165.743 | Devonport | 24.972 | 0.013
Bridgewater |  | 48184 | 127.9813 | 134.5963 | 136.718 | 140.2631 | 144.4158 | 149.1085 | 153.085 | 157.6782 | 159.7565 | 161.7978 | 163.3138 | 164.6025 | 211.8556 | 213.2217 | 213.1785 | 215.8928 | 219.7624 | 224.3634 | 228.3727 | 231.4076 | 232.8521 | 234.0845 | 234.8958 | 237.1189 | 201.0393 | 224.8634 | 246.5488 | 292.1757 | 362.95 | 540.8383 | 728.6096 | 906.7501 | 1068.9497 | 1213.6493 | 1354.5103 | 1490.5038 | Electrona | 20.258 | 0
Bridgewater |  | 48185 | 41.5983 | 43.7484 | 44.438 | 45.5903 | 46.9401 | 48.4654 | 49.7579 | 51.2508 | 51.9263 | 52.5898 | 53.0826 | 53.5014 | 226.3515 | 227.811 | 227.765 | 230.6649 | 234.7993 | 239.7151 | 243.9987 | 247.2413 | 248.7847 | 250.1014 | 250.9682 | 253.3434 | 244.0292 | 251.9176 | 278.5244 | 299.03 | 324.6697 | 391.0937 | 464.647 | 538.8557 | 611.1812 | 680.1165 | 751.1359 | 819.4664 | Emu Bay (RT) | 0 | 0
Bridgewater |  | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | George Town | 18.704 | 0.012
Bridgewater |  | 48188 | 5.8319 | 6.1334 | 6.2301 | 6.3916 | 6.5808 | 6.7947 | 6.9759 | 7.1852 | 7.2799 | 7.3729 | 7.442 | 7.5007 | 9.6998 | 9.7623 | 9.7604 | 9.8846 | 10.0618 | 10.2725 | 10.456 | 10.595 | 10.6611 | 10.7175 | 10.7547 | 10.8565 | 0 | 0 | 0 | 0.99282 | 2.5383 | 6.2037 | 9.864 | 13.1636 | 16.0348 | 18.4998 | 20.8278 | 23.0269 | Hadspen | 32.642 | 0.043
Bridgewater |  | 48189 | 51.0391 | 53.6771 | 54.5233 | 55.937 | 57.5932 | 59.4646 | 61.0504 | 62.8822 | 63.711 | 64.5251 | 65.1297 | 65.6436 | 97.7771 | 98.4076 | 98.3877 | 99.6404 | 101.4264 | 103.5498 | 105.4002 | 106.8009 | 107.4676 | 108.0364 | 108.4108 | 109.4368 | 174.3028 | 198.9489 | 254.9992 | 280.4968 | 310.5765 | 383.7308 | 458.0147 | 525.4487 | 583.9413 | 633.4964 | 679.2279 | 721.0647 | Huon River | 0.012 | 0
Bridgewater |  | 48190 | 137.422 | 144.5249 | 146.8031 | 150.6097 | 155.0688 | 160.1076 | 164.3774 | 169.3094 | 171.5411 | 173.7329 | 175.3608 | 176.7445 | 237.9058 | 239.4398 | 239.3914 | 242.4394 | 246.7848 | 251.9516 | 256.4538 | 259.8619 | 261.4841 | 262.868 | 263.779 | 266.2755 | 464.4354 | 506.4946 | 558.6045 | 630.4422 | 719.7431 | 939.5299 | 1168.0468 | 1383.1976 | 1579.3522 | 1756.0055 | 1931.8234 | 2103.3264 | Kermandie | 8.18 | 0
Bridgewater |  | 48191 | 44.6208 | 46.9271 | 47.6669 | 48.9029 | 50.3507 | 51.9868 | 53.3733 | 54.9747 | 55.6993 | 56.411 | 56.9395 | 57.3888 | 68.6974 | 69.1404 | 69.1264 | 70.0065 | 71.2613 | 72.7533 | 74.0533 | 75.0374 | 75.5059 | 75.9055 | 76.1685 | 76.8894 | 43.2908 | 49.4918 | 49.4918 | 76.9777 | 105.2535 | 176.2571 | 250.8717 | 321.001 | 383.8956 | 438.8281 | 490.8853 | 539.5768 | Kingston 11kV | 22.799 | 0.005
Bridgewater |  | 48192 | 121.1949 | 127.459 | 129.4683 | 132.8253 | 136.7579 | 141.2017 | 144.9673 | 149.317 | 151.2851 | 153.2181 | 154.6538 | 155.8741 | 212.3564 | 213.7257 | 213.6825 | 216.4031 | 220.2819 | 224.8937 | 228.9125 | 231.9546 | 233.4026 | 234.6378 | 235.451 | 237.6794 | 1085.804 | 1241.522 | 1381.3855 | 1496.9536 | 1571.1659 | 1750.2166 | 1930.9832 | 2095.5767 | 2239.6558 | 2363.7132 | 2480.9133 | 2591.3317 | Kingston 33kV | 0 | 0
Bridgewater |  | 48193 | 101.0763 | 106.3006 | 107.9763 | 110.7761 | 114.0558 | 117.7619 | 120.9025 | 124.5301 | 126.1715 | 127.7836 | 128.9809 | 129.9987 | 181.4505 | 182.6205 | 182.5836 | 184.9083 | 188.2226 | 192.1632 | 195.5971 | 198.1964 | 199.4337 | 200.4892 | 201.184 | 203.0881 | 367.5899 | 433.7158 | 507.872 | 547.4143 | 609.7618 | 758.5757 | 906.9783 | 1039.4505 | 1152.6227 | 1247.2114 | 1333.4592 | 1411.5212 | Knights Road | 16.562 | 0.024
Burnie |  | 91001 | 124.8322 | 131.2844 | 133.354 | 136.8118 | 140.8623 | 145.4395 | 149.3182 | 153.7984 | 155.8255 | 157.8166 | 159.2953 | 160.5523 | 163.633 | 164.6882 | 164.6549 | 166.7513 | 169.7401 | 173.2938 | 176.3905 | 178.7346 | 179.8504 | 180.8022 | 181.4288 | 183.1459 | 173.5106 | 187.7696 | 211.5764 | 243.9034 | 286.8892 | 391.9037 | 500.1816 | 601.119 | 691.9964 | 772.6548 | 851.2056 | 925.136 | Lindisfarne | 0 | 0
Burnie |  | 91002 | 71.3442 | 75.0318 | 76.2146 | 78.1908 | 80.5058 | 83.1217 | 85.3385 | 87.899 | 89.0576 | 90.1955 | 91.0406 | 91.759 | 49.5111 | 49.8303 | 49.8202 | 50.4546 | 51.3589 | 52.4342 | 53.3711 | 54.0804 | 54.418 | 54.706 | 54.8956 | 55.4151 | 112.13 | 121.766 | 124.5908 | 151.3286 | 191.6097 | 292.0459 | 397.9253 | 499.0121 | 592.386 | 677.553 | 762.8945 | 848.0334 | Meadowbank | 1.743 | 0.012
Burnie |  | 91003 | 122.9881 | 129.345 | 131.384 | 134.7907 | 138.7815 | 143.291 | 147.1124 | 151.5264 | 153.5236 | 155.4852 | 156.9421 | 158.1805 | 179.048 | 180.2026 | 180.1661 | 182.46 | 185.7304 | 189.6189 | 193.0073 | 195.5722 | 196.7931 | 197.8346 | 198.5202 | 200.3991 | 270.3893 | 350.4648 | 412.7949 | 453.7536 | 512.5792 | 658.4237 | 811.4178 | 957.1756 | 1092.0951 | 1215.9708 | 1341.373 | 1468.1429 | Mornington | 0 | 0
Burnie |  | 91004 | 102.7793 | 108.0916 | 109.7955 | 112.6425 | 115.9775 | 119.746 | 122.9395 | 126.6282 | 128.2973 | 129.9365 | 131.1541 | 132.1889 | 128.3091 | 129.1364 | 129.1103 | 130.7542 | 133.0978 | 135.8844 | 138.3126 | 140.1506 | 141.0255 | 141.7719 | 142.2632 | 143.6096 | 271.3375 | 279.219 | 302.8929 | 333.1866 | 372.0808 | 467.3226 | 566.0821 | 659.2428 | 744.9622 | 823.8039 | 904.754 | 987.2062 | Mowbray | 12.604 | 0.012
Burnie |  | 91005 | 63.0409 | 66.2993 | 67.3444 | 69.0906 | 71.1361 | 73.4476 | 75.4064 | 77.6689 | 78.6926 | 79.6981 | 80.4449 | 81.0796 | 130.7204 | 131.5633 | 131.5367 | 133.2115 | 135.5991 | 138.4381 | 140.9119 | 142.7845 | 143.6758 | 144.4363 | 144.9368 | 146.3085 | 559.8906 | 659.1229 | 736.9646 | 808.7196 | 882.4541 | 1058.8673 | 1236.5609 | 1398.1654 | 1539.9981 | 1662.5536 | 1778.4385 | 1885.293 | New Norfolk | 5.83 | 0.012
Burnie |  | 91006 | 121.6621 | 127.9505 | 129.9674 | 133.3374 | 137.2851 | 141.7461 | 145.5263 | 149.8927 | 151.8683 | 153.8088 | 155.25 | 156.475 | 259.1662 | 260.8373 | 260.7846 | 264.105 | 268.8387 | 274.4672 | 279.3718 | 283.0844 | 284.8516 | 286.3592 | 287.3516 | 290.0712 | 664.9257 | 769.9682 | 836.7409 | 967.3153 | 1087.5055 | 1376.636 | 1668.5406 | 1933.8902 | 2166.4857 | 2367.838 | 2560.1703 | 2744.8695 | Newton | 0 | 0
Burnie |  | 91007 | 81.8289 | 86.0584 | 87.415 | 89.6816 | 92.3368 | 95.3372 | 97.8797 | 100.8165 | 102.1454 | 103.4505 | 104.4199 | 105.2438 | 174.9971 | 176.1255 | 176.0899 | 178.3319 | 181.5283 | 185.3288 | 188.6406 | 191.1475 | 192.3407 | 193.3587 | 194.0288 | 195.8651 | 748.9674 | 871.9782 | 1018.0627 | 1163.9173 | 1304.9536 | 1653.8602 | 2016.9242 | 2356.6455 | 2661.4096 | 2928.611 | 3183.3204 | 3423.1054 | North Hobart | 14.614 | 0.06
Burnie |  | 91008 | 68.8823 | 72.4426 | 73.5846 | 75.4926 | 77.7277 | 80.2534 | 82.3936 | 84.8658 | 85.9844 | 87.083 | 87.899 | 88.5926 | 157.2194 | 158.2332 | 158.2012 | 160.2155 | 163.0872 | 166.5016 | 169.4769 | 171.7291 | 172.8011 | 173.7157 | 174.3177 | 175.9675 | 669.3927 | 810.1297 | 936.3237 | 1047.7339 | 1163.8933 | 1445.197 | 1730.6166 | 1990.6002 | 2218.0414 | 2413.6637 | 2598.5694 | 2773.8732 | Norwood | 17.898 | 0.035
Burnie |  | 91009 | 78.2928 | 82.3396 | 83.6375 | 85.8062 | 88.3467 | 91.2174 | 93.65 | 96.46 | 97.7314 | 98.9801 | 99.9076 | 100.6959 | 164.0962 | 165.1543 | 165.1209 | 167.2232 | 170.2205 | 173.7843 | 176.8897 | 179.2405 | 180.3594 | 181.3139 | 181.9423 | 183.6643 | 674.1934 | 788.7008 | 926.9005 | 1040.1925 | 1161.8077 | 1457.1231 | 1758.9725 | 2037.7036 | 2286.8434 | 2507.6861 | 2724.5092 | 2938.999 | Palmerston | 2.801 | 0.024
Burnie |  | 91010 | 74.4226 | 78.2692 | 79.5031 | 81.5645 | 83.9794 | 86.7082 | 89.0206 | 91.6916 | 92.9002 | 94.0872 | 94.9688 | 95.7182 | 179.1394 | 180.2946 | 180.2581 | 182.5532 | 185.8252 | 189.7157 | 193.1059 | 195.6721 | 196.8936 | 197.9356 | 198.6216 | 200.5014 | 422.9673 | 480.8486 | 550.9575 | 624.5841 | 666.9142 | 769.1208 | 872.8447 | 967.8251 | 1051.9278 | 1125.722 | 1197.4192 | 1267.6616 | Port Latta (RT) | 0 | 0
Burnie |  | 91011 | 84.5095 | 88.8775 | 90.2786 | 92.6195 | 95.3616 | 98.4603 | 101.0861 | 104.1191 | 105.4915 | 106.8394 | 107.8405 | 108.6914 | 100.3084 | 100.9552 | 100.9348 | 102.2199 | 104.0521 | 106.2305 | 108.1288 | 109.5658 | 110.2498 | 110.8333 | 111.2174 | 112.27 | 381.8218 | 455.329 | 518.9976 | 569.5743 | 638.2226 | 805.6658 | 977.6394 | 1137.1017 | 1279.8603 | 1405.8859 | 1527.9483 | 1643.0381 | Queenstown | 2.329 | 0
Burnie |  | 91012 | 88.5541 | 93.1312 | 94.5993 | 97.0522 | 99.9257 | 103.1726 | 105.9241 | 109.1023 | 110.5403 | 111.9527 | 113.0017 | 113.8934 | 62.6708 | 63.0749 | 63.0621 | 63.8651 | 65.0098 | 66.3708 | 67.5568 | 68.4546 | 68.8819 | 69.2465 | 69.4865 | 70.1441 | 147.1906 | 147.1906 | 155.8426 | 203.6749 | 261.1367 | 402.9261 | 550.5325 | 689.1565 | 814.5524 | 926.1195 | 1034.99 | 1138.5939 | Railton | 21.624 | 0.042
Chapel Street |  | 20534 | 27.6333 | 29.0616 | 29.5197 | 30.2851 | 31.1818 | 32.195 | 33.0536 | 34.0453 | 34.4941 | 34.9348 | 35.2622 | 35.5404 | 56.3236 | 56.6868 | 56.6753 | 57.3969 | 58.4257 | 59.6489 | 60.7148 | 61.5216 | 61.9057 | 62.2333 | 62.449 | 63.04 | 56.544 | 66.805 | 80.6605 | 95.587 | 112.7661 | 154.2047 | 196.108 | 234.2336 | 267.7037 | 296.8239 | 325.0241 | 352.9433 | Risdon 33kV | 0 | 0
Chapel Street |  | 20535 | 60.0821 | 63.1876 | 64.1836 | 65.8479 | 67.7975 | 70.0005 | 71.8673 | 74.0236 | 74.9993 | 75.9576 | 76.6693 | 77.2743 | 146.8833 | 147.8304 | 147.8005 | 149.6823 | 152.3652 | 155.5551 | 158.3349 | 160.439 | 161.4405 | 162.295 | 162.8574 | 164.3988 | 282.2252 | 330.2581 | 371.8596 | 434.1297 | 490.6644 | 626.3771 | 762.5615 | 884.935 | 990.1905 | 1078.7473 | 1159.9938 | 1233.9343 | Rokeby | 20.966 | 0.012
Chapel Street |  | 20536 | 58.2182 | 61.2273 | 62.1924 | 63.8051 | 65.6941 | 67.8288 | 69.6377 | 71.7271 | 72.6725 | 73.6011 | 74.2908 | 74.877 | 139.0365 | 139.933 | 139.9047 | 141.686 | 144.2256 | 147.2451 | 149.8763 | 151.868 | 152.8161 | 153.6249 | 154.1573 | 155.6163 | 320.6956 | 375.9192 | 443.64 | 494.0698 | 546.6423 | 673.1191 | 800.3144 | 914.8553 | 1013.5756 | 1096.794 | 1173.2803 | 1243.0056 | Rosebery 22kV | 1.195 | 0.012
Chapel Street |  | 20537 | 51.8234 | 54.502 | 55.3612 | 56.7967 | 58.4783 | 60.3784 | 61.9887 | 63.8486 | 64.6901 | 65.5167 | 66.1306 | 66.6524 | 119.4662 | 120.2365 | 120.2122 | 121.7428 | 123.9249 | 126.5194 | 128.7802 | 130.4916 | 131.3062 | 132.0011 | 132.4586 | 133.7122 | 221.3492 | 248.6398 | 291.6668 | 330.7103 | 372.3801 | 472.8851 | 574.231 | 665.7481 | 744.8531 | 811.7388 | 873.4109 | 929.8228 | Rosebery 44kV | 0 | 0
Chapel Street |  | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Savage River DL | 0 | 0
Chapel Street |  | 20539 | 18.6813 | 19.6469 | 19.9566 | 20.4741 | 21.0803 | 21.7653 | 22.3457 | 23.0162 | 23.3195 | 23.6175 | 23.8388 | 24.0269 | 35.1369 | 35.3635 | 35.3564 | 35.8065 | 36.4483 | 37.2114 | 37.8763 | 38.3797 | 38.6193 | 38.8237 | 38.9582 | 39.3269 | 41.9247 | 48.6327 | 50.0916 | 57.5951 | 69.9395 | 100.3778 | 131.3692 | 159.2867 | 183.1127 | 202.8547 | 220.6152 | 236.4372 | Scottsdale | 9.851 | 0.012
Chapel Street |  | 20540 | 98.6111 | 103.708 | 105.3428 | 108.0743 | 111.274 | 114.8898 | 117.9537 | 121.4928 | 123.0942 | 124.667 | 125.8351 | 126.828 | 116.7277 | 117.4804 | 117.4567 | 118.9522 | 121.0842 | 123.6193 | 125.8283 | 127.5005 | 128.2964 | 128.9754 | 129.4224 | 130.6473 | 7.05 | 7.05 | 7.05 | 12.5131 | 20.9057 | 40.4668 | 59.6238 | 76.5594 | 91.0235 | 103.2109 | 114.4831 | 124.8608 | Sheffield | 0 | 0
Chapel Street |  | 20541 | 108.1917 | 113.7838 | 115.5775 | 118.5744 | 122.085 | 126.052 | 129.4136 | 133.2966 | 135.0536 | 136.7792 | 138.0608 | 139.1502 | 214.8713 | 216.2568 | 216.2131 | 218.966 | 222.8906 | 227.5571 | 231.6235 | 234.7016 | 236.1667 | 237.4166 | 238.2394 | 240.4942 | 465.8514 | 490.1162 | 549.3372 | 600.67 | 637.9651 | 727.8248 | 818.981 | 902.7048 | 977.4676 | 1044.1097 | 1110.4598 | 1177.6758 | Smithton | 6.168 | 0.024
Chapel Street |  | 20544 | 69.562 | 73.1574 | 74.3106 | 76.2375 | 78.4946 | 81.0452 | 83.2066 | 85.7031 | 86.8328 | 87.9422 | 88.7663 | 89.4667 | 142.8665 | 143.7878 | 143.7587 | 145.5891 | 148.1986 | 151.3013 | 154.005 | 156.0516 | 157.0257 | 157.8568 | 158.4039 | 159.903 | 229.0522 | 275.0173 | 305.6281 | 338.396 | 381.8963 | 486.2887 | 590.9318 | 684.7837 | 765.2968 | 832.8305 | 894.5963 | 950.6435 | Sorell | 32.257 | 0.022
Chapel Street |  | 20545 | 25.9954 | 27.3391 | 27.77 | 28.4901 | 29.3336 | 30.2868 | 31.0945 | 32.0274 | 32.4496 | 32.8642 | 33.1721 | 33.4339 | 52.7131 | 53.053 | 53.0423 | 53.7176 | 54.6805 | 55.8253 | 56.8228 | 57.578 | 57.9374 | 58.244 | 58.4459 | 58.999 | 69.8978 | 95.2289 | 102.6556 | 116.8601 | 139.4224 | 193.6959 | 248.2641 | 297.3904 | 339.7232 | 375.4073 | 408.2098 | 438.1235 | St Leonards | 15.206 | 0.012
Chapel Street |  | 20547 | 119.4716 | 125.6467 | 127.6273 | 130.9366 | 134.8133 | 139.1939 | 142.906 | 147.1938 | 149.1339 | 151.0394 | 152.4547 | 153.6576 | 276.527 | 278.3102 | 278.2539 | 281.7967 | 286.8475 | 292.853 | 298.0862 | 302.0475 | 303.9331 | 305.5416 | 306.6005 | 309.5023 | 682.963 | 814.6864 | 934.7226 | 1025.3999 | 1128.8809 | 1379.3452 | 1633.3054 | 1864.4923 | 2066.5165 | 2239.6914 | 2401.9372 | 2552.9315 | St Marys | 15.463 | 0
Chapel Street |  | 20548 | 83.2248 | 87.5265 | 88.9062 | 91.2115 | 93.912 | 96.9636 | 99.5494 | 102.5363 | 103.8878 | 105.2152 | 106.2011 | 107.0391 | 216.5132 | 217.9094 | 217.8653 | 220.6392 | 224.5939 | 229.296 | 233.3935 | 236.4951 | 237.9714 | 239.2309 | 240.0599 | 242.3319 | 345.4435 | 418.9402 | 489.3717 | 558.912 | 605.654 | 718.7634 | 834.0391 | 940.3909 | 1035.7519 | 1121.1197 | 1206.6616 | 1294.4486 | Trevallyn | 46.227 | 0.06
Chapel Street |  | 20549 | 69.8381 | 73.4478 | 74.6056 | 76.5401 | 78.8062 | 81.367 | 83.5369 | 86.0434 | 87.1775 | 88.2914 | 89.1187 | 89.8219 | 149.2132 | 150.1754 | 150.145 | 152.0567 | 154.7821 | 158.0227 | 160.8465 | 162.984 | 164.0014 | 164.8694 | 165.4408 | 167.0066 | 435.9942 | 524.2975 | 580.0835 | 625.8345 | 677.2957 | 800.7522 | 924.5593 | 1035.7425 | 1131.319 | 1211.6921 | 1285.3993 | 1352.455 | Triabunna (RT) | 0 | 0
Chapel Street |  | 20551 | 44.0356 | 46.3117 | 47.0417 | 48.2615 | 49.6904 | 51.305 | 52.6732 | 54.2537 | 54.9688 | 55.6711 | 56.1928 | 56.6362 | 45.7398 | 46.0347 | 46.0254 | 46.6114 | 47.4469 | 48.4402 | 49.3058 | 49.9611 | 50.273 | 50.539 | 50.7142 | 51.1941 | 61.1169 | 72.5118 | 99.3037 | 110.5026 | 124.5779 | 161.4434 | 201.8362 | 241.278 | 277.8056 | 310.5077 | 342.0349 | 371.8193 | Tungatinah | 0.228 | 0
Chapel Street |  | 20552 | 66.8096 | 70.2628 | 71.3704 | 73.221 | 75.3888 | 77.8385 | 79.9144 | 82.3121 | 83.3971 | 84.4627 | 85.2541 | 85.9268 | 153.8062 | 154.798 | 154.7667 | 156.7372 | 159.5465 | 162.8868 | 165.7975 | 168.0009 | 169.0496 | 169.9443 | 170.5333 | 172.1473 | 499.5989 | 576.2719 | 644.7789 | 691.8162 | 745.2409 | 873.3209 | 1001.7204 | 1117.0175 | 1216.139 | 1299.5099 | 1375.9872 | 1445.5861 | Ulverstone | 23.656 | 0.024
Chapel Street |  | 20553 | 71.9051 | 75.6216 | 76.8137 | 78.8055 | 81.1386 | 83.7752 | 86.0093 | 88.59 | 89.7576 | 90.9045 | 91.7563 | 92.4803 | 147.797 | 148.7501 | 148.72 | 150.6135 | 153.3131 | 156.5229 | 159.3199 | 161.4371 | 162.4449 | 163.3046 | 163.8706 | 165.4215 | 369.9958 | 434.7211 | 505.6074 | 587.6613 | 640.8216 | 773.6528 | 913.9908 | 1048.3145 | 1172.7382 | 1286.5228 | 1400.7268 | 1511.1612 | Waddamana | 0.791 | 0
Chapel Street |  | 20554 | 67.1399 | 70.6102 | 71.7233 | 73.583 | 75.7616 | 78.2234 | 80.3095 | 82.7191 | 83.8094 | 84.8803 | 85.6756 | 86.3516 | 119.0205 | 119.7879 | 119.7637 | 121.2886 | 123.4625 | 126.0473 | 128.2998 | 130.0048 | 130.8163 | 131.5087 | 131.9644 | 133.2134 | 115.8202 | 141.1866 | 160.4485 | 178.1953 | 203.1064 | 264.0228 | 326.5967 | 384.3571 | 435.4517 | 479.5981 | 521.0442 | 559.4499 | Wesley Vale | 10.335 | 0.019
Creek Road |  | 10001 | 88.6634 | 93.2462 | 94.7161 | 97.172 | 100.049 | 103.3 | 106.0549 | 109.237 | 110.6768 | 112.0909 | 113.1412 | 114.034 | 203.058 | 204.3674 | 204.3261 | 206.9276 | 210.6365 | 215.0465 | 218.8893 | 221.7981 | 223.1827 | 224.3639 | 225.1415 | 227.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Bellerive | 6.108 | 0.014
Creek Road |  | 10002 | 91.8241 | 96.5702 | 98.0925 | 100.6359 | 103.6155 | 106.9824 | 109.8354 | 113.131 | 114.6221 | 116.0866 | 117.1744 | 118.099 | 201.5688 | 202.8686 | 202.8276 | 205.41 | 209.0918 | 213.4693 | 217.2839 | 220.1715 | 221.5459 | 222.7184 | 223.4903 | 225.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Cambridge | 7.805 | 0.024
Creek Road |  | 10003 | 90.5741 | 95.2556 | 96.7571 | 99.266 | 102.205 | 105.526 | 108.3403 | 111.5909 | 113.0618 | 114.5064 | 115.5793 | 116.4913 | 208.2177 | 209.5603 | 209.518 | 212.1856 | 215.9888 | 220.5107 | 224.4512 | 227.434 | 228.8537 | 230.0649 | 230.8622 | 233.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Claremont | 11.167 | 0
Creek Road |  | 10007 | 109.0672 | 114.7046 | 116.5127 | 119.5338 | 123.0729 | 127.072 | 130.4608 | 134.3752 | 136.1464 | 137.8859 | 139.178 | 140.2762 | 208.0883 | 209.4301 | 209.3877 | 212.0537 | 215.8545 | 220.3737 | 224.3117 | 227.2926 | 228.7115 | 229.9219 | 230.7188 | 232.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Derwent Park | 3.878 | 0.024
Creek Road |  | 10008 | 82.1664 | 86.4133 | 87.7755 | 90.0515 | 92.7176 | 95.7304 | 98.2834 | 101.2323 | 102.5666 | 103.8771 | 104.8505 | 105.6778 | 195.9438 | 197.2073 | 197.1674 | 199.6778 | 203.2568 | 207.5122 | 211.2204 | 214.0273 | 215.3634 | 216.5032 | 217.2535 | 219.3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-East Hobart | 0.491 | 0.027
Creek Road |  | 10022 | 80.9877 | 85.1737 | 86.5163 | 88.7597 | 91.3876 | 94.3571 | 96.8735 | 99.7801 | 101.0953 | 102.387 | 103.3464 | 104.1618 | 186.8807 | 188.0857 | 188.0477 | 190.442 | 193.8554 | 197.914 | 201.4506 | 204.1278 | 205.402 | 206.4891 | 207.2047 | 209.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Geilston Bay | 10.85 | 0
Creek Road |  | 10024 | 82.0903 | 86.3333 | 87.6943 | 89.9681 | 92.6318 | 95.6418 | 98.1924 | 101.1386 | 102.4717 | 103.781 | 104.7534 | 105.58 | 195.1691 | 196.4276 | 196.3879 | 198.8883 | 202.4532 | 206.6918 | 210.3853 | 213.1811 | 214.5119 | 215.6472 | 216.3946 | 218.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-Howrah | 13.516 | 0.024
Creek Road |  | 10026 | 103.3306 | 108.6714 | 110.3845 | 113.2467 | 116.5996 | 120.3884 | 123.599 | 127.3075 | 128.9855 | 130.6335 | 131.8576 | 132.898 | 196.5014 | 197.7685 | 197.7285 | 200.2461 | 203.8352 | 208.1027 | 211.8215 | 214.6364 | 215.9763 | 217.1193 | 217.8718 | 219.9338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Zs-New Town | 8.702 | 0.032
Derby |  | 55001 | 95.7784 | 100.7289 | 102.3167 | 104.9698 | 108.0776 | 111.5895 | 114.5654 | 118.0028 | 119.5582 | 121.0858 | 122.2204 | 123.1848 | 48.2655 | 48.5767 | 48.5669 | 49.1853 | 50.0669 | 51.1151 | 52.0285 | 52.7199 | 53.049 | 53.3298 | 53.5146 | 54.021 | 165.1315 | 170.2661 | 193.3871 | 226.5938 | 266.7801 | 363.6872 | 462.2642 | 553.1267 | 634.5439 | 707.3198 | 779.8892 | 853.2474 | Zs-Rosny Park | 7.466 | 0
Derby |  | 55002 | 36.9578 | 38.868 | 39.4807 | 40.5044 | 41.7036 | 43.0587 | 44.2071 | 45.5335 | 46.1336 | 46.7231 | 47.1609 | 47.533 | 28.3072 | 28.4898 | 28.484 | 28.8467 | 29.3637 | 29.9785 | 30.5142 | 30.9197 | 31.1127 | 31.2774 | 31.3858 | 31.6828 | 53.712 | 56.5905 | 60.5432 | 89.2591 | 138.806 | 270.2839 | 417.7924 | 567.1237 | 712.5697 | 851.6468 | 997.0016 | 1145.8566 | Zs-Sandy Bay | 18.762 | 0.011
Derby |  | 55003 | 28.802 | 30.2906 | 30.7681 | 31.5659 | 32.5005 | 33.5566 | 34.4515 | 35.4852 | 35.9529 | 36.4123 | 36.7535 | 37.0435 | 16.4553 | 16.5614 | 16.5581 | 16.7689 | 17.0694 | 17.4268 | 17.7382 | 17.9739 | 18.0861 | 18.1819 | 18.2449 | 18.4176 | 18.28 | 18.28 | 24.3036 | 36.7481 | 51.0155 | 87.0125 | 125.3427 | 162.2241 | 196.5125 | 228.0302 | 260.0134 | 292.5852 | Zs-Summerleas | 7.197 | 0
Derwent Bridge |  | 49621 | 0.076359 | 0.080306 | 0.081571 | 0.083687 | 0.086164 | 0.088964 | 0.091337 | 0.094077 | 0.095317 | 0.096535 | 0.09744 | 0.098208 | 0.089145 | 0.08972 | 0.089701 | 0.090844 | 0.092472 | 0.094408 | 0.096095 | 0.097372 | 0.09798 | 0.098498 | 0.09884 | 0.099775 | 0 | 0 | 0 | 1.4503 | 3.6786 | 8.8833 | 13.9968 | 18.535 | 22.4307 | 25.7396 | 28.842 | 31.7607 | Zs-Trial Harbour | 0.809 | 0
Devonport |  | 80001 | 55.6534 | 58.5299 | 59.4526 | 60.9941 | 62.8 | 64.8406 | 66.5698 | 68.5672 | 69.471 | 70.3586 | 71.0179 | 71.5782 | 83.1996 | 83.736 | 83.7191 | 84.785 | 86.3047 | 88.1116 | 89.6861 | 90.878 | 91.4453 | 91.9293 | 92.2479 | 93.1209 | 207.9282 | 250.6716 | 274.1389 | 305.529 | 334.6124 | 402.8637 | 469.8306 | 528.7161 | 578.3407 | 619.3116 | 656.2619 | 689.3767 | Zs-West Hobart | 13.843 | 0.024
Devonport |  | 80002 | 126.5233 | 133.0629 | 135.1604 | 138.6651 | 142.7705 | 147.4097 | 151.3409 | 155.8818 | 157.9364 | 159.9544 | 161.4532 | 162.7272 | 124.2372 | 125.0383 | 125.013 | 126.6047 | 128.874 | 131.5721 | 133.9232 | 135.703 | 136.5501 | 137.2728 | 137.7485 | 139.0522 | 35.222 | 35.222 | 35.222 | 37.0574 | 39.754 | 45.7244 | 51.2375 | 55.7995 | 59.4259 | 62.2627 | 64.702 | 66.8014
Devonport |  | 80003 | 149.2169 | 156.9295 | 159.4033 | 163.5365 | 168.3784 | 173.8497 | 178.486 | 183.8413 | 186.2645 | 188.6444 | 190.412 | 191.9145 | 185.0742 | 186.2676 | 186.2299 | 188.601 | 191.9815 | 196.0008 | 199.5033 | 202.1545 | 203.4165 | 204.4931 | 205.2018 | 207.1439 | 395.7012 | 445.9094 | 492.0873 | 536.6681 | 602.4663 | 758.3133 | 913.0945 | 1051.2121 | 1169.6473 | 1269.4765 | 1361.821 | 1445.7538
Devonport |  | 80004 | 42.6497 | 44.8541 | 45.5612 | 46.7426 | 48.1265 | 49.6903 | 51.0155 | 52.5462 | 53.2388 | 53.919 | 54.4242 | 54.8537 | 102.487 | 103.1478 | 103.127 | 104.44 | 106.312 | 108.5377 | 110.4773 | 111.9454 | 112.6442 | 113.2404 | 113.6329 | 114.7083 | 281.108 | 377.564 | 434.0157 | 503.5542 | 568.8113 | 724.1288 | 879.0116 | 1018.0173 | 1138.395 | 1241.4305 | 1338.6989 | 1430.7183
Devonport |  | 80005 | 57.6495 | 60.6293 | 61.585 | 63.1819 | 65.0525 | 67.1663 | 68.9575 | 71.0266 | 71.9627 | 72.8822 | 73.5651 | 74.1456 | 151.6009 | 152.5785 | 152.5476 | 154.4899 | 157.259 | 160.5514 | 163.4204 | 165.5921 | 166.6258 | 167.5077 | 168.0882 | 169.679 | 366.0303 | 442.6047 | 534.7376 | 611.0216 | 697.8631 | 905.6487 | 1114.0948 | 1302.0461 | 1464.9763 | 1603.7947 | 1733.359 | 1853.7373
Devonport |  | 80006 | 105.5634 | 111.0197 | 112.7698 | 115.6938 | 119.1192 | 122.9898 | 126.2698 | 130.0584 | 131.7727 | 133.4564 | 134.7069 | 135.7698 | 105.7283 | 106.4101 | 106.3886 | 107.7431 | 109.6743 | 111.9704 | 113.9713 | 115.4859 | 116.2068 | 116.8219 | 117.2267 | 118.3362 | 455.9051 | 497.3813 | 536.8039 | 602.8291 | 646.4836 | 754.3963 | 868.1273 | 976.2733 | 1075.0388 | 1163.2439 | 1248.9181 | 1326.9691
Devonport |  | 80007 | 73.8071 | 77.622 | 78.8456 | 80.89 | 83.285 | 85.9912 | 88.2845 | 90.9334 | 92.132 | 93.3092 | 94.1835 | 94.9266 | 160.291 | 161.3246 | 161.292 | 163.3456 | 166.2734 | 169.7545 | 172.788 | 175.0842 | 176.1771 | 177.1096 | 177.7234 | 179.4054 | 541.4932 | 646.8871 | 731.6314 | 801.3698 | 885.6233 | 1089.3965 | 1296.8384 | 1487.7705 | 1658.1835 | 1809.4258 | 1958.5638 | 2107.18
Devonport |  | 80008 | 66.0278 | 69.4405 | 70.5352 | 72.3641 | 74.5066 | 76.9276 | 78.9792 | 81.3489 | 82.4211 | 83.4742 | 84.2564 | 84.9212 | 155.3915 | 156.3935 | 156.3619 | 158.3527 | 161.191 | 164.5657 | 167.5064 | 169.7325 | 170.792 | 171.6959 | 172.291 | 173.9216 | 309.8018 | 371.8489 | 428.3748 | 505.8315 | 612.7733 | 871.9628 | 1135.8532 | 1377.8803 | 1591.8717 | 1778.4978 | 1957.613 | 2129.642
Devonport |  | 80009 | 71.292 | 74.9768 | 76.1587 | 78.1335 | 80.4468 | 83.0608 | 85.276 | 87.8346 | 88.9923 | 90.1294 | 90.9739 | 91.6918 | 161.127 | 162.166 | 162.1332 | 164.1976 | 167.1406 | 170.6399 | 173.6891 | 175.9973 | 177.096 | 178.0333 | 178.6503 | 180.3411 | 327.4908 | 371.8049 | 415.7636 | 472.6998 | 558.0039 | 763.7161 | 971.4839 | 1159.7998 | 1323.6024 | 1463.4626 | 1594.3572 | 1716.7956
Devonport |  | 80010 | 68.9707 | 72.5356 | 73.679 | 75.5895 | 77.8275 | 80.3564 | 82.4994 | 84.9747 | 86.0947 | 87.1948 | 88.0118 | 88.7063 | 198.2147 | 199.4928 | 199.4525 | 201.992 | 205.6124 | 209.9172 | 213.6683 | 216.5078 | 217.8593 | 219.0124 | 219.7714 | 221.8514 | 981.8264 | 1233.0835 | 1397.2928 | 1507.5121 | 1613.9174 | 1869.9873 | 2128.8631 | 2364.6604 | 2571.8871 | 2751.9347 | 2924.8782 | 3092.3382
Devonport |  | 80011 | 98.9533 | 104.0678 | 105.7083 | 108.4493 | 111.6602 | 115.2884 | 118.363 | 121.9144 | 123.5213 | 125.0996 | 126.2718 | 127.2681 | 158.456 | 159.4778 | 159.4455 | 161.4756 | 164.3699 | 167.8111 | 170.8099 | 173.0798 | 174.1602 | 175.082 | 175.6888 | 177.3515 | 529.7704 | 632.2386 | 743.3366 | 799.9007 | 870.7665 | 1043.0132 | 1220.9477 | 1387.469 | 1538.3103 | 1673.2718 | 1805.9051 | 1935.6675
Electrona |  | 33271 | 82.6431 | 86.9147 | 88.2848 | 90.574 | 93.2556 | 96.2859 | 98.8537 | 101.8197 | 103.1617 | 104.4799 | 105.4589 | 106.291 | 146.1296 | 147.0719 | 147.0421 | 148.9143 | 151.5834 | 154.757 | 157.5225 | 159.6158 | 160.6122 | 161.4623 | 162.0218 | 163.5552 | 345.5719 | 437.6339 | 502.8521 | 543.0185 | 571.9285 | 640.0803 | 707.4329 | 768.0472 | 820.5023 | 864.9966 | 906.1444 | 942.6347
Electrona |  | 33272 | 94.9982 | 99.9083 | 101.4833 | 104.1147 | 107.1972 | 110.6805 | 113.6322 | 117.0416 | 118.5843 | 120.0995 | 121.2248 | 122.1814 | 208.7206 | 210.0665 | 210.024 | 212.6981 | 216.5105 | 221.0434 | 224.9933 | 227.9833 | 229.4065 | 230.6207 | 231.4199 | 233.6101 | 517.2529 | 553.2057 | 607.5954 | 669.4964 | 736.9579 | 903.842 | 1078.3459 | 1243.1478 | 1392.9817 | 1526.6192 | 1656.748 | 1777.4722
Electrona |  | 33273 | 0.86119 | 0.9057 | 0.91998 | 0.94383 | 0.97177 | 1.0034 | 1.0301 | 1.061 | 1.075 | 1.0887 | 1.0989 | 1.1076 | 1.289 | 1.2973 | 1.297 | 1.3135 | 1.3371 | 1.3651 | 1.3895 | 1.4079 | 1.4167 | 1.4242 | 1.4292 | 1.4427 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Electrona |  | 33274 | 120.5232 | 126.7527 | 128.7508 | 132.0892 | 136 | 140.4192 | 144.164 | 148.4895 | 150.4467 | 152.369 | 153.7967 | 155.0102 | 170.8896 | 171.9915 | 171.9567 | 174.1461 | 177.2675 | 180.9788 | 184.2128 | 186.6609 | 187.8261 | 188.8202 | 189.4745 | 191.2678 | 533.3492 | 609.89 | 749.091 | 809.5414 | 853.225 | 957.2376 | 1060.868 | 1153.4338 | 1232.6764 | 1299.12 | 1359.9535 | 1415.2764
Electrona |  | 33275 | 43.9044 | 46.1737 | 46.9016 | 48.1177 | 49.5423 | 51.1522 | 52.5163 | 54.092 | 54.805 | 55.5052 | 56.0253 | 56.4674 | 76.195 | 76.6864 | 76.6709 | 77.6471 | 79.0388 | 80.6935 | 82.1355 | 83.227 | 83.7466 | 84.1898 | 84.4816 | 85.2811 | 527.6849 | 563.6107 | 611.2893 | 683.5439 | 779.7429 | 1020.5676 | 1274.3335 | 1515.0413 | 1734.5883 | 1931.4174 | 2124.9436 | 2306.8102
Electrona |  | 33276 | 107.2464 | 112.7896 | 114.5676 | 117.5383 | 121.0183 | 124.9506 | 128.2829 | 132.1319 | 133.8735 | 135.584 | 136.8545 | 137.9344 | 212.406 | 213.7757 | 213.7324 | 216.4537 | 220.3334 | 224.9463 | 228.966 | 232.0088 | 233.4571 | 234.6927 | 235.5061 | 237.735 | 735.242 | 771.9507 | 824.9006 | 919.5807 | 1005.7303 | 1217.2121 | 1436.1822 | 1642.456 | 1830.7112 | 2000.1994 | 2167.5063 | 2328.7077
Electrona |  | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay |  | 90019 | 35.1989 | 37.0183 | 37.6018 | 38.5768 | 39.7189 | 41.0096 | 42.1032 | 43.3665 | 43.9381 | 44.4995 | 44.9165 | 45.2709 | 36.0106 | 36.2428 | 36.2355 | 36.6969 | 37.3546 | 38.1367 | 38.8182 | 39.334 | 39.5796 | 39.789 | 39.9269 | 40.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emu Bay |  | 90020 | 34.6767 | 36.4691 | 37.044 | 38.0045 | 39.1297 | 40.4012 | 41.4786 | 42.7232 | 43.2863 | 43.8394 | 44.2501 | 44.5993 | 46.7082 | 47.0094 | 46.9999 | 47.5983 | 48.4514 | 49.4658 | 50.3498 | 51.0189 | 51.3374 | 51.6091 | 51.7879 | 52.2781 | 0 | 0 | 0 | 7.589 | 20.3774 | 52.4734 | 85.5273 | 115.4897 | 141.1293 | 162.3806 | 181.4741 | 198.4286
Emu Bay |  | 90021 | 27.376 | 28.791 | 29.2448 | 30.0031 | 30.8914 | 31.8952 | 32.7458 | 33.7283 | 34.1729 | 34.6095 | 34.9338 | 35.2094 | 40.6287 | 40.8907 | 40.8824 | 41.4029 | 42.145 | 43.0274 | 43.7963 | 44.3783 | 44.6553 | 44.8917 | 45.0472 | 45.4736 | 0 | 0 | 0 | 9.7672 | 25.2575 | 62.653 | 100.5257 | 134.8877 | 164.6231 | 189.6177 | 212.3386 | 232.6535
Emu Bay |  | 90023 | 71.3049 | 74.9904 | 76.1726 | 78.1477 | 80.4614 | 83.0759 | 85.2914 | 87.8505 | 89.0085 | 90.1457 | 90.9904 | 91.7084 | 107.2401 | 107.9316 | 107.9098 | 109.2837 | 111.2425 | 113.5715 | 115.6009 | 117.1372 | 117.8684 | 118.4922 | 118.9029 | 120.0282 | 57.9803 | 73.1866 | 80.7496 | 125.0509 | 175.5161 | 297.8757 | 422.5925 | 537.1233 | 638.4699 | 726.854 | 811.6541 | 893.1108
Emu Bay |  | 90024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53001 | 91.7323 | 96.4737 | 97.9945 | 100.5354 | 103.512 | 106.8755 | 109.7257 | 113.0179 | 114.5076 | 115.9707 | 117.0574 | 117.981 | 151.828 | 152.807 | 152.7761 | 154.7213 | 157.4945 | 160.7918 | 163.6651 | 165.8401 | 166.8753 | 167.7585 | 168.3399 | 169.9331 | 685.8533 | 801.0168 | 889.6631 | 955.2478 | 1005.5041 | 1125.2545 | 1245.1293 | 1353.3073 | 1447.5306 | 1527.5113 | 1603.0203 | 1674.2908
George Town |  | 53002 | 9.5847 | 10.0801 | 10.239 | 10.5045 | 10.8155 | 11.167 | 11.4648 | 11.8088 | 11.9644 | 12.1173 | 12.2308 | 12.3273 | 12.8527 | 12.9356 | 12.9329 | 13.0976 | 13.3324 | 13.6115 | 13.8547 | 14.0389 | 14.1265 | 14.2013 | 14.2505 | 14.3853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53003 | 107.0314 | 112.5635 | 114.3379 | 117.3026 | 120.7756 | 124.7001 | 128.0257 | 131.867 | 133.6051 | 135.3122 | 136.5801 | 137.6578 | 142.7396 | 143.66 | 143.631 | 145.4597 | 148.0669 | 151.1668 | 153.8681 | 155.9129 | 156.8862 | 157.7165 | 158.2631 | 159.761 | 813.2555 | 923.2165 | 1006.0339 | 1116.7109 | 1235.6663 | 1523.4507 | 1816.6048 | 2086.2851 | 2325.8958 | 2535.9426 | 2738.1865 | 2930.2147
George Town |  | 53004 | 36.198 | 38.069 | 38.6691 | 39.6718 | 40.8463 | 42.1736 | 43.2983 | 44.5974 | 45.1853 | 45.7626 | 46.1914 | 46.5559 | 56.1727 | 56.5349 | 56.5235 | 57.2432 | 58.2692 | 59.4891 | 60.5522 | 61.3569 | 61.7399 | 62.0666 | 62.2817 | 62.8712 | 238.3686 | 255.231 | 283.9252 | 309.4693 | 338.4944 | 407.5582 | 476.4565 | 539.1723 | 594.3885 | 642.5034 | 688.7678 | 733.3094
George Town |  | 53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town |  | 53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
George Town |  | 53007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15929 | 0.41415 | 1.0354 | 1.6725 | 2.2619 | 2.7875 | 3.2495 | 3.6955 | 4.1256
George Town |  | 53008 | 46.7633 | 49.1803 | 49.9556 | 51.2509 | 52.7683 | 54.4829 | 55.9359 | 57.6142 | 58.3736 | 59.1195 | 59.6734 | 60.1443 | 69.5657 | 70.0143 | 70.0002 | 70.8914 | 72.1621 | 73.6728 | 74.9894 | 75.9859 | 76.4602 | 76.8649 | 77.1313 | 77.8613 | 312.781 | 358.0599 | 380.3059 | 437.3446 | 505.28 | 669.4479 | 836.3361 | 989.2455 | 1124.3827 | 1242.2721 | 1355.5782 | 1463.3362
George Town |  | 53009 | 29.2071 | 30.7168 | 31.201 | 32.01 | 32.9577 | 34.0286 | 34.9361 | 35.9844 | 36.4587 | 36.9245 | 37.2705 | 37.5646 | 52.6218 | 52.9611 | 52.9504 | 53.6246 | 54.5857 | 55.7286 | 56.7244 | 57.4782 | 57.837 | 58.1431 | 58.3446 | 58.8968 | 911.5911 | 1047.3615 | 1149.7639 | 1252.6087 | 1338.5152 | 1542.4023 | 1746.1847 | 1931.1784 | 2093.2918 | 2233.5088 | 2366.9907 | 2492.3317
George Town |  | 53010 | 43.4249 | 45.6694 | 46.3893 | 47.5922 | 49.0012 | 50.5935 | 51.9427 | 53.5012 | 54.2064 | 54.899 | 55.4134 | 55.8507 | 51.9473 | 52.2823 | 52.2717 | 52.9373 | 53.8861 | 55.0143 | 55.9973 | 56.7415 | 57.0957 | 57.3979 | 57.5968 | 58.1419 | 0 | 0 | 0 | 2.0707 | 5.3839 | 13.4599 | 21.7429 | 29.4046 | 36.2381 | 42.2433 | 48.0414 | 53.6324
Gordon |  | 49801 | 4.8765 | 5.1286 | 5.2094 | 5.3445 | 5.5027 | 5.6815 | 5.833 | 6.0081 | 6.0872 | 6.165 | 6.2228 | 6.2719 | 9.5588 | 9.6204 | 9.6185 | 9.741 | 9.9155 | 10.1231 | 10.304 | 10.441 | 10.5061 | 10.5618 | 10.5984 | 10.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gretna |  | 37002 | 50.0879 | 52.6768 | 53.5072 | 54.8946 | 56.5199 | 58.3564 | 59.9127 | 61.7104 | 62.5237 | 63.3226 | 63.916 | 64.4203 | 17.1698 | 17.2805 | 17.277 | 17.497 | 17.8106 | 18.1835 | 18.5084 | 18.7544 | 18.8715 | 18.9713 | 19.0371 | 19.2173 | 6.24 | 6.24 | 6.24 | 10.5555 | 17.5417 | 34.7973 | 52.7749 | 69.7653 | 85.4336 | 99.9531 | 115.1216 | 131.3733
Hadspen |  | 67081 | 68.7366 | 72.2894 | 73.429 | 75.3329 | 77.5633 | 80.0837 | 82.2194 | 84.6863 | 85.8025 | 86.8988 | 87.7131 | 88.4052 | 125.9139 | 126.7258 | 126.7002 | 128.3134 | 130.6132 | 133.3478 | 135.7306 | 137.5344 | 138.393 | 139.1254 | 139.6076 | 140.9289 | 402.812 | 477.3123 | 570.8251 | 617.1603 | 666.3465 | 785.7307 | 906.6136 | 1016.0712 | 1111.0079 | 1191.9092 | 1267.8342 | 1339.7244
Hadspen |  | 67082 | 185.3443 | 194.9242 | 197.9969 | 203.1309 | 209.145 | 215.941 | 221.6998 | 228.3517 | 231.3616 | 234.3177 | 236.5133 | 238.3795 | 130.5967 | 131.4388 | 131.4123 | 133.0854 | 135.4708 | 138.3071 | 140.7786 | 142.6494 | 143.5399 | 144.2996 | 144.7997 | 146.1701 | 628.1141 | 687.4882 | 749.6442 | 830.3352 | 933.3362 | 1182.3314 | 1435.8509 | 1668.81 | 1875.3965 | 2056.008 | 2229.339 | 2392.4502
Hadspen |  | 67083 | 102.1326 | 107.4116 | 109.1048 | 111.9338 | 115.2478 | 118.9927 | 122.166 | 125.8315 | 127.4901 | 129.1191 | 130.3289 | 131.3573 | 118.7513 | 119.517 | 119.4928 | 121.0142 | 123.1833 | 125.7623 | 128.0096 | 129.7107 | 130.5204 | 131.2112 | 131.666 | 132.9121 | 79.2853 | 83.1514 | 91.7471 | 107.3929 | 133.0579 | 197.7709 | 267.1686 | 335.0506 | 399.7055 | 460.7314 | 523.9715 | 588.9442
Hadspen |  | 67084 | 141.5752 | 148.8927 | 151.2398 | 155.1614 | 159.7553 | 164.9464 | 169.3452 | 174.4263 | 176.7254 | 178.9834 | 180.6606 | 182.0861 | 141.8243 | 142.7388 | 142.71 | 144.527 | 147.1175 | 150.1975 | 152.8815 | 154.9132 | 155.8802 | 156.7052 | 157.2483 | 158.7366 | 76.2533 | 76.4234 | 83.1836 | 97.2982 | 120.0422 | 176.4572 | 236.298 | 294.8228 | 351.4549 | 406.7897 | 467.1871 | 531.663
Hadspen |  | 67085 | 61.0409 | 64.1959 | 65.2079 | 66.8987 | 68.8794 | 71.1175 | 73.0141 | 75.2049 | 76.1961 | 77.1697 | 77.8928 | 78.5074 | 111.7148 | 112.4351 | 112.4124 | 113.8437 | 115.8842 | 118.3103 | 120.4245 | 122.0248 | 122.7866 | 123.4364 | 123.8642 | 125.0365 | 528.9254 | 616.5762 | 670.0171 | 706.2884 | 740.2393 | 819.1745 | 896.0166 | 963.1159 | 1019.294 | 1065.3816 | 1106.6876 | 1143.4824
Hadspen |  | 67086 | 81.4059 | 85.6135 | 86.9631 | 89.218 | 91.8595 | 94.8444 | 97.3738 | 100.2954 | 101.6174 | 102.9157 | 103.8801 | 104.6998 | 176.3224 | 177.4594 | 177.4235 | 179.6825 | 182.9031 | 186.7324 | 190.0692 | 192.5951 | 193.7974 | 194.823 | 195.4982 | 197.3485 | 1122.6154 | 1310.593 | 1508.478 | 1613.7955 | 1723.7863 | 1990.5811 | 2261.5445 | 2508.3398 | 2723.7711 | 2907.8997 | 3079.6149 | 3238.4808
Hadspen |  | 67087 | 83.5547 | 87.8733 | 89.2586 | 91.573 | 94.2842 | 97.3479 | 99.944 | 102.9427 | 104.2996 | 105.6322 | 106.622 | 107.4633 | 151.1564 | 152.1311 | 152.1003 | 154.0369 | 156.7979 | 160.0806 | 162.9412 | 165.1065 | 166.1372 | 167.0165 | 167.5953 | 169.1815 | 864.4763 | 970.3083 | 1179.8776 | 1260.3277 | 1352.188 | 1570.787 | 1788.7459 | 1983.7921 | 2151.1499 | 2291.7411 | 2420.5427 | 2535.9197
Hadspen |  | 67088 | 44.8626 | 47.1814 | 47.9252 | 49.1678 | 50.6236 | 52.2685 | 53.6624 | 55.2726 | 56.0011 | 56.7166 | 57.2481 | 57.6998 | 90.0355 | 90.6161 | 90.5978 | 91.7513 | 93.3958 | 95.3512 | 97.055 | 98.3448 | 98.9587 | 99.4825 | 99.8273 | 100.7721 | 614.2081 | 700.1056 | 784.943 | 851.427 | 912.0891 | 1058.4545 | 1206.74 | 1342.0849 | 1461.3232 | 1565.2194 | 1665.2253 | 1761.9086
Hadspen |  | 67089 | 53.0605 | 55.803 | 56.6827 | 58.1524 | 59.8741 | 61.8197 | 63.4683 | 65.3727 | 66.2343 | 67.0806 | 67.7092 | 68.2434 | 105.3305 | 106.0097 | 105.9883 | 107.3377 | 109.2616 | 111.5492 | 113.5425 | 115.0514 | 115.7696 | 116.3823 | 116.7856 | 117.8909 | 591.2843 | 680.4192 | 782.2485 | 848.2993 | 913.5348 | 1071.1329 | 1230.9216 | 1376.6043 | 1504.3045 | 1614.3339 | 1718.2684 | 1816.1956
Hadspen |  | 67090 | 178.7527 | 187.9919 | 190.9554 | 195.9067 | 201.707 | 208.2612 | 213.8152 | 220.2306 | 223.1334 | 225.9844 | 228.102 | 229.9018 | 251.4886 | 253.1103 | 253.0591 | 256.2811 | 260.8746 | 266.3364 | 271.0957 | 274.6983 | 276.4131 | 277.8761 | 278.8391 | 281.4781 | 989.2083 | 1128.6993 | 1266.6831 | 1370.1299 | 1483.9945 | 1754.3568 | 2024.8542 | 2268.8569 | 2481.5801 | 2665.353 | 2841.3107 | 3011.4902
Hadspen |  | 67091 | 52.2038 | 54.902 | 55.7675 | 57.2135 | 58.9074 | 60.8215 | 62.4436 | 64.3171 | 65.1649 | 65.9975 | 66.6159 | 67.1416 | 132.0003 | 132.8514 | 132.8246 | 134.5157 | 136.9268 | 139.7935 | 142.2915 | 144.1825 | 145.0825 | 145.8504 | 146.3559 | 147.741 | 323.7766 | 379.3443 | 418.9872 | 489.6783 | 569.5833 | 769.5122 | 980.1811 | 1180.547 | 1364.5084 | 1531.1683 | 1697.1574 | 1862.222
Huon River |  | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Huon River |  | 38423 | 39.6526 | 41.7021 | 42.3595 | 43.4579 | 44.7445 | 46.1984 | 47.4305 | 48.8536 | 49.4975 | 50.13 | 50.5997 | 50.999 | 43.017 | 43.2944 | 43.2856 | 43.8367 | 44.6225 | 45.5567 | 46.3708 | 46.987 | 47.2803 | 47.5305 | 47.6953 | 48.1467 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
Kermandie |  | 31002 | 101.7455 | 107.0045 | 108.6912 | 111.5095 | 114.811 | 118.5417 | 121.703 | 125.3546 | 127.0069 | 128.6297 | 129.835 | 130.8594 | 117.5917 | 118.35 | 118.3261 | 119.8326 | 121.9805 | 124.5343 | 126.7597 | 128.4442 | 129.246 | 129.93 | 130.3803 | 131.6143 | 77.4966 | 85.7988 | 93.3555 | 107.2899 | 129.6152 | 184.0717 | 239.885 | 291.4008 | 337.2308 | 377.4804 | 416.5226 | 454.7138
Kermandie |  | 31007 | 69.8143 | 73.4228 | 74.5802 | 76.514 | 78.7794 | 81.3393 | 83.5085 | 86.0141 | 87.1478 | 88.2613 | 89.0883 | 89.7913 | 134.7005 | 135.5691 | 135.5417 | 137.2675 | 139.7278 | 142.6532 | 145.2023 | 147.132 | 148.0504 | 148.834 | 149.3498 | 150.7633 | 231.2838 | 251.9903 | 263.6379 | 302.9809 | 362.7188 | 511.7613 | 669.8754 | 822.623 | 965.9773 | 1099.0913 | 1234.8881 | 1361.8237
Kermandie |  | 31008 | 108.0382 | 113.6223 | 115.4134 | 118.4061 | 121.9117 | 125.8731 | 129.23 | 133.1074 | 134.8619 | 136.585 | 137.8648 | 138.9527 | 129.7426 | 130.5792 | 130.5528 | 132.215 | 134.5848 | 137.4025 | 139.8578 | 141.7164 | 142.6011 | 143.3558 | 143.8526 | 145.2141 | 251.3387 | 273.438 | 296.6033 | 343.9314 | 401.9323 | 546.8027 | 700.4237 | 848.6671 | 987.7197 | 1117.0292 | 1249.5994 | 1381.8831
Kermandie |  | 31010 | 86.9712 | 91.4665 | 92.9083 | 95.3174 | 98.1394 | 101.3284 | 104.0307 | 107.152 | 108.5644 | 109.9515 | 110.9818 | 111.8575 | 80.392 | 80.9104 | 80.894 | 81.924 | 83.3924 | 85.1383 | 86.6597 | 87.8113 | 88.3595 | 88.8271 | 89.135 | 89.9786 | 99.6484 | 105.7714 | 113.1114 | 129.329 | 155.4166 | 219.6473 | 286.5096 | 349.5868 | 407.235 | 459.3325 | 511.0767 | 560.5976
Kingston 11kV |  | 34251 | 56.3899 | 59.3045 | 60.2394 | 61.8013 | 63.6311 | 65.6987 | 67.4508 | 69.4746 | 70.3903 | 71.2897 | 71.9577 | 72.5255 | 128.6859 | 129.5157 | 129.4895 | 131.1382 | 133.4887 | 136.2834 | 138.7188 | 140.5622 | 141.4397 | 142.1883 | 142.681 | 144.0314 | 659.3548 | 727.3215 | 828.2056 | 910.2527 | 946.0472 | 1032.42 | 1120.4104 | 1201.6321 | 1274.3069 | 1338.6653 | 1401.3816 | 1462.3012
Kingston 11kV |  | 34252 | 111.6585 | 117.4298 | 119.2809 | 122.3738 | 125.997 | 130.0911 | 133.5604 | 137.5678 | 139.3811 | 141.162 | 142.4847 | 143.609 | 251.836 | 253.4599 | 253.4086 | 256.6351 | 261.2349 | 266.7042 | 271.4701 | 275.0777 | 276.7949 | 278.2598 | 279.2242 | 281.8668 | 1196.662 | 1328.1139 | 1472.5164 | 1618.1629 | 1714.4475 | 1944.5369 | 2174.4061 | 2380.1107 | 2556.3866 | 2704.2257 | 2839.5104 | 2962.3832
Kingston 11kV |  | 34253 | 50.2974 | 52.8971 | 53.731 | 55.1242 | 56.7562 | 58.6005 | 60.1633 | 61.9684 | 62.7852 | 63.5874 | 64.1833 | 64.6897 | 122.9428 | 123.7356 | 123.7106 | 125.2857 | 127.5313 | 130.2013 | 132.5279 | 134.2891 | 135.1274 | 135.8426 | 136.3134 | 137.6035 | 463.9158 | 528.8996 | 628.9652 | 681.2175 | 719.6539 | 811.7986 | 904.1341 | 986.9946 | 1058.182 | 1118.022 | 1172.8902 | 1222.8106
Kingston 11kV |  | 34254 | 7.9371 | 8.3474 | 8.479 | 8.6988 | 8.9564 | 9.2474 | 9.494 | 9.7789 | 9.9078 | 10.0344 | 10.1284 | 10.2083 | 11.1804 | 11.2525 | 11.2502 | 11.3935 | 11.5977 | 11.8405 | 12.0521 | 12.2122 | 12.2885 | 12.3535 | 12.3963 | 12.5137 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
Kingston 11kV |  | 34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34256 | 62.7765 | 66.0212 | 67.0619 | 68.8008 | 70.8378 | 73.1396 | 75.0901 | 77.3432 | 78.3626 | 79.3639 | 80.1075 | 80.7396 | 144.7955 | 145.7291 | 145.6997 | 147.5548 | 150.1995 | 153.3441 | 156.0843 | 158.1585 | 159.1458 | 159.9881 | 160.5426 | 162.062 | 480.5132 | 557.988 | 672.5486 | 723.1808 | 771.0623 | 885.7898 | 1000.7145 | 1103.8129 | 1192.3484 | 1266.7229 | 1334.8548 | 1396.768
Kingston 11kV |  | 34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.4115 | 232.1186 | 257.7582 | 253.5571 | 253.3961 | 253.7698 | 254.9041 | 258.2804 | 268.9445 | 277.653 | 283.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4376 | 75.7319 | 76.339 | 75.0948 | 75.0471 | 75.1578 | 75.4937 | 76.4937 | 79.652 | 82.2312 | 83.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston 11kV |  | 34259 | 100.5116 | 105.7067 | 107.373 | 110.1571 | 113.4186 | 117.104 | 120.227 | 123.8343 | 125.4665 | 127.0696 | 128.2603 | 129.2723 | 236.3474 | 237.8714 | 237.8234 | 240.8514 | 245.1683 | 250.3012 | 254.774 | 258.1598 | 259.7713 | 261.1462 | 262.0512 | 264.5313 | 996.9094 | 1138.8981 | 1296.2601 | 1407.4419 | 1478.7793 | 1650.2556 | 1822.5613 | 1977.5972 | 2111.1113 | 2223.571 | 2326.8522 | 2420.9306
Kingston 11kV |  | 34260 | 47.1188 | 49.5542 | 50.3354 | 51.6405 | 53.1695 | 54.8972 | 56.3612 | 58.0523 | 58.8174 | 59.5689 | 60.1271 | 60.6016 | 76.3584 | 76.8507 | 76.8352 | 77.8135 | 79.2082 | 80.8665 | 82.3116 | 83.4054 | 83.9261 | 84.3702 | 84.6626 | 85.4639 | 99.7487 | 127.5088 | 148.1355 | 169.5062 | 192.4337 | 247.0714 | 301.4996 | 350.0771 | 391.6164 | 426.4066 | 458.2269 | 487.1403
Kingston 11kV |  | 34261 | 66.5899 | 70.0317 | 71.1357 | 72.9802 | 75.1409 | 77.5825 | 79.6515 | 82.0414 | 83.1228 | 84.1849 | 84.9737 | 85.6442 | 111.771 | 112.4917 | 112.4689 | 113.9009 | 115.9424 | 118.3698 | 120.4851 | 122.0862 | 122.8483 | 123.4985 | 123.9265 | 125.0994 | 0 | 0 | 0 | 20.7423 | 54.1093 | 135.3173 | 217.7596 | 292.4987 | 357.1674 | 411.7646 | 461.9375 | 507.6229
Kingston 11kV |  | 34262 | 67.3074 | 70.7863 | 71.9022 | 73.7666 | 75.9506 | 78.4185 | 80.5098 | 82.9254 | 84.0185 | 85.092 | 85.8893 | 86.567 | 133.2638 | 134.1231 | 134.096 | 135.8034 | 138.2375 | 141.1316 | 143.6536 | 145.5626 | 146.4713 | 147.2465 | 147.7568 | 149.1552 | 36.9928 | 38.3424 | 38.3424 | 46.7312 | 60.4001 | 94.5122 | 130.6207 | 165.4502 | 198.2105 | 228.8623 | 260.5087 | 293.0764
Kingston 11kV |  | 34263 | 60.4724 | 63.598 | 64.6006 | 66.2756 | 68.2379 | 70.4552 | 72.3341 | 74.5045 | 75.4865 | 76.451 | 77.1674 | 77.7762 | 127.7162 | 128.5398 | 128.5138 | 130.15 | 132.4828 | 135.2565 | 137.6735 | 139.5031 | 140.3739 | 141.1168 | 141.6059 | 142.9461 | 363.9402 | 409.3921 | 466.1888 | 526.0266 | 571.3465 | 682.2842 | 797.6352 | 907.6155 | 1011.2576 | 1110.5879 | 1218.7753 | 1340.049
Kingston 11kV |  | 34264 | 101.7666 | 107.0267 | 108.7138 | 111.5327 | 114.8348 | 118.5663 | 121.7283 | 125.3806 | 127.0332 | 128.6564 | 129.8619 | 130.8866 | 168.2642 | 169.3492 | 169.315 | 171.4708 | 174.5442 | 178.1984 | 181.3828 | 183.7932 | 184.9405 | 185.9193 | 186.5637 | 188.3294 | 232.9853 | 248.6839 | 261.0295 | 291.9213 | 334.0519 | 436.7308 | 542.4518 | 640.7562 | 728.9937 | 807.1235 | 883.216 | 955.447
Kingston 33kV |  | 36240 | 99.6662 | 104.8176 | 106.4699 | 109.2306 | 112.4646 | 116.1191 | 119.2158 | 122.7928 | 124.4113 | 126.0009 | 127.1815 | 128.1851 | 113.904 | 114.6385 | 114.6153 | 116.0746 | 118.1551 | 120.6289 | 122.7844 | 124.4162 | 125.1928 | 125.8554 | 126.2916 | 127.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Knights Road |  | 30603 | 167.9767 | 176.6589 | 179.4437 | 184.0966 | 189.5471 | 195.7063 | 200.9255 | 206.9541 | 209.6819 | 212.3611 | 214.3509 | 216.0423 | 232.6274 | 234.1274 | 234.0801 | 237.0605 | 241.3095 | 246.3616 | 250.764 | 254.0964 | 255.6826 | 257.0358 | 257.9266 | 260.3677 | 278.4738 | 323.9695 | 336.7861 | 394.0063 | 454.7155 | 602.997 | 756.0797 | 899.3455 | 1029.3511 | 1146.2562 | 1262.3289 | 1373.6653
Knights Road |  | 30604 | 102.1115 | 107.3893 | 109.0822 | 111.9106 | 115.224 | 118.968 | 122.1407 | 125.8055 | 127.4637 | 129.0923 | 130.3019 | 131.3301 | 43.3572 | 43.6367 | 43.6279 | 44.1834 | 44.9753 | 45.9169 | 46.7374 | 47.3586 | 47.6542 | 47.9064 | 48.0724 | 48.5274 | 289.8047 | 322.4866 | 352.5112 | 392.0443 | 446.7498 | 578.7189 | 713.3273 | 837.8457 | 949.5204 | 1048.6674 | 1145.6964 | 1238.87
Knights Road |  | 30605 | 202.6175 | 213.0901 | 216.4492 | 222.0617 | 228.6362 | 236.0656 | 242.3611 | 249.6329 | 252.9233 | 256.1549 | 258.5552 | 260.5953 | 217.7263 | 219.1303 | 219.086 | 221.8754 | 225.8523 | 230.5807 | 234.7011 | 237.8201 | 239.3047 | 240.5712 | 241.405 | 243.6897 | 131.0558 | 152.6553 | 165.5713 | 192.8054 | 221.873 | 292.4711 | 364.9318 | 432.4052 | 493.4428 | 548.3085 | 602.9004 | 656.0658
Knights Road |  | 30606 | 144.5045 | 151.9735 | 154.3692 | 158.3719 | 163.0608 | 168.3593 | 172.8492 | 178.0355 | 180.3821 | 182.6869 | 184.3987 | 185.8537 | 305.2075 | 307.1756 | 307.1135 | 311.0237 | 316.5984 | 323.2268 | 329.0027 | 333.3749 | 335.456 | 337.2314 | 338.4001 | 341.6029 | 253.4635 | 303.9118 | 326.4497 | 375.8313 | 436.1876 | 584.3656 | 737.8171 | 881.4389 | 1011.2952 | 1127.2187 | 1241.182 | 1353.4402
Knights Road |  | 30607 | 70.6275 | 74.278 | 75.4489 | 77.4053 | 79.697 | 82.2867 | 84.4812 | 87.016 | 88.1629 | 89.2894 | 90.126 | 90.8372 | 140.6305 | 141.5373 | 141.5087 | 143.3104 | 145.879 | 148.9332 | 151.5946 | 153.6091 | 154.5681 | 155.3861 | 155.9246 | 157.4003 | 480.6929 | 522.8974 | 544.3956 | 626.6691 | 705.7093 | 898.6077 | 1097.7609 | 1284.3331 | 1453.5682 | 1606.0951 | 1758.1423 | 1903.3355
Knights Road |  | 30608 | 146.0839 | 153.6345 | 156.0564 | 160.1028 | 164.843 | 170.1994 | 174.7384 | 179.9813 | 182.3536 | 184.6835 | 186.414 | 187.885 | 163.0993 | 164.151 | 164.1178 | 166.2074 | 169.1865 | 172.7286 | 175.8152 | 178.1517 | 179.2638 | 180.2125 | 180.8371 | 182.5486 | 158.2967 | 170.9375 | 173.8589 | 196.6386 | 228.2622 | 305.8604 | 385.9058 | 460.1667 | 526.2814 | 583.9014 | 638.6402 | 688.3216
Lindisfarne |  | 25305 | 42.5566 | 44.7562 | 45.4618 | 46.6406 | 48.0214 | 49.5819 | 50.9041 | 52.4315 | 53.1226 | 53.8013 | 54.3054 | 54.7339 | 77.5443 | 78.0444 | 78.0286 | 79.0221 | 80.4384 | 82.1225 | 83.59 | 84.7008 | 85.2296 | 85.6807 | 85.9776 | 86.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25307 | 72.5746 | 76.3258 | 77.529 | 79.5393 | 81.8942 | 84.5553 | 86.8102 | 89.4149 | 90.5935 | 91.751 | 92.6107 | 93.3415 | 158.3575 | 159.3786 | 159.3464 | 161.3752 | 164.2677 | 167.7068 | 170.7037 | 172.9722 | 174.052 | 174.9731 | 175.5795 | 177.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25308 | 70.6752 | 74.3282 | 75.4999 | 77.4576 | 79.7508 | 82.3423 | 84.5382 | 87.0747 | 88.2224 | 89.3497 | 90.1869 | 90.8985 | 154.5619 | 155.5586 | 155.5271 | 157.5073 | 160.3305 | 163.6872 | 166.6122 | 168.8263 | 169.8802 | 170.7793 | 171.3712 | 172.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25309 | 92.8263 | 97.6242 | 99.1631 | 101.7344 | 104.7465 | 108.1501 | 111.0343 | 114.3658 | 115.8732 | 117.3538 | 118.4534 | 119.388 | 151.1792 | 152.154 | 152.1232 | 154.0601 | 156.8214 | 160.1047 | 162.9657 | 165.1314 | 166.1622 | 167.0416 | 167.6205 | 169.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lindisfarne |  | 25310 | 45.058 | 47.3869 | 48.1339 | 49.382 | 50.844 | 52.4961 | 53.8961 | 55.5133 | 56.245 | 56.9636 | 57.4974 | 57.9511 | 82.6796 | 83.2127 | 83.1959 | 84.2552 | 85.7654 | 87.561 | 89.1256 | 90.3101 | 90.8738 | 91.3548 | 91.6714 | 92.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank |  | 45001 | 60.6982 | 63.8355 | 64.8418 | 66.5231 | 68.4927 | 70.7183 | 72.6042 | 74.7827 | 75.7684 | 76.7365 | 77.4555 | 78.0667 | 39.6618 | 39.9175 | 39.9094 | 40.4176 | 41.142 | 42.0034 | 42.7539 | 43.3221 | 43.5925 | 43.8233 | 43.9751 | 44.3913 | 20.808 | 29.7404 | 33.3308 | 38.4259 | 46.436 | 65.6251 | 84.9793 | 102.5974 | 118.0745 | 131.4831 | 144.2581 | 156.4261
Meadowbank |  | 45002 | 65.0442 | 68.4062 | 69.4845 | 71.2862 | 73.3968 | 75.7817 | 77.8027 | 80.1371 | 81.1934 | 82.2308 | 83.0013 | 83.6563 | 67.9413 | 68.3794 | 68.3656 | 69.236 | 70.477 | 71.9525 | 73.2383 | 74.2115 | 74.6748 | 75.07 | 75.3302 | 76.0431 | 22.2352 | 22.2352 | 24.89 | 48.5258 | 86.954 | 182.3044 | 282.0276 | 376.2696 | 462.3181 | 539.846 | 616.5665 | 692.1847
Meadowbank |  | 45003 | 94.3546 | 99.2315 | 314.9937 | 323.1613 | 332.7292 | 343.5409 | 352.7026 | 363.2852 | 368.0736 | 372.7765 | 376.2695 | 379.2385 | 31.9232 | 32.129 | 262.7076 | 266.0524 | 270.8211 | 276.491 | 281.4318 | 285.1718 | 286.952 | 288.4707 | 289.4705 | 292.2101 | 51.7037 | 59.0408 | 62.4138 | 87.0436 | 126.9212 | 225.7764 | 329.2751 | 427.1423 | 516.2736 | 596.0071 | 674.0296 | 749.9312
Mornington |  | 24401 | 74.1864 | 78.0209 | 79.2508 | 81.3057 | 83.7129 | 86.4331 | 88.7382 | 91.4007 | 92.6054 | 93.7886 | 94.6675 | 95.4144 | 146.2113 | 147.1541 | 147.1244 | 148.9976 | 151.6682 | 154.8435 | 157.6105 | 159.7051 | 160.702 | 161.5525 | 162.1124 | 163.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24402 | 65.4047 | 68.7852 | 69.8696 | 71.6812 | 73.8035 | 76.2017 | 78.2339 | 80.5812 | 81.6433 | 82.6865 | 83.4613 | 84.1198 | 125.8022 | 126.6134 | 126.5878 | 128.1996 | 130.4974 | 133.2295 | 135.6102 | 137.4124 | 138.2702 | 139.002 | 139.4837 | 140.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24405 | 126.5404 | 133.0809 | 135.1787 | 138.6838 | 142.7899 | 147.4297 | 151.3614 | 155.9029 | 157.9578 | 159.9761 | 161.4751 | 162.7492 | 267.7691 | 269.4958 | 269.4413 | 272.8719 | 277.7628 | 283.578 | 288.6455 | 292.4813 | 294.3072 | 295.8648 | 296.8901 | 299.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington |  | 24406 | 74.175 | 78.0089 | 79.2386 | 81.2932 | 83.7001 | 86.4198 | 88.7245 | 91.3866 | 92.5912 | 93.7742 | 94.6529 | 95.3998 | 144.3336 | 145.2643 | 145.2349 | 147.0841 | 149.7204 | 152.8549 | 155.5864 | 157.654 | 158.6382 | 159.4778 | 160.0305 | 161.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mowbray |  | 62004 | 71.7159 | 75.4227 | 76.6116 | 78.5981 | 80.9252 | 83.5548 | 85.783 | 88.3569 | 89.5215 | 90.6653 | 91.5149 | 92.237 | 186.5274 | 187.7302 | 187.6922 | 190.082 | 193.489 | 197.5399 | 201.0698 | 203.7419 | 205.0137 | 206.0988 | 206.813 | 208.7704 | 734.179 | 808.4375 | 909.3219 | 994.801 | 1060.2982 | 1219.9796 | 1384.196 | 1537.0594 | 1674.9083 | 1798.0868 | 1919.7983 | 2040.9692
Mowbray |  | 62005 | 65.1572 | 68.525 | 69.6052 | 71.41 | 73.5242 | 75.9133 | 77.9378 | 80.2763 | 81.3344 | 82.3736 | 83.1455 | 83.8015 | 139.2146 | 140.1123 | 140.0839 | 141.8675 | 144.4103 | 147.4337 | 150.0683 | 152.0626 | 153.0119 | 153.8217 | 154.3548 | 155.8156 | 269.4376 | 307.3521 | 344.078 | 390.4606 | 452.3569 | 606.0983 | 767.1113 | 919.5103 | 1058.7875 | 1184.1455 | 1307.6404 | 1428.31
Mowbray |  | 62006 | 45.6024 | 47.9595 | 48.7155 | 49.9787 | 51.4584 | 53.1305 | 54.5474 | 56.1841 | 56.9246 | 57.6519 | 58.1922 | 58.6513 | 112.976 | 113.7045 | 113.6816 | 115.129 | 117.1925 | 119.6461 | 121.7841 | 123.4025 | 124.1729 | 124.8301 | 125.2627 | 126.4482 | 258.5037 | 323.4958 | 382.4777 | 440.3965 | 497.5944 | 635.2106 | 773.6506 | 898.3902 | 1005.9974 | 1096.821 | 1180.4343 | 1256.8114
Mowbray |  | 62008 | 40.0046 | 42.0724 | 42.7356 | 43.8437 | 45.1418 | 46.6086 | 47.8516 | 49.2873 | 49.937 | 50.575 | 51.0489 | 51.4517 | 241.9296 | 243.4897 | 243.4404 | 246.54 | 250.9589 | 256.213 | 260.7914 | 264.2572 | 265.9068 | 267.3141 | 268.2405 | 270.7792 | 305.6246 | 363.1643 | 398.3322 | 467.8619 | 537.6611 | 708.0841 | 883.8113 | 1047.8175 | 1195.7766 | 1327.3542 | 1455.5754 | 1579.7494
Mowbray |  | 62009 | 74.0513 | 77.8788 | 79.1065 | 81.1577 | 83.5605 | 86.2757 | 88.5766 | 91.2342 | 92.4368 | 93.6179 | 94.4951 | 95.2407 | 126.6865 | 127.5034 | 127.4776 | 129.1007 | 131.4147 | 134.166 | 136.5635 | 138.3783 | 139.2421 | 139.9791 | 140.4642 | 141.7936 | 189.076 | 205.7728 | 236.9439 | 266.0744 | 314.5967 | 438.1392 | 570.5842 | 698.2786 | 816.2224 | 922.5281 | 1026.5147 | 1126.7621
Mowbray |  | 62010 | 57.9101 | 60.9033 | 61.8634 | 63.4675 | 65.3465 | 67.4699 | 69.2692 | 71.3476 | 72.288 | 73.2117 | 73.8977 | 74.4808 | 117.6461 | 118.4048 | 118.3808 | 119.8881 | 122.0369 | 124.5919 | 126.8183 | 128.5036 | 129.3058 | 129.9902 | 130.4407 | 131.6752 | 309.8897 | 356.3833 | 394.1357 | 451.9023 | 530.1729 | 723.5148 | 925.2901 | 1116.403 | 1292.3772 | 1453.416 | 1616.3458 | 1781.3564
Mowbray |  | 62013 | 133.037 | 139.9132 | 142.1188 | 145.8038 | 150.1207 | 154.9987 | 159.1323 | 163.9069 | 166.0673 | 168.1892 | 169.7652 | 171.1047 | 174.727 | 175.8537 | 175.8182 | 178.0567 | 181.2482 | 185.0428 | 188.3495 | 190.8525 | 192.0439 | 193.0603 | 193.7293 | 195.5629 | 118.0174 | 172.4863 | 179.2939 | 230.2669 | 279.2814 | 397.2249 | 516.9895 | 627.2881 | 726.1156 | 814.5239 | 903.004 | 993.5884
NA |  | 14072 | 10.0189 | 10.5367 | 10.7028 | 10.9804 | 11.3055 | 11.6728 | 11.9841 | 12.3437 | 12.5064 | 12.6662 | 12.7849 | 12.8857 | 16.7426 | 16.8506 | 16.8472 | 17.0617 | 17.3675 | 17.7311 | 18.048 | 18.2878 | 18.402 | 18.4994 | 18.5635 | 18.7392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 37001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 39564 | 8.9828 | 9.4471 | 9.596 | 9.8448 | 10.1363 | 10.4657 | 10.7448 | 11.0672 | 11.213 | 11.3563 | 11.4627 | 11.5532 | 10.266 | 10.3322 | 10.3301 | 10.4617 | 10.6492 | 10.8721 | 11.0664 | 11.2135 | 11.2835 | 11.3432 | 11.3825 | 11.4902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 39566 | 83.6111 | 87.9327 | 89.3189 | 91.6349 | 94.3479 | 97.4136 | 100.0115 | 103.0123 | 104.3701 | 105.7036 | 106.6941 | 107.536 | 82.5162 | 83.0483 | 83.0315 | 84.0887 | 85.5958 | 87.3879 | 88.9495 | 90.1315 | 90.6942 | 91.1742 | 91.4902 | 92.3561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 49302 | 0.013308 | 0.013996 | 0.014216 | 0.014585 | 0.015017 | 0.015505 | 0.015918 | 0.016396 | 0.016612 | 0.016824 | 0.016982 | 0.017116 | 0.015209 | 0.015307 | 0.015304 | 0.015499 | 0.015777 | 0.016107 | 0.016395 | 0.016613 | 0.016716 | 0.016805 | 0.016863 | 0.017023 | 0 | 0 | 0 | 0.053096 | 0.13805 | 0.34512 | 0.55751 | 0.75397 | 0.92918 | 1.0832 | 1.2318 | 1.3752
NA |  | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 84121 | 104.4823 | 109.8826 | 111.6148 | 114.5089 | 117.8992 | 121.7302 | 124.9766 | 128.7264 | 130.4231 | 132.0895 | 133.3272 | 134.3793 | 49.1438 | 49.4607 | 49.4507 | 50.0804 | 50.978 | 52.0453 | 52.9753 | 53.6793 | 54.0144 | 54.3003 | 54.4884 | 55.0041 | 225.8866 | 247.1632 | 265.0574 | 311.604 | 378.093 | 539.6466 | 704.8 | 856.9938 | 992.1262 | 1110.2098 | 1223.3548 | 1328.8402
NA |  | 84122 | 175.4869 | 184.5573 | 187.4666 | 192.3275 | 198.0218 | 204.4563 | 209.9089 | 216.207 | 219.0568 | 221.8557 | 223.9345 | 225.7015 | 9.755 | 9.8179 | 9.816 | 9.9409 | 10.1191 | 10.331 | 10.5156 | 10.6553 | 10.7218 | 10.7786 | 10.8159 | 10.9183 | 3 | 3 | 3 | 7.4495 | 14.5687 | 31.9218 | 49.7198 | 66.1829 | 80.8663 | 93.7699 | 106.2285 | 118.2421
NA |  | 18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NA |  | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Norfolk |  | 39010 | 35.5269 | 37.3632 | 37.9522 | 38.9362 | 40.089 | 41.3917 | 42.4955 | 43.7706 | 44.3475 | 44.9141 | 45.335 | 45.6927 | 69.9765 | 70.4277 | 70.4135 | 71.31 | 72.5881 | 74.1079 | 75.4321 | 76.4346 | 76.9117 | 77.3188 | 77.5867 | 78.321 | 257.9005 | 285.6999 | 324.4826 | 382.0516 | 432.6129 | 555.2891 | 680.2368 | 794.7892 | 895.9754 | 984.113 | 1068.6181 | 1149.7549
New Norfolk |  | 39011 | 32.6559 | 34.3438 | 34.8852 | 35.7897 | 36.8494 | 38.0467 | 39.0614 | 40.2334 | 40.7637 | 41.2845 | 41.6714 | 42.0002 | 60.3952 | 60.7847 | 60.7724 | 61.5461 | 62.6493 | 63.9609 | 65.1039 | 65.9691 | 66.3809 | 66.7322 | 66.9635 | 67.5972 | 157.1768 | 188.0828 | 212.5719 | 239.0743 | 282.5468 | 391.6442 | 507.1764 | 617.577 | 719.0307 | 810.302 | 899.5713 | 980.6756
New Norfolk |  | 39012 | 35.7458 | 37.5934 | 38.186 | 39.1761 | 40.336 | 41.6467 | 42.7574 | 44.0403 | 44.6207 | 45.1909 | 45.6143 | 45.9742 | 65.6845 | 66.1081 | 66.0947 | 66.9362 | 68.136 | 69.5625 | 70.8055 | 71.7465 | 72.1944 | 72.5765 | 72.828 | 73.5172 | 65.7996 | 65.7996 | 78.476 | 102.1319 | 137.357 | 226.3421 | 319.7983 | 407.2988 | 485.5103 | 553.8239 | 618.8712 | 680.257
New Norfolk |  | 39013 | 39.9056 | 41.9682 | 42.6297 | 43.7351 | 45.03 | 46.4932 | 47.7331 | 49.1653 | 49.8133 | 50.4498 | 50.9225 | 51.3243 | 77.2042 | 77.702 | 77.6863 | 78.6754 | 80.0856 | 81.7622 | 83.2233 | 84.3293 | 84.8557 | 85.3048 | 85.6004 | 86.4106 | 208.0972 | 216.548 | 249.4023 | 272.2186 | 302.6605 | 376.4097 | 451.3269 | 519.6594 | 579.484 | 630.8888 | 679.2698 | 724.6649
NewNorfolk |  | 39565 | 71.4514 | 75.1445 | 76.3291 | 78.3082 | 80.6267 | 83.2466 | 85.4667 | 88.031 | 89.1913 | 90.3309 | 91.1774 | 91.8968 | 135.0801 | 135.9511 | 135.9237 | 137.6543 | 140.1216 | 143.0552 | 145.6115 | 147.5466 | 148.4676 | 149.2534 | 149.7707 | 151.1881 | 424.245 | 465.5004 | 518.5152 | 587.6257 | 676.0281 | 890.5101 | 1109.7957 | 1312.464 | 1493.733 | 1653.774 | 1810.5639 | 1965.0714
NewNorfolk |  | 39568 | 55.6149 | 58.4895 | 59.4115 | 60.952 | 62.7566 | 64.7958 | 66.5239 | 68.5199 | 69.423 | 70.31 | 70.9688 | 71.5288 | 85.6693 | 86.2217 | 86.2043 | 87.3019 | 88.8666 | 90.7272 | 92.3484 | 93.5757 | 94.1598 | 94.6582 | 94.9862 | 95.8852 | 217.625 | 228.2665 | 233.1543 | 259.1053 | 300.1891 | 399.8488 | 502.4355 | 598.7132 | 686.9108 | 767.4586 | 848.9774 | 929.7207
NewNorfolk |  | 39569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24245 | 0.63038 | 1.576 | 2.5458 | 3.4428 | 4.2429 | 4.9461 | 5.6249 | 6.2796
NewNorfolk |  | 39570 | 30.821 | 32.4141 | 32.925 | 33.7788 | 34.7789 | 35.909 | 36.8666 | 37.9728 | 38.4733 | 38.9649 | 39.33 | 39.6403 | 22.1578 | 22.3007 | 22.2962 | 22.5801 | 22.9848 | 23.466 | 23.8853 | 24.2027 | 24.3538 | 24.4827 | 24.5676 | 24.8001 | 26.65 | 26.65 | 26.65 | 31.3575 | 39.2787 | 59.5204 | 81.1026 | 101.6028 | 120.1189 | 136.3776 | 151.8827 | 166.523
NewNorfolk |  | 39571 | 73.1481 | 76.9289 | 78.1416 | 80.1678 | 82.5413 | 85.2234 | 87.4962 | 90.1214 | 91.3093 | 92.476 | 93.3425 | 94.079 | 55.4073 | 55.7646 | 55.7534 | 56.4632 | 57.4753 | 58.6786 | 59.7271 | 60.5209 | 60.8987 | 61.221 | 61.4331 | 62.0146 | 84.5894 | 98.6034 | 102.267 | 124.7381 | 161.5396 | 253.8589 | 351.5997 | 444.895 | 530.4525 | 606.9688 | 681.9715 | 753.8633
Newton | Risdon | 96202 | 85.7145 | 90.1449 | 91.5659 | 93.9401 | 96.7214 | 99.8643 | 102.5275 | 105.6038 | 106.9957 | 108.3628 | 109.3782 | 110.2413 | 105.147 | 105.825 | 105.8036 | 107.1507 | 109.0712 | 111.3548 | 113.3446 | 114.8509 | 115.5678 | 116.1795 | 116.5821 | 117.6855 | 49 | 49 | 49 | 64.6898 | 89.5848 | 149.3947 | 209.4217 | 263.3193 | 309.5852 | 348.3779 | 383.8038 | 415.8468
North Hobart |  | 18131A | 115.2398 | 121.1961 | 123.1066 | 126.2987 | 130.0381 | 134.2635 | 137.8441 | 141.9801 | 143.8515 | 145.6895 | 147.0546 | 148.2149 | 16.3296 | 16.4349 | 16.4316 | 16.6408 | 16.9391 | 17.2937 | 17.6027 | 17.8367 | 17.948 | 18.043 | 18.1055 | 18.2769 | 5 | 5 | 5 | 16.8605 | 37.2348 | 91.2917 | 152.2312 | 214.4423 | 275.5923 | 334.5174 | 396.533 | 461.4642
North Hobart |  | 18131B | 136.5923 | 143.6523 | 145.9168 | 149.7004 | 154.1326 | 159.1409 | 163.385 | 168.2872 | 170.5054 | 172.684 | 174.3021 | 175.6774 | 170.9133 | 172.0154 | 171.9806 | 174.1703 | 177.2921 | 181.0039 | 184.2384 | 186.6868 | 187.8522 | 188.8464 | 189.5009 | 191.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18132A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.0495 | 181.2105 | 181.1739 | 183.4806 | 186.7693 | 190.6795 | 194.0869 | 196.6662 | 197.8939 | 198.9412 | 199.6307 | 201.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18132B | 38.3985 | 40.3832 | 41.0198 | 42.0835 | 43.3294 | 44.7374 | 45.9305 | 47.3086 | 47.9321 | 48.5446 | 48.9994 | 49.3861 | 36.3824 | 36.617 | 36.6096 | 37.0758 | 37.7403 | 38.5304 | 39.219 | 39.7401 | 39.9882 | 40.1999 | 40.3392 | 40.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18133A | 36.9659 | 38.8765 | 39.4893 | 40.5133 | 41.7128 | 43.0682 | 44.2167 | 45.5434 | 46.1437 | 46.7333 | 47.1712 | 47.5434 | 35.2062 | 35.4333 | 35.4261 | 35.8771 | 36.5202 | 37.2848 | 37.9511 | 38.4554 | 38.6955 | 38.9003 | 39.0351 | 39.4045 | 0 | 0 | 0 | 4.4357 | 12.4847 | 35.5685 | 64.2993 | 97.1525 | 133.4961 | 172.6877 | 218.1346 | 269.3588
North Hobart |  | 18133B | 20.299 | 21.3482 | 21.6847 | 22.247 | 22.9056 | 23.6499 | 24.2807 | 25.0092 | 25.3388 | 25.6626 | 25.903 | 26.1074 | 38.315 | 38.5621 | 38.5543 | 39.0452 | 39.745 | 40.5771 | 41.3022 | 41.8511 | 42.1123 | 42.3352 | 42.4819 | 42.884 | 68.1579 | 77.2137 | 83.1924 | 103.7175 | 129.7592 | 190.5796 | 249.8839 | 301.675 | 345.0318 | 380.6232 | 412.5832 | 441.1464
North Hobart |  | 18134A | 30.0382 | 31.5907 | 32.0887 | 32.9208 | 33.8955 | 34.9969 | 35.9302 | 37.0082 | 37.496 | 37.9751 | 38.331 | 38.6334 | 62.8694 | 63.2748 | 63.262 | 64.0675 | 65.2158 | 66.5812 | 67.771 | 68.6716 | 69.1003 | 69.466 | 69.7067 | 70.3665 | 59.1449 | 70.0487 | 77.1234 | 83.6367 | 94.0155 | 119.0654 | 144.3364 | 167.1608 | 186.8875 | 203.56 | 218.9211 | 232.9561
North Hobart |  | 18134B | 14.5779 | 15.3314 | 15.5731 | 15.9769 | 16.4499 | 16.9845 | 17.4374 | 17.9606 | 18.1974 | 18.4299 | 18.6026 | 18.7493 | 43.2383 | 43.5171 | 43.5083 | 44.0622 | 44.852 | 45.791 | 46.6093 | 47.2287 | 47.5235 | 47.775 | 47.9406 | 48.3943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.7584 | 178.0744 | 219.7683 | 245.9584 | 273.0125 | 338.2516 | 404.01 | 463.3533 | 514.6027 | 557.8854 | 597.7356 | 634.1216
North Hobart |  | 18135B | 58.2306 | 61.2404 | 62.2058 | 63.8187 | 65.7082 | 67.8433 | 69.6526 | 71.7425 | 72.6881 | 73.6169 | 74.3067 | 74.893 | 102.0212 | 102.6791 | 102.6583 | 103.9654 | 105.8288 | 108.0445 | 109.9752 | 111.4367 | 112.1323 | 112.7258 | 113.1165 | 114.187 | 125.3247 | 135.931 | 138.8985 | 175.648 | 199.4522 | 257.3318 | 316.1651 | 369.6932 | 416.2717 | 455.8769 | 492.5578 | 526.2205
North Hobart |  | 18136A | 34.014 | 35.7721 | 36.336 | 37.2782 | 38.3819 | 39.6291 | 40.6859 | 41.9067 | 42.459 | 43.0015 | 43.4045 | 43.747 | 102.181 | 102.8399 | 102.8191 | 104.1282 | 105.9945 | 108.2137 | 110.1474 | 111.6112 | 112.3079 | 112.9023 | 113.2936 | 114.3658 | 40.1356 | 61.4556 | 99.4423 | 143.7229 | 173.3235 | 249.1716 | 332.8212 | 418.0617 | 503.7282 | 590.1218 | 687.0333 | 796.3812
North Hobart |  | 18141B | 111.1759 | 116.9222 | 118.7653 | 121.8449 | 125.4523 | 129.5288 | 132.9831 | 136.9732 | 138.7786 | 140.5518 | 141.8688 | 142.9882 | 179.7419 | 180.9009 | 180.8643 | 183.1671 | 186.4502 | 190.3537 | 193.7553 | 196.3301 | 197.5557 | 198.6013 | 199.2896 | 201.1757 | 25.3393 | 30.1538 | 38.2953 | 43.0323 | 50.5805 | 68.7986 | 87.1775 | 103.7771 | 118.1238 | 130.2492 | 141.4209 | 151.6282
North Hobart |  | 18142A | 8.175 | 8.5975 | 8.733 | 8.9595 | 9.2248 | 9.5245 | 9.7785 | 10.0719 | 10.2047 | 10.335 | 10.4319 | 10.5142 | 21.5986 | 21.7379 | 21.7335 | 22.0102 | 22.4047 | 22.8738 | 23.2825 | 23.5919 | 23.7392 | 23.8648 | 23.9475 | 24.1742 | 0 | 0 | 0 | 0.47823 | 1.5916 | 5.5191 | 11.2695 | 18.7017 | 27.7075 | 38.1062 | 50.8105 | 65.709
North Hobart |  | 18142B | 22.0395 | 23.1786 | 23.544 | 24.1545 | 24.8696 | 25.6777 | 26.3625 | 27.1535 | 27.5114 | 27.8629 | 28.124 | 28.3459 | 35.5204 | 35.7494 | 35.7422 | 36.1973 | 36.8461 | 37.6175 | 38.2897 | 38.7985 | 39.0407 | 39.2474 | 39.3834 | 39.7561 | 109.7499 | 116.7538 | 147.4535 | 166.3447 | 180.8394 | 217.3349 | 256.4373 | 294.9014 | 332.3575 | 369.5442 | 411.6152 | 460.6644
North Hobart |  | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.5204 | 728.0648 | 833.2577 | 903.9928 | 976.2374 | 1150.934 | 1327.9328 | 1488.9958 | 1629.7716 | 1750.5734 | 1863.9998 | 1969.9244
North Hobart |  | 18143B | 85.3335 | 89.7441 | 91.1588 | 93.5225 | 96.2914 | 99.4203 | 102.0717 | 105.1343 | 106.5201 | 107.8811 | 108.892 | 109.7512 | 227.1272 | 228.5918 | 228.5455 | 231.4554 | 235.604 | 240.5366 | 244.8349 | 248.0886 | 249.6373 | 250.9585 | 251.8282 | 254.2116 | 97.0245 | 128.5019 | 173.5014 | 189.0204 | 207.3083 | 250.7803 | 293.9891 | 332.4776 | 365.3329 | 392.8073 | 417.9004 | 440.6696
North Hobart |  | 18144A | 40.5557 | 42.6519 | 43.3242 | 44.4476 | 45.7636 | 47.2506 | 48.5107 | 49.9662 | 50.6248 | 51.2717 | 51.7521 | 52.1604 | 104.3569 | 105.0298 | 105.0086 | 106.3455 | 108.2517 | 110.518 | 112.493 | 113.9879 | 114.6995 | 115.3065 | 115.7061 | 116.8012 | 483.9383 | 589.4019 | 639.3161 | 718.2215 | 765.7772 | 879.9135 | 994.4295 | 1097.3173 | 1185.7975 | 1260.2235 | 1328.4854 | 1390.5856
North Hobart |  | 18144B | 53.5145 | 56.2805 | 57.1677 | 58.6501 | 60.3865 | 62.3487 | 64.0115 | 65.9321 | 66.8011 | 67.6546 | 68.2886 | 68.8274 | 147.5615 | 148.513 | 148.483 | 150.3735 | 153.0688 | 156.2734 | 159.066 | 161.1798 | 162.186 | 163.0444 | 163.6094 | 165.1579 | 32.5018 | 41.9273 | 45.7008 | 54.5654 | 63.5939 | 85.3891 | 107.3835 | 127.2579 | 144.4458 | 158.9843 | 172.3928 | 184.6589
North Hobart |  | 18145A | 31.5009 | 33.1291 | 33.6513 | 34.5239 | 35.546 | 36.7011 | 37.6798 | 38.8104 | 39.3219 | 39.8244 | 40.1975 | 40.5147 | 55.5256 | 55.8837 | 55.8724 | 56.5837 | 57.5979 | 58.8038 | 59.8546 | 60.65 | 61.0287 | 61.3517 | 61.5643 | 62.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart |  | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.3914 | 349.0811 | 379.1786 | 418.1648 | 450.7281 | 528.9664 | 607.5611 | 678.2723 | 739.1757 | 790.4942 | 837.6546 | 880.6523
North Hobart |  | 18146A | 70.4956 | 74.1393 | 75.308 | 77.2607 | 79.5482 | 82.133 | 84.3234 | 86.8534 | 87.9982 | 89.1226 | 89.9577 | 90.6675 | 187.0952 | 188.3016 | 188.2636 | 190.6606 | 194.0779 | 198.1412 | 201.6819 | 204.3621 | 205.6378 | 206.7262 | 207.4426 | 209.4059 | 1045.6764 | 1266.54 | 1481.5708 | 1630.9011 | 1736.7186 | 1990.3186 | 2244.3636 | 2472.267 | 2667.9998 | 2832.477 | 2983.2367 | 3120.3535
North Hobart |  | 18146B | 93.4583 | 98.2889 | 99.8383 | 102.4271 | 105.4596 | 108.8864 | 111.7903 | 115.1444 | 116.6621 | 118.1527 | 119.2599 | 120.2009 | 268.7607 | 270.4937 | 270.439 | 273.8823 | 278.7913 | 284.6281 | 289.7143 | 293.5644 | 295.397 | 296.9604 | 297.9895 | 300.8098 | 36.2208 | 39.1008 | 43.4593 | 53.3228 | 67.9925 | 100.7871 | 131.2712 | 156.5854 | 176.7201 | 192.4407 | 205.9066 | 217.4334
Norwood |  | 65060 | 27.0639 | 28.4628 | 28.9114 | 29.6611 | 30.5393 | 31.5316 | 32.3725 | 33.3438 | 33.7833 | 34.215 | 34.5356 | 34.8081 | 42.2075 | 42.4797 | 42.4711 | 43.0119 | 43.7828 | 44.6994 | 45.4982 | 46.1028 | 46.3906 | 46.6362 | 46.7978 | 47.2407 | 329.3452 | 392.3245 | 446.5208 | 495.6722 | 558.6456 | 708.4635 | 857.4956 | 990.3214 | 1103.7197 | 1198.5026 | 1284.9745 | 1363.3036
Norwood |  | 65061 | 64.1256 | 67.4401 | 68.5032 | 70.2794 | 72.3602 | 74.7115 | 76.7039 | 79.0054 | 80.0467 | 81.0695 | 81.8291 | 82.4748 | 126.5403 | 127.3563 | 127.3305 | 128.9517 | 131.263 | 134.0112 | 136.4059 | 138.2186 | 139.0814 | 139.8175 | 140.3021 | 141.63 | 479.8046 | 566.7689 | 675.6808 | 755.6804 | 838.0014 | 1038.526 | 1243.8501 | 1433.0197 | 1600.4705 | 1745.914 | 1884.1597 | 2015.1952
Norwood |  | 65062 | 74.8979 | 78.7691 | 80.0108 | 82.0855 | 84.5158 | 87.262 | 89.5892 | 92.2772 | 93.4935 | 94.6881 | 95.5753 | 96.3295 | 154.9499 | 155.9491 | 155.9175 | 157.9027 | 160.7329 | 164.098 | 167.0304 | 169.2501 | 170.3067 | 171.208 | 171.8014 | 173.4273 | 315.6522 | 410.6178 | 508.197 | 527.7843 | 551.5758 | 608.3206 | 664.9239 | 715.5123 | 758.8138 | 795.0901 | 828.249 | 858.332
Norwood |  | 65063 | 24.581 | 25.8515 | 26.259 | 26.9399 | 27.7375 | 28.6388 | 29.4026 | 30.2848 | 30.6839 | 31.076 | 31.3672 | 31.6147 | 56.0412 | 56.4026 | 56.3912 | 57.1092 | 58.1328 | 59.3499 | 60.4104 | 61.2132 | 61.5954 | 61.9213 | 62.1359 | 62.724 | 645.0531 | 726.3325 | 806.6939 | 865.2751 | 920.463 | 1053.2957 | 1186.8755 | 1307.0372 | 1410.3561 | 1497.1257 | 1576.4785 | 1648.3813
Norwood |  | 65064 | 42.2914 | 44.4773 | 45.1785 | 46.3499 | 47.7222 | 49.2729 | 50.5869 | 52.1047 | 52.7915 | 53.466 | 53.967 | 54.3929 | 98.7814 | 99.4184 | 99.3983 | 100.6638 | 102.4681 | 104.6134 | 106.4828 | 107.8979 | 108.5714 | 109.1461 | 109.5243 | 110.5609 | 833.9814 | 940.1543 | 1031.3221 | 1121.616 | 1176.8886 | 1310.4639 | 1446.2381 | 1570.8581 | 1681.4757 | 1778.6033 | 1872.5622 | 1963.3856
Norwood |  | 65065 | 65.6334 | 69.0258 | 70.1139 | 71.9319 | 74.0616 | 76.4681 | 78.5074 | 80.863 | 81.9288 | 82.9756 | 83.7531 | 84.414 | 152.1583 | 153.1394 | 153.1085 | 155.0579 | 157.8371 | 161.1416 | 164.0211 | 166.2008 | 167.2383 | 168.1235 | 168.7061 | 170.3028 | 496.6688 | 520.4243 | 621.8424 | 679.4093 | 759.5477 | 954.7079 | 1154.0051 | 1336.9728 | 1498.6604 | 1639.5565 | 1774.9398 | 1905.7079
Norwood |  | 65066 | 95.097 | 100.0123 | 101.5889 | 104.223 | 107.3088 | 110.7957 | 113.7504 | 117.1634 | 118.7077 | 120.2245 | 121.351 | 122.3085 | 112.1587 | 112.8819 | 112.8591 | 114.296 | 116.3446 | 118.7804 | 120.903 | 122.5097 | 123.2745 | 123.9269 | 124.3564 | 125.5333 | 252.144 | 319.6896 | 350.2393 | 389.0191 | 423.5158 | 507.0566 | 592.3658 | 671.1165 | 741.37 | 803.224 | 863.0625 | 920.7774
Norwood |  | 65067 | 43.9403 | 46.2115 | 46.9399 | 48.1571 | 49.5828 | 51.194 | 52.5593 | 54.1363 | 54.8498 | 55.5506 | 56.0712 | 56.5136 | 68.2223 | 68.6622 | 68.6483 | 69.5223 | 70.7684 | 72.2501 | 73.5411 | 74.5184 | 74.9836 | 75.3805 | 75.6417 | 76.3576 | 0 | 0 | 0 | 0.37167 | 0.96635 | 2.4159 | 3.9026 | 5.2778 | 6.5043 | 7.5821 | 8.6228 | 9.6263
Palmerston |  | 51001 | 11.2892 | 11.8727 | 12.0599 | 12.3726 | 12.7389 | 13.1528 | 13.5036 | 13.9088 | 14.0921 | 14.2721 | 14.4059 | 14.5195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0385 | 79.7824 | 96.6004 | 119.8266 | 157.0271 | 247.9895 | 341.6681 | 428.5923 | 506.1159 | 573.8984 | 638.6115 | 699.4132
Palmerston |  | 51002 | 11.2892 | 11.8727 | 12.0599 | 12.3726 | 12.7389 | 13.1528 | 13.5036 | 13.9088 | 14.0921 | 14.2721 | 14.4059 | 14.5195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9057 | 25.7547 | 64.3869 | 104.0095 | 140.6605 | 173.3492 | 202.0757 | 229.8116 | 256.5569
Palmerston |  | 51003 | 245.962 | 258.675 | 262.7527 | 269.5658 | 277.5468 | 286.5654 | 294.2077 | 303.0352 | 307.0294 | 310.9524 | 313.866 | 316.3426 | 122.9684 | 123.7613 | 123.7363 | 125.3117 | 127.5578 | 130.2284 | 132.5555 | 134.3171 | 135.1555 | 135.8709 | 136.3417 | 137.6321 | 119.7902 | 128.6051 | 151.0979 | 186.4083 | 225.4577 | 318.9328 | 412.8587 | 497.7842 | 571.6753 | 634.9149 | 694.2918 | 749.9194
Palmerston |  | 51004 | 153.5842 | 161.5225 | 164.0687 | 168.3229 | 173.3064 | 178.9378 | 183.7099 | 189.2219 | 191.716 | 194.1656 | 195.985 | 197.5314 | 94.817 | 95.4284 | 95.4091 | 96.6239 | 98.3557 | 100.4149 | 102.2093 | 103.5676 | 104.2141 | 104.7657 | 105.1288 | 106.1237 | 127.2226 | 150.6878 | 158.5526 | 201.9511 | 255.3275 | 387.4765 | 525.5205 | 655.7829 | 774.2564 | 880.0679 | 983.1703 | 1078.8317
Port Latta |  | 94001 | 88.2024 | 92.7613 | 94.2236 | 96.6668 | 99.5288 | 102.7629 | 105.5034 | 108.669 | 110.1013 | 111.5081 | 112.5529 | 113.441 | 60.3174 | 60.7064 | 60.6941 | 61.4669 | 62.5686 | 63.8785 | 65.02 | 65.8841 | 66.2954 | 66.6462 | 66.8772 | 67.5101 | 522.5316 | 600.3608 | 669.2858 | 774.651 | 889.1623 | 1173.5869 | 1472.6235 | 1757.9277 | 2021.9022 | 2263.5658 | 2506.8971 | 2745.6119
Port Latta |  | 94002 | 159.1807 | 167.4083 | 170.0472 | 174.4565 | 179.6216 | 185.4582 | 190.4041 | 196.1171 | 198.702 | 201.2409 | 203.1266 | 204.7293 | 185.8407 | 187.0391 | 187.0012 | 189.3822 | 192.7766 | 196.8126 | 200.3296 | 202.9918 | 204.259 | 205.3401 | 206.0517 | 208.0018 | 55.435 | 58.8753 | 64.0365 | 84.8639 | 120.2027 | 212.1738 | 313.4961 | 414.714 | 512.6936 | 606.5239 | 705.4308 | 809.4795
Queenstown |  | 98001 | 37.2375 | 39.1622 | 39.7795 | 40.811 | 42.0193 | 43.3846 | 44.5416 | 45.8781 | 46.4828 | 47.0767 | 47.5178 | 47.8928 | 50.1956 | 50.5193 | 50.509 | 51.1521 | 52.069 | 53.1591 | 54.109 | 54.8281 | 55.1704 | 55.4624 | 55.6546 | 56.1813 | 142.3231 | 188.0936 | 194.6669 | 230.9889 | 270.182 | 368.32 | 472.8397 | 574.4418 | 670.765 | 761.4905 | 855.6191 | 952.8426
Queenstown |  | 98002 | 35.3108 | 37.136 | 37.7214 | 38.6994 | 39.8452 | 41.14 | 42.2371 | 43.5044 | 44.0778 | 44.641 | 45.0593 | 45.4148 | 67.6353 | 68.0714 | 68.0577 | 68.9242 | 70.1596 | 71.6284 | 72.9084 | 73.8773 | 74.3385 | 74.7319 | 74.9909 | 75.7007 | 78.338 | 104.2099 | 110.3468 | 128.3114 | 157.8792 | 232.0226 | 309.9784 | 383.3586 | 449.2519 | 506.7884 | 561.1639 | 611.7232
Queenstown |  | 98003 | 22.1026 | 23.245 | 23.6115 | 24.2237 | 24.9409 | 25.7513 | 26.4381 | 27.2313 | 27.5903 | 27.9428 | 28.2046 | 28.4272 | 41.2281 | 41.494 | 41.4856 | 42.0138 | 42.7668 | 43.6622 | 44.4424 | 45.033 | 45.3142 | 45.554 | 45.7119 | 46.1445 | 435.729 | 515.3914 | 557.7259 | 632.0165 | 726.7054 | 951.6898 | 1176.267 | 1378.3461 | 1553.8698 | 1704.5352 | 1847.287 | 1982.8347
Railton |  | 85001 | 121.0101 | 127.2648 | 129.2709 | 132.6229 | 136.5494 | 140.9865 | 144.7464 | 149.0894 | 151.0545 | 152.9845 | 154.418 | 155.6365 | 183.5816 | 184.7654 | 184.728 | 187.08 | 190.4332 | 194.4201 | 197.8943 | 200.5242 | 201.776 | 202.8439 | 203.5469 | 205.4733 | 418.8944 | 439.9477 | 478.6088 | 548.2907 | 644.0061 | 875.3207 | 1110.673 | 1326.7915 | 1518.4431 | 1686.4317 | 1849.0815 | 2007.6576
Railton |  | 85002 | 168.0463 | 176.7321 | 179.5181 | 184.1729 | 189.6257 | 195.7874 | 201.0088 | 207.0399 | 209.7688 | 212.4491 | 214.4398 | 216.1318 | 166.6459 | 167.7205 | 167.6866 | 169.8216 | 172.8654 | 176.4846 | 179.6383 | 182.0255 | 183.1618 | 184.1312 | 184.7694 | 186.5181 | 281.283 | 313.8152 | 323.9541 | 352.5729 | 388.8305 | 477.8995 | 570.1841 | 656.4607 | 734.1475 | 802.9234 | 869.6547 | 932.0846
Railton |  | 85003 | 32.793 | 34.4879 | 35.0316 | 35.9399 | 37.004 | 38.2064 | 39.2253 | 40.4023 | 40.9348 | 41.4578 | 41.8463 | 42.1765 | 95.9252 | 96.5437 | 96.5242 | 97.7532 | 99.5053 | 101.5886 | 103.4039 | 104.7781 | 105.4321 | 105.9901 | 106.3575 | 107.3641 | 71.564 | 96.495 | 103.9962 | 131.7203 | 160.3846 | 229.6004 | 299.933 | 364.3983 | 421.3842 | 471.0331 | 518.5739 | 564.0566
Railton |  | 85004 | 31.2263 | 32.8403 | 33.358 | 34.2229 | 35.2361 | 36.3811 | 37.3513 | 38.472 | 38.9791 | 39.4772 | 39.8471 | 40.1615 | 61.7053 | 62.1032 | 62.0906 | 62.8811 | 64.0082 | 65.3483 | 66.5161 | 67.4 | 67.8207 | 68.1797 | 68.416 | 69.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton |  | 85005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277.6444 | 279.4347 | 279.3782 | 282.9353 | 288.0066 | 294.0363 | 299.2906 | 303.268 | 305.1611 | 306.7762 | 307.8394 | 310.7529 | 516.3141 | 564.6811 | 629.0731 | 733.7288 | 858.0279 | 1158.732 | 1464.3248 | 1744.0849 | 1991.0468 | 2205.8309 | 2412.3575 | 2612.2369
Railton |  | 85006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.5578 | 193.7995 | 193.7603 | 196.2273 | 199.7444 | 203.9263 | 207.5704 | 210.3289 | 211.6418 | 212.762 | 213.4993 | 215.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Railton |  | 85007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345.3587 | 347.5857 | 347.5154 | 351.94 | 358.2481 | 365.7485 | 372.2842 | 377.2316 | 379.5865 | 381.5955 | 382.9179 | 386.542 | 588.57 | 691.5437 | 798.197 | 875.343 | 970.4183 | 1200.2205 | 1434.0959 | 1649.2649 | 1840.944 | 2010.1216 | 2175.0134 | 2336.0997
Railton |  | 85008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186.5192 | 187.722 | 187.684 | 190.0736 | 193.4805 | 197.5312 | 201.061 | 203.733 | 205.0048 | 206.0898 | 206.804 | 208.7612 | 83.9879 | 90.4084 | 99.4262 | 112.8903 | 129.405 | 170.6359 | 213.6473 | 253.6888 | 289.1728 | 319.7337 | 348.2575 | 374.5198
Richmond |  | 40001 | 19.7122 | 20.7311 | 21.0579 | 21.6039 | 22.2435 | 22.9663 | 23.5788 | 24.2863 | 24.6064 | 24.9208 | 25.1543 | 25.3528 | 36.9975 | 37.2361 | 37.2286 | 37.7026 | 38.3784 | 39.1819 | 39.882 | 40.412 | 40.6643 | 40.8795 | 41.0212 | 41.4094 | 181.0362 | 200.9374 | 211.2904 | 249.1241 | 302.9018 | 434.0703 | 568.4961 | 692.4853 | 802.5404 | 898.6967 | 991.0403 | 1079.8185
Richmond |  | 40002 | 87.0228 | 91.5207 | 92.9634 | 95.3739 | 98.1977 | 101.3885 | 104.0924 | 107.2156 | 108.6288 | 110.0167 | 111.0476 | 111.9238 | 117.3335 | 118.0901 | 118.0663 | 119.5695 | 121.7127 | 124.2608 | 126.4813 | 128.1622 | 128.9622 | 129.6448 | 130.0941 | 131.3253 | 66.5525 | 68.1372 | 75.6271 | 84.2184 | 97.7419 | 129.0955 | 161.2084 | 190.784 | 216.9705 | 239.7592 | 261.5083 | 282.2174
Richmond |  | 40003 | 32.6408 | 34.3279 | 34.869 | 35.7732 | 36.8323 | 38.0291 | 39.0433 | 40.2148 | 40.7448 | 41.2654 | 41.6521 | 41.9808 | 43.4286 | 43.7086 | 43.6998 | 44.2562 | 45.0494 | 45.9926 | 46.8144 | 47.4366 | 47.7327 | 47.9853 | 48.1516 | 48.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11004 | 111.4324 | 117.192 | 119.0394 | 122.126 | 125.7418 | 129.8276 | 133.29 | 137.2892 | 139.0988 | 140.8761 | 142.1961 | 143.3181 | 168.7489 | 169.8371 | 169.8027 | 171.9647 | 175.0469 | 178.7118 | 181.9053 | 184.3226 | 185.4733 | 186.4549 | 187.1011 | 188.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11005 | 115.3496 | 121.3117 | 123.224 | 126.4192 | 130.162 | 134.3915 | 137.9756 | 142.1154 | 143.9886 | 145.8284 | 147.1948 | 148.3563 | 162.6469 | 163.6957 | 163.6626 | 165.7464 | 168.7172 | 172.2495 | 175.3275 | 177.6575 | 178.7665 | 179.7127 | 180.3355 | 182.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11006 | 116.8274 | 122.8658 | 124.8026 | 128.0387 | 131.8296 | 136.1132 | 139.7432 | 143.9361 | 145.8332 | 147.6966 | 149.0805 | 150.2568 | 163.9427 | 164.9998 | 164.9665 | 167.0669 | 170.0613 | 173.6218 | 176.7243 | 179.0728 | 180.1907 | 181.1444 | 181.7721 | 183.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11021 | 89.3615 | 93.9804 | 95.4618 | 97.9371 | 100.8367 | 104.1133 | 106.8899 | 110.097 | 111.5482 | 112.9735 | 114.032 | 114.9318 | 157.8115 | 158.8291 | 158.797 | 160.8188 | 163.7013 | 167.1286 | 170.1151 | 172.3758 | 173.4519 | 174.3699 | 174.9742 | 176.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11023 | 92.9283 | 97.7315 | 99.2721 | 101.8462 | 104.8615 | 108.2689 | 111.1563 | 114.4915 | 116.0005 | 117.4827 | 118.5835 | 119.5192 | 191.995 | 193.233 | 193.1939 | 195.6537 | 199.1606 | 203.3302 | 206.9637 | 209.7141 | 211.0232 | 212.1401 | 212.8752 | 214.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11025 | 90.546 | 95.226 | 96.7272 | 99.2353 | 102.1733 | 105.4933 | 108.3067 | 111.5563 | 113.0267 | 114.4709 | 115.5435 | 116.4552 | 164.2687 | 165.3279 | 165.2945 | 167.3991 | 170.3995 | 173.967 | 177.0757 | 179.4289 | 180.549 | 181.5046 | 182.1336 | 183.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Risdon |  | 11027 | 88.6419 | 93.2235 | 94.6931 | 97.1484 | 100.0247 | 103.2749 | 106.0291 | 109.2104 | 110.6499 | 112.0637 | 113.1137 | 114.0063 | 173.1471 | 174.2636 | 174.2283 | 176.4467 | 179.6092 | 183.3696 | 186.6463 | 189.1267 | 190.3073 | 191.3145 | 191.9776 | 193.7945 | 374.0307 | 464.6561 | 515.2042 | 565.1905 | 628.0559 | 782.1903 | 940.4773 | 1086.2038 | 1214.6382 | 1325.2599 | 1428.9723 | 1525.1956
Rokeby |  | 28221 | 78.3861 | 82.4376 | 83.7372 | 85.9084 | 88.4519 | 91.3261 | 93.7616 | 96.5749 | 97.8478 | 99.098 | 100.0266 | 100.8158 | 165.0863 | 166.1508 | 166.1172 | 168.2323 | 171.2476 | 174.8329 | 177.9571 | 180.322 | 181.4477 | 182.408 | 183.0401 | 184.7725 | 602.939 | 700.8652 | 823.9176 | 898.8732 | 948.6621 | 1066.8254 | 1184.6514 | 1290.4287 | 1381.7828 | 1459.2947 | 1531.2909 | 1597.2692
Rokeby |  | 28222 | 75.2835 | 79.1746 | 80.4227 | 82.508 | 84.9509 | 87.7113 | 90.0504 | 92.7523 | 93.9748 | 95.1756 | 96.0674 | 96.8254 | 162.2077 | 163.2536 | 163.2206 | 165.2988 | 168.2616 | 171.7843 | 174.854 | 177.1777 | 178.2837 | 179.2273 | 179.8484 | 181.5506 | 921.8682 | 1103.4154 | 1306.3764 | 1378.8661 | 1451.2009 | 1625.0548 | 1799.9892 | 1957.797 | 2094.1536 | 2209.4062 | 2315.5649 | 2410.1594
Rokeby |  | 28223 | 109.2528 | 114.8997 | 116.711 | 119.7372 | 123.2823 | 127.2882 | 130.6828 | 134.6039 | 136.3781 | 138.1206 | 139.4148 | 140.5149 | 241.9073 | 243.4671 | 243.4179 | 246.5172 | 250.9357 | 256.1893 | 260.7673 | 264.2327 | 265.8822 | 267.2894 | 268.2157 | 270.7542 | 376.6409 | 474.0857 | 616.1816 | 666.0801 | 718.0402 | 843.8497 | 971.3582 | 1087.2317 | 1188.1353 | 1274.1478 | 1354.1149 | 1427.8336
Rokeby |  | 28224 | 60.4502 | 63.5747 | 64.5769 | 66.2513 | 68.2129 | 70.4294 | 72.3076 | 74.4771 | 75.4588 | 76.423 | 77.1391 | 77.7477 | 144.2532 | 145.1833 | 145.154 | 147.0021 | 149.637 | 152.7698 | 155.4997 | 157.5662 | 158.5498 | 159.3889 | 159.9413 | 161.455 | 1.52 | 1.52 | 1.52 | 1.7164 | 2.0306 | 2.7966 | 3.5822 | 4.3089 | 4.957 | 5.5266 | 6.0765 | 6.6068
Rokeby |  | 28225 | 3.0807 | 3.2399 | 3.291 | 3.3763 | 3.4763 | 3.5893 | 3.685 | 3.7955 | 3.8456 | 3.8947 | 3.9312 | 3.9622 | 4.0729 | 4.0991 | 4.0983 | 4.1505 | 4.2249 | 4.3133 | 4.3904 | 4.4487 | 4.4765 | 4.5002 | 4.5158 | 4.5585 | 213.7942 | 280.5297 | 320.8515 | 354.9969 | 395.2099 | 492.272 | 590.1998 | 678.6585 | 755.1258 | 819.7691 | 879.345 | 933.7972
Rokeby |  | 28228 | 60.1464 | 63.2552 | 64.2523 | 65.9183 | 67.87 | 70.0753 | 71.9441 | 74.1028 | 75.0795 | 76.0388 | 76.7513 | 77.3569 | 128.6854 | 129.5151 | 129.489 | 131.1376 | 133.4881 | 136.2829 | 138.7182 | 140.5616 | 141.4391 | 142.1877 | 142.6804 | 144.0308 | 31.2018 | 37.4422 | 57.6609 | 64.0328 | 67.7545 | 76.737 | 85.7988 | 93.9833 | 101.0571 | 107.0356 | 112.5438 | 117.5766
Rokeby |  | 28229 | 4.927 | 5.1817 | 5.2634 | 5.3998 | 5.5597 | 5.7404 | 5.8934 | 6.0703 | 6.1503 | 6.2289 | 6.2872 | 6.3368 | 11.7618 | 11.8376 | 11.8352 | 11.9859 | 12.2008 | 12.4562 | 12.6788 | 12.8473 | 12.9275 | 12.9959 | 13.0409 | 13.1644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby |  | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.0443 | 972.1924 | 1165.835 | 1252.0011 | 1309.5153 | 1447.2659 | 1585.3961 | 1709.6224 | 1816.7028 | 1907.072 | 1990.2743 | 2066.2614
Rokeby |  | 28231 | 118.9917 | 125.142 | 127.1147 | 130.4107 | 134.2718 | 138.6348 | 142.332 | 146.6026 | 148.5349 | 150.4328 | 151.8424 | 153.0405 | 217.6117 | 219.0149 | 218.9706 | 221.7586 | 225.7334 | 230.4594 | 234.5776 | 237.6949 | 239.1788 | 240.4446 | 241.2779 | 243.5614 | 535.2669 | 605.8822 | 673.5566 | 743.1335 | 810.3107 | 972.9782 | 1139.4127 | 1293.476 | 1431.4004 | 1553.3232 | 1671.765 | 1782.8457
Rokeby |  | 28232 | 75.7386 | 79.6533 | 80.9089 | 83.0069 | 85.4645 | 88.2415 | 90.5948 | 93.313 | 94.543 | 95.751 | 96.6482 | 97.4108 | 173.6888 | 174.8088 | 174.7734 | 176.9987 | 180.1712 | 183.9432 | 187.2302 | 189.7184 | 190.9027 | 191.9131 | 192.5782 | 194.4008 | 66.439 | 84.6631 | 86.3341 | 99.7146 | 121.9164 | 178.3714 | 239.1756 | 298.65 | 355.1153 | 408.2381 | 463.4067 | 520.9635
Rosebery 22kV |  | 97001 | 15.0997 | 15.8801 | 16.1304 | 16.5487 | 17.0387 | 17.5923 | 18.0615 | 18.6034 | 18.8486 | 19.0894 | 19.2683 | 19.4203 | 31.3483 | 31.5504 | 31.544 | 31.9456 | 32.5182 | 33.199 | 33.7923 | 34.2414 | 34.4551 | 34.6375 | 34.7575 | 35.0865 | 130.3652 | 148.3338 | 166.7803 | 198.6749 | 224.1819 | 287.359 | 353.022 | 414.1939 | 468.6334 | 515.8146 | 560.1419 | 601.1843
Rosebery 22kV |  | 97002 | 18.9829 | 19.9641 | 20.2788 | 20.8046 | 21.4206 | 22.1166 | 22.7064 | 23.3877 | 23.696 | 23.9987 | 24.2236 | 24.4148 | 38.1278 | 38.3737 | 38.3659 | 38.8544 | 39.5508 | 40.3789 | 41.1004 | 41.6466 | 41.9066 | 42.1284 | 42.2744 | 42.6745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV |  | 97014 | 186.1898 | 195.8134 | 198.9001 | 204.0575 | 210.099 | 216.926 | 222.7111 | 229.3934 | 232.4169 | 235.3866 | 237.5922 | 239.4669 | 221.7492 | 223.1791 | 223.134 | 225.975 | 230.0253 | 234.8412 | 239.0377 | 242.2143 | 243.7263 | 245.0163 | 245.8654 | 248.1924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 44kV |  | 97013 | 17.1512 | 18.0376 | 18.322 | 18.7971 | 19.3536 | 19.9825 | 20.5154 | 21.1309 | 21.4094 | 21.683 | 21.8862 | 22.0589 | 31.3377 | 31.5398 | 31.5334 | 31.9349 | 32.5073 | 33.1879 | 33.7809 | 34.2298 | 34.4435 | 34.6258 | 34.7458 | 35.0746 | 111.7537 | 137.1794 | 144.2691 | 150.1108 | 159.6886 | 183.7351 | 209.2331 | 233.6444 | 256.1244 | 276.3877 | 296.2353 | 315.3856
Savage River |  | 95001 | 19.6049 | 20.6182 | 20.9432 | 21.4863 | 22.1224 | 22.8413 | 23.4504 | 24.154 | 24.4724 | 24.7851 | 25.0173 | 25.2147 | 29.5581 | 29.7487 | 29.7427 | 30.1214 | 30.6613 | 31.3032 | 31.8626 | 32.286 | 32.4876 | 32.6595 | 32.7727 | 33.0828 | 577.3695 | 653.3557 | 695.4537 | 778.5968 | 888.0136 | 1155.8923 | 1432.2982 | 1689.9662 | 1922.1611 | 2129.172 | 2333.113 | 2535.3371
Scottsdale |  | 54003 | 146.4575 | 154.0274 | 156.4554 | 160.5123 | 165.2645 | 170.6346 | 175.1852 | 180.4415 | 182.8199 | 185.1558 | 186.8907 | 188.3654 | 146.3093 | 147.2527 | 147.2229 | 149.0974 | 151.7698 | 154.9473 | 157.7161 | 159.8121 | 160.8097 | 161.6608 | 162.221 | 163.7563 | 12.58 | 12.58 | 16.2942 | 23.6289 | 32.7492 | 54.9757 | 77.6578 | 98.4125 | 116.621 | 132.2893 | 147.0557 | 160.9325
Scottsdale |  | 54004 | 4.6571 | 4.8978 | 4.975 | 5.104 | 5.2551 | 5.4259 | 5.5706 | 5.7377 | 5.8134 | 5.8877 | 5.9428 | 5.9897 | 5.8274 | 5.865 | 5.8638 | 5.9385 | 6.0449 | 6.1715 | 6.2817 | 6.3652 | 6.405 | 6.4389 | 6.4612 | 6.5223 | 208.1658 | 219.6515 | 226.6599 | 274.1218 | 346.2209 | 521.9736 | 702.958 | 872.0398 | 1025.5843 | 1164.2746 | 1303.1013 | 1442.1459
Scottsdale |  | 54005 | 65.5696 | 68.9587 | 70.0457 | 71.862 | 73.9896 | 76.3938 | 78.4311 | 80.7844 | 81.8492 | 82.895 | 83.6717 | 84.332 | 79.7528 | 80.2671 | 80.2508 | 81.2726 | 82.7293 | 84.4614 | 85.9706 | 87.1131 | 87.6569 | 88.1209 | 88.4263 | 89.2631 | 4.02 | 4.02 | 4.02 | 8.6204 | 15.981 | 33.9226 | 52.3242 | 69.3456 | 84.5269 | 97.8681 | 110.7492 | 123.1702
Scottsdale |  | 54006 | 0.79372 | 0.83474 | 0.8479 | 0.86989 | 0.89564 | 0.92474 | 0.94941 | 0.97789 | 0.99078 | 1.0034 | 1.0128 | 1.0208 | 44.9967 | 45.2869 | 45.2777 | 45.8542 | 46.6761 | 47.6533 | 48.5048 | 49.1494 | 49.4562 | 49.718 | 49.8903 | 50.3625 | 436.9898 | 513.7843 | 562.0719 | 613.8807 | 670.6216 | 807.6142 | 947.9554 | 1079.1704 | 1199.2226 | 1309.1886 | 1421.4218 | 1536.939
Scottsdale |  | 54007 | 44.5717 | 46.8755 | 47.6144 | 48.8491 | 50.2953 | 51.9296 | 53.3145 | 54.9142 | 55.638 | 56.3489 | 56.8769 | 57.3257 | 93.3435 | 93.9454 | 93.9264 | 95.1223 | 96.8272 | 98.8544 | 100.6209 | 101.9581 | 102.5945 | 103.1375 | 103.4949 | 104.4745 | 80.26 | 83.7736 | 95.4767 | 125.418 | 168.4776 | 272.7141 | 379.0988 | 477.3 | 565.0103 | 642.4756 | 717.8351 | 791.0953
Smithton |  | 93001 | 121.6033 | 127.8886 | 129.9046 | 133.273 | 137.2188 | 141.6776 | 145.4559 | 149.8202 | 151.7949 | 153.7344 | 155.175 | 156.3994 | 113.3972 | 114.1284 | 114.1054 | 115.5582 | 117.6294 | 120.0921 | 122.2381 | 123.8626 | 124.6358 | 125.2954 | 125.7297 | 126.9196 | 64.432 | 69.4248 | 71.1648 | 102.2147 | 152.2214 | 275.6495 | 404.8147 | 527.7684 | 641.5575 | 745.9449 | 851.3077 | 955.6618
Smithton |  | 93002 | 166.7711 | 175.391 | 178.1558 | 182.7753 | 188.1867 | 194.3016 | 199.4834 | 205.4687 | 208.1769 | 210.8369 | 212.8124 | 214.4916 | 122.9452 | 123.738 | 123.713 | 125.2882 | 127.5338 | 130.2039 | 132.5305 | 134.2918 | 135.1301 | 135.8453 | 136.3161 | 137.6062 | 159.3585 | 179.8626 | 203.7944 | 230.3646 | 267.7225 | 359.8281 | 455.1291 | 543.6955 | 622.6317 | 691.512 | 757.0726 | 818.9528
Smithton |  | 93003 | 111.5598 | 117.326 | 119.1755 | 122.2657 | 125.8856 | 129.9761 | 133.4424 | 137.4462 | 139.2579 | 141.0372 | 142.3587 | 143.482 | 112.2118 | 112.9354 | 112.9125 | 114.3502 | 116.3997 | 118.8367 | 120.9603 | 122.5677 | 123.3329 | 123.9856 | 124.4153 | 125.5928 | 107.6714 | 114.5735 | 131.1609 | 146.5082 | 161.9375 | 198.0619 | 233.4327 | 264.479 | 290.6023 | 312.1413 | 331.5424 | 348.9082
Smithton |  | 93004 | 93.8952 | 98.7483 | 100.3049 | 102.9058 | 105.9525 | 109.3954 | 112.3128 | 115.6826 | 117.2074 | 118.705 | 119.8173 | 120.7627 | 114.9188 | 115.6598 | 115.6365 | 117.1088 | 119.2078 | 121.7036 | 123.8784 | 125.5246 | 126.3082 | 126.9767 | 127.4167 | 128.6226 | 250.992 | 278.4441 | 301.4517 | 355.4906 | 434.1341 | 625.205 | 819.7206 | 997.4273 | 1153.1324 | 1286.3532 | 1411.2241 | 1527.5549
Smithton |  | 93005 | 80.7522 | 84.9261 | 86.2648 | 88.5016 | 91.1219 | 94.0828 | 96.5919 | 99.49 | 100.8014 | 102.0894 | 103.0459 | 103.859 | 120.65 | 121.428 | 121.4034 | 122.9491 | 125.1529 | 127.7731 | 130.0563 | 131.7847 | 132.6073 | 133.3092 | 133.7712 | 135.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smithton |  | 93006 | 68.6768 | 72.2265 | 73.365 | 75.2674 | 77.4958 | 80.014 | 82.1478 | 84.6126 | 85.7278 | 86.8232 | 87.6368 | 88.3283 | 68.3 | 68.7404 | 68.7265 | 69.6015 | 70.8491 | 72.3324 | 73.6249 | 74.6033 | 75.069 | 75.4663 | 75.7279 | 76.4446 | 651.2667 | 841.9093 | 1023.1312 | 1113.562 | 1196.3719 | 1393.4016 | 1589.6581 | 1765.0746 | 1915.5522 | 2042.2242 | 2158.9151 | 2265.9247
Sorell |  | 41511 | 58.2694 | 61.2811 | 62.2472 | 63.8612 | 65.7519 | 67.8885 | 69.699 | 71.7902 | 72.7365 | 73.6658 | 74.3561 | 74.9428 | 125.4877 | 126.2969 | 126.2714 | 127.8791 | 130.1712 | 132.8965 | 135.2713 | 137.0689 | 137.9246 | 138.6545 | 139.1351 | 140.4519 | 153.2509 | 170.5435 | 200.2176 | 222.0591 | 242.0653 | 289.6973 | 337.3222 | 380.1632 | 417.2317 | 448.7717 | 478.2132 | 505.647
Sorell |  | 41512 | 92.9189 | 97.7216 | 99.262 | 101.8358 | 104.8509 | 108.2579 | 111.145 | 114.4798 | 115.9887 | 117.4708 | 118.5715 | 119.5071 | 129.2303 | 130.0636 | 130.0373 | 131.693 | 134.0535 | 136.86 | 139.3057 | 141.1569 | 142.0381 | 142.7898 | 143.2847 | 144.6408 | 802.0427 | 1045.7252 | 1256.2631 | 1345.614 | 1442.3542 | 1676.2045 | 1913.6195 | 2130.7179 | 2322.0439 | 2488.2206 | 2646.8134 | 2798.0029
Sorell |  | 41513 | 83.4816 | 87.7965 | 89.1805 | 91.4929 | 94.2018 | 97.2628 | 99.8566 | 102.8527 | 104.2084 | 105.5399 | 106.5288 | 107.3694 | 141.786 | 142.7002 | 142.6714 | 144.4879 | 147.0777 | 150.1569 | 152.8401 | 154.8713 | 155.8381 | 156.6628 | 157.2058 | 158.6936 | 153.6671 | 175.0495 | 196.5501 | 239.0782 | 290.6442 | 417.5661 | 549.9774 | 675.7183 | 792.0941 | 899.3488 | 1008.8205 | 1120.8902
Sorell |  | 41514 | 51.9166 | 54.6 | 55.4607 | 56.8988 | 58.5834 | 60.487 | 62.1001 | 63.9634 | 64.8064 | 65.6345 | 66.2495 | 66.7722 | 69.3097 | 69.7567 | 69.7426 | 70.6305 | 71.8965 | 73.4018 | 74.7134 | 75.7063 | 76.1789 | 76.5821 | 76.8475 | 77.5748 | 410.1948 | 460.9972 | 493.0281 | 625.7315 | 789.9264 | 1199.9813 | 1636.1193 | 2058.9812 | 2457.3393 | 2828.2528 | 3206.8742 | 3568.5084
Sorell |  | 41515 | 51.9476 | 54.6326 | 55.4938 | 56.9328 | 58.6184 | 60.5231 | 62.1372 | 64.0016 | 64.8451 | 65.6737 | 66.2891 | 66.8121 | 102.8764 | 103.5398 | 103.5189 | 104.8369 | 106.716 | 108.9502 | 110.8971 | 112.3708 | 113.0723 | 113.6707 | 114.0647 | 115.1442 | 367.9298 | 400.0471 | 441.4956 | 528.6738 | 655.1152 | 968.4243 | 1294.0595 | 1597.6279 | 1868.5802 | 2105.0407 | 2330.0345 | 2540.5202
Sorell |  | 41516 | 78.6059 | 82.6688 | 83.972 | 86.1493 | 88.7 | 91.5822 | 94.0245 | 96.8457 | 98.1222 | 99.3759 | 100.3071 | 101.0986 | 150.1943 | 151.1628 | 151.1323 | 153.0565 | 155.7999 | 159.0617 | 161.9041 | 164.0557 | 165.0798 | 165.9535 | 166.5286 | 168.1047 | 867.503 | 1001.1435 | 1176.9602 | 1301.725 | 1401.5363 | 1639.0733 | 1876.6758 | 2090.875 | 2276.9857 | 2436.1818 | 2585.4077 | 2720.3359
Sorell |  | 41517 | 64.9339 | 68.2901 | 69.3666 | 71.1653 | 73.2723 | 75.6532 | 77.6707 | 80.0012 | 81.0557 | 82.0913 | 82.8605 | 83.5143 | 116.4061 | 117.1567 | 117.133 | 118.6244 | 120.7506 | 123.2786 | 125.4816 | 127.1491 | 127.9428 | 128.62 | 129.0657 | 130.2873 | 971.056 | 1137.5542 | 1365.5486 | 1473.3613 | 1583.9831 | 1846.8841 | 2109.1725 | 2344.4884 | 2547.3529 | 2718.9947 | 2877.7778 | 3022.198
Sorell |  | 41518 | 67.965 | 71.4779 | 72.6046 | 74.4872 | 76.6926 | 79.1846 | 81.2964 | 83.7356 | 84.8393 | 85.9233 | 86.7284 | 87.4128 | 133.0331 | 133.8909 | 133.8639 | 135.5683 | 137.9982 | 140.8873 | 143.4049 | 145.3106 | 146.2177 | 146.9916 | 147.501 | 148.897 | 162.2862 | 176.1792 | 204.3312 | 229.0475 | 264.1985 | 347.4703 | 429.9897 | 503.2937 | 565.7061 | 617.7641 | 665.1922 | 708.1279
St Leonards |  | 66101 | 29.2753 | 30.7885 | 31.2738 | 32.0847 | 33.0347 | 34.1081 | 35.0177 | 36.0684 | 36.5438 | 37.0107 | 37.3575 | 37.6523 | 57.172 | 57.5407 | 57.529 | 58.2615 | 59.3058 | 60.5474 | 61.6294 | 62.4484 | 62.8382 | 63.1708 | 63.3897 | 63.9896 | 646.886 | 735.5323 | 890.9025 | 986.1631 | 1077.226 | 1296.4654 | 1517.8745 | 1719.2075 | 1895.9421 | 2049.6091 | 2197.8335 | 2342.7496
St Leonards |  | 66102 | 67.0886 | 70.5562 | 71.6684 | 73.5268 | 75.7037 | 78.1636 | 80.2481 | 82.6559 | 83.7453 | 84.8154 | 85.6101 | 86.2856 | 160.4443 | 161.4789 | 161.4463 | 163.5018 | 166.4324 | 169.9169 | 172.9532 | 175.2516 | 176.3456 | 177.279 | 177.8933 | 179.577 | 638.8332 | 719.9602 | 815.2075 | 917.4078 | 999.0965 | 1197.9098 | 1402.0278 | 1591.9938 | 1763.8068 | 1918.4206 | 2072.6966 | 2227.4807
St Leonards |  | 66103 | 66.273 | 69.6985 | 70.7972 | 72.6329 | 74.7833 | 77.2134 | 79.2725 | 81.651 | 82.7273 | 83.7843 | 84.5694 | 85.2367 | 176.0305 | 177.1656 | 177.1297 | 179.385 | 182.6003 | 186.4232 | 189.7545 | 192.2762 | 193.4765 | 194.5005 | 195.1745 | 197.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards |  | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.7301 | 478.3932 | 553.3131 | 596.1618 | 654.9368 | 798.8361 | 948.1448 | 1089.3987 | 1220.168 | 1341.6173 | 1467.9837 | 1601.9837
St Leonards |  | 66105 | 48.9091 | 51.4371 | 52.2479 | 53.6027 | 55.1897 | 56.9831 | 58.5027 | 60.258 | 61.0523 | 61.8324 | 62.4117 | 62.9042 | 108.9455 | 109.648 | 109.6259 | 111.0216 | 113.0116 | 115.3776 | 117.4393 | 119 | 119.7429 | 120.3766 | 120.7938 | 121.937 | 486.816 | 553.5116 | 623.6564 | 692.3774 | 779.4302 | 992.5586 | 1212.3826 | 1417.1904 | 1601.5946 | 1765.7017 | 1926.704 | 2085.0279
St Leonards |  | 66106 | 74.5928 | 78.4483 | 79.6849 | 81.7511 | 84.1715 | 86.9066 | 89.2242 | 91.9013 | 93.1127 | 94.3024 | 95.186 | 95.9371 | 156.7789 | 157.7899 | 157.758 | 159.7666 | 162.6302 | 166.035 | 169.002 | 171.2479 | 172.3169 | 173.2289 | 173.8293 | 175.4745 | 164.4552 | 196.7178 | 206.6484 | 231.5913 | 263.5794 | 342.4093 | 423.9586 | 499.6995 | 567.0827 | 625.6667 | 681.0937 | 732.96
St Leonards |  | 66107 | 39.9121 | 41.975 | 42.6367 | 43.7423 | 45.0373 | 46.5008 | 47.7409 | 49.1733 | 49.8215 | 50.458 | 50.9308 | 51.3327 | 103.524 | 104.1915 | 104.1704 | 105.4968 | 107.3877 | 109.6359 | 111.5951 | 113.0781 | 113.784 | 114.3862 | 114.7826 | 115.869 | 0 | 0 | 0 | 0.96375 | 2.3628 | 5.3947 | 8.107 | 10.259 | 11.8836 | 13.0809 | 14.0456 | 14.821
St Leonards |  | 66108 | 1.2419 | 1.3061 | 1.3267 | 1.3611 | 1.4014 | 1.4469 | 1.4855 | 1.5301 | 1.5502 | 1.5701 | 1.5848 | 1.5973 | 1.3711 | 1.38 | 1.3797 | 1.3973 | 1.4223 | 1.4521 | 1.478 | 1.4977 | 1.507 | 1.515 | 1.5203 | 1.5347 | 332.5099 | 395.6661 | 448.6872 | 483.6588 | 515.2871 | 591.4293 | 668.4248 | 738.4767 | 799.7381 | 852.3238 | 901.6918 | 947.7884
St Leonards |  | 66109 | 26.9355 | 28.3277 | 28.7743 | 29.5204 | 30.3944 | 31.382 | 32.219 | 33.1857 | 33.6231 | 34.0527 | 34.3718 | 34.643 | 58.3488 | 58.725 | 58.7131 | 59.4607 | 60.5264 | 61.7936 | 62.8979 | 63.7337 | 64.1316 | 64.471 | 64.6944 | 65.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards |  | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.5733 | 200.7163 | 210.9051 | 232.6599 | 262.3607 | 334.2833 | 407.8133 | 475.6849 | 535.9459 | 588.3366 | 637.9009 | 684.0551
St Marys |  | 57003 | 18.3166 | 19.2634 | 19.567 | 20.0744 | 20.6687 | 21.3403 | 21.9094 | 22.5668 | 22.8643 | 23.1564 | 23.3734 | 23.5578 | 35.5948 | 35.8243 | 35.817 | 36.2731 | 36.9232 | 37.6963 | 38.3699 | 38.8798 | 39.1225 | 39.3295 | 39.4658 | 39.8394 | 669.8822 | 756.4733 | 826.549 | 919.6976 | 1036.3285 | 1319.8256 | 1611.3237 | 1883.8253 | 2132.2273 | 2358.5003 | 2588.4336 | 2822.9685
St Marys |  | 57004 | 102.6323 | 107.9371 | 109.6386 | 112.4814 | 115.8117 | 119.5749 | 122.7638 | 126.4472 | 128.1139 | 129.7508 | 130.9666 | 132 | 161.9496 | 162.9939 | 162.9609 | 165.0358 | 167.9938 | 171.511 | 174.5758 | 176.8958 | 178.0001 | 178.9421 | 179.5623 | 181.2617 | 63.1705 | 89.402 | 96.3607 | 106.6832 | 123.5401 | 165.304 | 208.5383 | 248.538 | 283.8594 | 314.2676 | 342.7231 | 369.0565
St Marys |  | 57005 | 28.6109 | 30.0897 | 30.564 | 31.3565 | 32.2849 | 33.334 | 34.2229 | 35.2498 | 35.7144 | 36.1707 | 36.5097 | 36.7977 | 45.9634 | 46.2598 | 46.2504 | 46.8393 | 47.6789 | 48.6771 | 49.5469 | 50.2053 | 50.5187 | 50.7861 | 50.9621 | 51.4444 | 1476.7204 | 1652.2157 | 1866.954 | 2055.4579 | 2236.3775 | 2674.1251 | 3119.8592 | 3528.8456 | 3890.1036 | 4203.7764 | 4501.9835 | 4781.5004
St Marys |  | 57006 | 101.612 | 106.864 | 108.5485 | 111.3631 | 114.6603 | 118.386 | 121.5432 | 125.19 | 126.8401 | 128.4608 | 129.6645 | 130.6876 | 222.0546 | 223.4865 | 223.4413 | 226.2862 | 230.3421 | 235.1646 | 239.3669 | 242.5479 | 244.062 | 245.3537 | 246.204 | 248.5342 | 655.322 | 763.6561 | 854.1567 | 958.8608 | 1054.3109 | 1289.4785 | 1534.1568 | 1764.3963 | 1973.5025 | 2160.2798 | 2342.5669 | 2516.8619
Trevallyn |  | 61021 | 77.5847 | 81.5948 | 82.881 | 85.0301 | 87.5476 | 90.3923 | 92.803 | 95.5875 | 96.8474 | 98.0848 | 99.0039 | 99.7851 | 164.7031 | 165.7651 | 165.7316 | 167.8418 | 170.8501 | 174.4271 | 177.544 | 179.9034 | 181.0265 | 181.9846 | 182.6153 | 184.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn |  | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391.553 | 413.2571 | 474.1536 | 543.4136 | 635.5032 | 860.2043 | 1091.3946 | 1306.4463 | 1499.8468 | 1671.669 | 1839.6852 | 2003.8347
Trevallyn |  | 61023 | 67.2378 | 70.7131 | 71.8278 | 73.6903 | 75.8721 | 78.3374 | 80.4266 | 82.8397 | 83.9316 | 85.004 | 85.8005 | 86.4775 | 134.9448 | 135.815 | 135.7875 | 137.5164 | 139.9812 | 142.9119 | 145.4657 | 147.3988 | 148.3189 | 149.1039 | 149.6207 | 151.0367 | 20 | 20 | 20 | 37.0695 | 65.7401 | 139.8829 | 221.6773 | 304.3926 | 386.3768 | 467.487 | 556.2036 | 652.96
Trevallyn |  | 61024 | 116.6441 | 122.6731 | 124.6069 | 127.8379 | 131.6228 | 135.8997 | 139.524 | 143.7103 | 145.6045 | 147.4649 | 148.8467 | 150.0212 | 173.3389 | 174.4566 | 174.4213 | 176.6421 | 179.8082 | 183.5727 | 186.8531 | 189.3362 | 190.5181 | 191.5265 | 192.1902 | 194.0092 | 578.5569 | 686.7038 | 752.7904 | 845.0332 | 932.3138 | 1144.608 | 1361.3177 | 1560.1751 | 1735.4784 | 1887.223 | 2031.1588 | 2167.5908
Trevallyn |  | 61025 | 73.4165 | 77.2111 | 78.4283 | 80.4619 | 82.8441 | 85.5361 | 87.8172 | 90.4521 | 91.6443 | 92.8152 | 93.6849 | 94.4242 | 154.4457 | 155.4416 | 155.4101 | 157.3889 | 160.2099 | 163.564 | 166.4869 | 168.6993 | 169.7525 | 170.6509 | 171.2423 | 172.863 | 22.9499 | 22.9499 | 22.9499 | 31.3285 | 44.2362 | 74.2721 | 103.4517 | 128.8465 | 150.0415 | 167.3988 | 182.9604 | 196.8583
Trevallyn |  | 61026 | 99.804 | 104.9626 | 106.6172 | 109.3817 | 112.6202 | 116.2796 | 119.3806 | 122.9626 | 124.5833 | 126.1751 | 127.3574 | 128.3623 | 107.8538 | 108.5493 | 108.5274 | 109.9092 | 111.8791 | 114.2215 | 116.2626 | 117.8076 | 118.543 | 119.1704 | 119.5834 | 120.7152 | 1266.7825 | 1439.7214 | 1561.2759 | 1687.0003 | 1811.1083 | 2111.9146 | 2417.0172 | 2694.171 | 2934.972 | 3139.326 | 3328.0947 | 3500.7375
Trevallyn |  | 61027 | 92.5037 | 97.2849 | 98.8185 | 101.3808 | 104.3824 | 107.7742 | 110.6484 | 113.9683 | 115.4705 | 116.9459 | 118.0417 | 118.9731 | 203.5776 | 204.8904 | 204.8489 | 207.4571 | 211.1755 | 215.5967 | 219.4494 | 222.3657 | 223.7538 | 224.938 | 225.7176 | 227.8538 | 1236.4134 | 1394.2827 | 1533.4222 | 1652.6834 | 1770.5662 | 2051.779 | 2332.9048 | 2587.7435 | 2811.135 | 3004.2591 | 3187.6863 | 3356.0337
Trevallyn |  | 61028 | 101.8239 | 107.0869 | 108.775 | 111.5955 | 114.8995 | 118.633 | 121.7968 | 125.4512 | 127.1048 | 128.7288 | 129.935 | 130.9603 | 247.9779 | 249.5769 | 249.5264 | 252.7035 | 257.2329 | 262.6183 | 267.3112 | 270.8636 | 272.5544 | 273.9969 | 274.9465 | 277.5487 | 518.0775 | 613.0201 | 690.484 | 732.4759 | 781.5305 | 899.415 | 1017.9407 | 1124.7863 | 1217.1281 | 1295.3384 | 1367.7035 | 1434.2098
Trevallyn |  | 61029 | 49.3435 | 51.894 | 52.712 | 54.0788 | 55.6799 | 57.4892 | 59.0223 | 60.7933 | 61.5945 | 62.3816 | 62.9661 | 63.4629 | 113.3237 | 114.0545 | 114.0314 | 115.4833 | 117.5532 | 120.0143 | 122.1589 | 123.7823 | 124.555 | 125.2142 | 125.6482 | 126.8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn |  | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527.5008 | 620.624 | 743.948 | 804.2199 | 848.0336 | 950.9699 | 1053.5232 | 1145.7417 | 1225.9315 | 1294.9669 | 1360.6008 | 1423.1967
Trevallyn |  | 61037 | 51.8625 | 54.5431 | 55.4029 | 56.8395 | 58.5224 | 60.424 | 62.0354 | 63.8967 | 64.7389 | 65.5661 | 66.1805 | 66.7027 | 89.0883 | 89.6627 | 89.6446 | 90.786 | 92.4132 | 94.348 | 96.0339 | 97.3102 | 97.9176 | 98.4359 | 98.777 | 99.7119 | 10 | 10 | 10 | 44.1282 | 102.7506 | 256.8939 | 427.9784 | 599.5339 | 765.5065 | 923.6479 | 1088.8935 | 1260.7597
Trevallyn |  | 61039 | 106.6754 | 112.1891 | 113.9576 | 116.9125 | 120.3739 | 124.2853 | 127.5998 | 131.4284 | 133.1607 | 134.8621 | 136.1258 | 137.1999 | 143.698 | 144.6246 | 144.5953 | 146.4363 | 149.061 | 152.1818 | 154.9012 | 156.9598 | 157.9396 | 158.7755 | 159.3257 | 160.8336 | 106.2308 | 133.3017 | 142.6501 | 196.3903 | 282.1731 | 491.1403 | 706.0766 | 906.4199 | 1087.396 | 1249.0781 | 1407.8646 | 1563.1016
Trevallyn |  | 61040 | 103.0312 | 108.3565 | 110.0646 | 112.9185 | 116.2617 | 120.0395 | 123.2408 | 126.9386 | 128.6117 | 130.255 | 131.4755 | 132.5129 | 183.8212 | 185.0065 | 184.9691 | 187.3242 | 190.6818 | 194.6739 | 198.1526 | 200.7859 | 202.0393 | 203.1087 | 203.8125 | 205.7415 | 831.0693 | 998.5495 | 1163.8321 | 1271.4647 | 1360.4073 | 1572.9782 | 1785.8011 | 1977.1038 | 2142.1679 | 2281.8608 | 2411.0583 | 2529.754
Trevallyn |  | 61041 | 67.9365 | 71.4479 | 72.5742 | 74.456 | 76.6604 | 79.1514 | 81.2623 | 83.7005 | 84.8037 | 85.8873 | 86.6921 | 87.3761 | 143.8673 | 144.795 | 144.7657 | 146.6089 | 149.2367 | 152.3612 | 155.0838 | 157.1447 | 158.1257 | 158.9626 | 159.5135 | 161.0232 | 1555.2425 | 1885.1667 | 2099.1643 | 2273.186 | 2411.5244 | 2740.3233 | 3068.7151 | 3364.2671 | 3620.5908 | 3837.7857 | 4040.7029 | 4228.326
Trevallyn |  | 61043 | 132.6268 | 139.4819 | 141.6806 | 145.3544 | 149.6579 | 154.5208 | 158.6417 | 163.4016 | 165.5554 | 167.6707 | 169.2418 | 170.5772 | 247.5499 | 249.1462 | 249.0958 | 252.2673 | 256.7889 | 262.1651 | 266.8499 | 270.3961 | 272.0841 | 273.5241 | 274.472 | 277.0697 | 96.6826 | 103.8832 | 117.5561 | 127.7813 | 144.3364 | 185.0458 | 226.9222 | 265.4477 | 299.2824 | 328.253 | 355.2166 | 380.0439
Triabunna |  | 43505 | 11.263 | 11.8451 | 12.0318 | 12.3438 | 12.7093 | 13.1222 | 13.4722 | 13.8764 | 14.0593 | 14.239 | 14.3724 | 14.4858 | 18.1938 | 18.3111 | 18.3074 | 18.5405 | 18.8728 | 19.268 | 19.6123 | 19.8729 | 19.997 | 20.1028 | 20.1725 | 20.3634 | 377.1965 | 413.4441 | 450.1398 | 511.1269 | 592.7314 | 788.9331 | 987.4638 | 1168.7332 | 1328.5229 | 1467.6051 | 1600.9144 | 1725.9775
Triabunna |  | 43506 | 40.7636 | 42.8706 | 43.5464 | 44.6755 | 45.9982 | 47.4929 | 48.7594 | 50.2224 | 50.8844 | 51.5346 | 52.0174 | 52.4279 | 59.9827 | 60.3694 | 60.3572 | 61.1257 | 62.2213 | 63.524 | 64.6591 | 65.5184 | 65.9274 | 66.2763 | 66.506 | 67.1354 | 393.7613 | 420.0721 | 457.1037 | 520.8713 | 603.0404 | 803.8826 | 1010.6901 | 1202.806 | 1374.8581 | 1526.6666 | 1673.8767 | 1815.0323
Triabunna |  | 43507 | 64.8799 | 68.2333 | 69.3089 | 71.1061 | 73.2113 | 75.5902 | 77.6061 | 79.9346 | 80.9882 | 82.023 | 82.7916 | 83.4449 | 83.7253 | 84.2652 | 84.2482 | 85.3208 | 86.8501 | 88.6684 | 90.2529 | 91.4523 | 92.0232 | 92.5102 | 92.8308 | 93.7094 | 17.36 | 17.36 | 17.36 | 27.5993 | 46.2755 | 99.0232 | 162.304 | 230.8525 | 301.9403 | 373.528 | 451.0962 | 531.3901
Tungatinah |  | 49303 | 7.1458 | 7.5152 | 7.6337 | 7.8316 | 8.0635 | 8.3255 | 8.5475 | 8.804 | 8.92 | 9.034 | 9.1186 | 9.1906 | 11.159 | 11.231 | 11.2287 | 11.3717 | 11.5755 | 11.8178 | 12.029 | 12.1889 | 12.265 | 12.3299 | 12.3726 | 12.4897 | 0 | 0 | 0 | 0.63715 | 1.6566 | 4.1415 | 6.6901 | 9.0476 | 11.1502 | 12.9979 | 14.782 | 16.5023
Tungatinah |  | 49307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4782 | 2.4942 | 2.4937 | 2.5255 | 2.5707 | 2.6246 | 2.6715 | 2.707 | 2.7239 | 2.7383 | 2.7478 | 2.7738 | 96.9417 | 108.1079 | 118.9793 | 138.6468 | 161.5576 | 217.5563 | 275.4199 | 329.5083 | 378.2607 | 421.0584 | 462.3503 | 500.0564
Ulverstone |  | 82001 | 83.7917 | 88.1226 | 89.5118 | 91.8328 | 94.5516 | 97.624 | 100.2275 | 103.2348 | 104.5955 | 105.9319 | 106.9245 | 107.7682 | 72.0984 | 72.5633 | 72.5486 | 73.4723 | 74.7892 | 76.355 | 77.7194 | 78.7523 | 79.2439 | 79.6633 | 79.9394 | 80.6959 | 1123.256 | 1318.0637 | 1457.839 | 1572.7157 | 1692.9341 | 1980.3131 | 2267.5435 | 2524.6513 | 2744.9635 | 2929.6493 | 3098.5104 | 3251.7083
Ulverstone |  | 82002 | 67.6282 | 71.1237 | 72.2449 | 74.1181 | 76.3126 | 78.7923 | 80.8935 | 83.3207 | 84.4189 | 85.4975 | 86.2987 | 86.9796 | 226.7505 | 228.2127 | 228.1665 | 231.0716 | 235.2133 | 240.1377 | 244.4289 | 247.6772 | 249.2233 | 250.5423 | 251.4106 | 253.79 | 1140.0542 | 1364.9105 | 1492.928 | 1631.7522 | 1758.9225 | 2063.892 | 2371.2079 | 2649.9151 | 2892.9929 | 3101.1699 | 3296.1072 | 3476.2536
Ulverstone |  | 82003 | 84.1736 | 88.5242 | 89.9197 | 92.2513 | 94.9826 | 98.0689 | 100.6843 | 103.7053 | 105.0722 | 106.4147 | 107.4118 | 108.2594 | 116.2159 | 116.9652 | 116.9416 | 118.4305 | 120.5533 | 123.0772 | 125.2765 | 126.9413 | 127.7338 | 128.4098 | 128.8548 | 130.0743 | 92.8609 | 96.6349 | 103.2159 | 131.3507 | 173.6554 | 278.6422 | 388.8935 | 493.6654 | 589.6623 | 675.9962 | 760.6861 | 839.3811
Ulverstone |  | 82004 | 51.5741 | 54.2398 | 55.0948 | 56.5234 | 58.1969 | 60.088 | 61.6904 | 63.5414 | 64.3789 | 65.2015 | 65.8124 | 66.3317 | 43.9727 | 44.2562 | 44.2473 | 44.8107 | 45.6138 | 46.5688 | 47.401 | 48.0309 | 48.3307 | 48.5865 | 48.7549 | 49.2163 | 622.0242 | 732.2128 | 829.3269 | 911.337 | 1016.6985 | 1265.192 | 1510.1874 | 1726.6555 | 1909.9843 | 2062.1299 | 2200.0922 | 2324.4206
Ulverstone |  | 82005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.3678 | 60.6217 | 68.7456 | 75.9557 | 87.0622 | 112.9424 | 138.1496 | 160.159 | 178.5913 | 193.7336 | 207.3448 | 219.5255
Ulverstone |  | 82006 | 73.5525 | 77.3542 | 78.5736 | 80.611 | 82.9976 | 85.6946 | 87.9799 | 90.6197 | 91.8141 | 92.9872 | 93.8585 | 94.5991 | 185.6625 | 186.8597 | 186.8219 | 189.2006 | 192.5918 | 196.6239 | 200.1375 | 202.7972 | 204.0631 | 205.1432 | 205.8541 | 207.8024 | 69.838 | 77.244 | 77.439 | 97.6522 | 123.3403 | 185.7693 | 249.5408 | 308.2126 | 360.1914 | 405.5156 | 448.9053 | 490.3771
Ulverstone |  | 82007 | 39.1009 | 41.1219 | 41.7702 | 42.8533 | 44.122 | 45.5557 | 46.7706 | 48.1739 | 48.8089 | 49.4325 | 49.8957 | 50.2894 | 40.1992 | 40.4584 | 40.4503 | 40.9653 | 41.6995 | 42.5726 | 43.3333 | 43.9092 | 44.1833 | 44.4171 | 44.5711 | 44.9929 | 1098.7541 | 1287.399 | 1411.6717 | 1548.7479 | 1644.8004 | 1873.7046 | 2101.7851 | 2305.2974 | 2479.101 | 2624.2864 | 2756.5492 | 2876.1034
Ulverstone |  | 82008 | 37.5177 | 39.4568 | 40.0788 | 41.118 | 42.3354 | 43.7111 | 44.8768 | 46.2233 | 46.8325 | 47.4309 | 47.8754 | 48.2531 | 26.5165 | 26.6875 | 26.6821 | 27.0218 | 27.5061 | 28.082 | 28.5838 | 28.9637 | 29.1445 | 29.2987 | 29.4003 | 29.6785 | 70.0136 | 73.9136 | 79.1925 | 103.9758 | 146.748 | 261.0145 | 391.4264 | 527.3923 | 665.3751 | 804.1594 | 957.9001 | 1128.1213
Waddamana |  | 49202 | 10.2622 | 10.7927 | 10.9628 | 11.247 | 11.58 | 11.9563 | 12.2752 | 12.6435 | 12.8101 | 12.9738 | 13.0954 | 13.1987 | 17.8846 | 17.9999 | 17.9963 | 18.2254 | 18.5521 | 18.9405 | 19.279 | 19.5352 | 19.6571 | 19.7612 | 19.8297 | 20.0173 | 0 | 0 | 0 | 1.7096 | 5.4432 | 18.0782 | 36.1111 | 59.0599 | 86.5871 | 118.1172 | 156.3312 | 200.7458
Wayatinah |  | 49411 | 8.8687 | 9.3271 | 9.4741 | 9.7198 | 10.0076 | 10.3328 | 10.6083 | 10.9266 | 11.0706 | 11.2121 | 11.3172 | 11.4065 | 11.5131 | 11.5873 | 11.585 | 11.7325 | 11.9428 | 12.1928 | 12.4107 | 12.5756 | 12.6541 | 12.7211 | 12.7652 | 12.886 | 0 | 0 | 0 | 0.67237 | 1.7482 | 4.3704 | 7.0599 | 9.5476 | 11.7665 | 13.7163 | 15.599 | 17.4144
Wayatinah |  | 49412 | 25.5515 | 26.8722 | 27.2958 | 28.0036 | 28.8327 | 29.7696 | 30.5635 | 31.4805 | 31.8954 | 32.303 | 32.6057 | 32.8629 | 23.6462 | 23.7987 | 23.7939 | 24.0968 | 24.5287 | 25.0423 | 25.4898 | 25.8285 | 25.9897 | 26.1273 | 26.2178 | 26.466 | 109.0721 | 140.7551 | 162.2277 | 184.2506 | 214.0893 | 289.7462 | 370.7649 | 449.0505 | 521.7478 | 587.7926 | 653.0088 | 716.5161
Wesley Vale |  | 81001 | 27.3077 | 28.7191 | 29.1718 | 29.9283 | 30.8143 | 31.8156 | 32.6641 | 33.6442 | 34.0876 | 34.5232 | 34.8466 | 35.1216 | 48.6829 | 48.9968 | 48.9869 | 49.6106 | 50.4998 | 51.5571 | 52.4784 | 53.1758 | 53.5078 | 53.791 | 53.9774 | 54.4882 | 421.6238 | 464.6598 | 504.0969 | 540.0746 | 584.5908 | 691.8869 | 801.8567 | 903.2784 | 993.1844 | 1071.5244 | 1146.4756 | 1218.2042
Wesley Vale |  | 81002 | 47.2751 | 49.7186 | 50.5024 | 51.8119 | 53.3459 | 55.0793 | 56.5482 | 58.2449 | 59.0126 | 59.7666 | 60.3266 | 60.8026 | 63.3213 | 63.7296 | 63.7167 | 64.528 | 65.6846 | 67.0598 | 68.2581 | 69.1652 | 69.5969 | 69.9653 | 70.2078 | 70.8722 | 1361.0297 | 1534.8994 | 1702.5796 | 1857.7961 | 1996.1132 | 2322.8455 | 2646.8053 | 2934.9295 | 3180.7203 | 3386.3738 | 3574.7061 | 3746.6404
Wesley Vale |  | 81003 | 94.6792 | 99.5728 | 101.1425 | 103.765 | 106.8372 | 110.3088 | 113.2506 | 116.6486 | 118.1861 | 119.6962 | 120.8177 | 121.771 | 184.7729 | 185.9643 | 185.9267 | 188.294 | 191.6689 | 195.6818 | 199.1785 | 201.8254 | 203.0853 | 204.1602 | 204.8677 | 206.8066 | 462.1673 | 568.942 | 683.6493 | 752.9895 | 803.4015 | 924.1364 | 1045.031 | 1153.4553 | 1246.5541 | 1324.7679 | 1396.4355 | 1461.5896
Zs-Bellerive | Lindisfarne | 27171 | 69.0914 | 72.6625 | 73.808 | 75.7218 | 77.9637 | 80.497 | 82.6438 | 85.1234 | 86.2454 | 87.3474 | 88.1659 | 88.8615 | 148.6448 | 149.6033 | 149.573 | 151.4774 | 154.1925 | 157.4207 | 160.2337 | 162.3631 | 163.3767 | 164.2413 | 164.8105 | 166.3703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6711 | 82.2454 | 89.5413 | 98.7251 | 113.0849 | 147.122 | 180.8918 | 210.9432 | 236.5876 | 258.0357 | 277.6386 | 295.4498
Zs-Bellerive | Lindisfarne | 27173 | 20.9931 | 22.0782 | 22.4262 | 23.0077 | 23.6889 | 24.4586 | 25.1109 | 25.8644 | 26.2053 | 26.5401 | 26.7888 | 27.0002 | 39.9372 | 40.1947 | 40.1866 | 40.6982 | 41.4277 | 42.295 | 43.0508 | 43.6229 | 43.8952 | 44.1276 | 44.2805 | 44.6996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363.3368 | 442.1784 | 527.4105 | 566.5799 | 620.2013 | 748.9911 | 878.3061 | 994.5906 | 1094.6987 | 1179.0181 | 1256.4805 | 1327.0858
Zs-Bellerive | Lindisfarne | 27175 | 64.2531 | 67.5741 | 68.6393 | 70.4191 | 72.504 | 74.86 | 76.8564 | 79.1624 | 80.2058 | 81.2306 | 81.9918 | 82.6387 | 146.7896 | 147.7361 | 147.7062 | 149.5869 | 152.268 | 155.4559 | 158.2339 | 160.3367 | 161.3376 | 162.1915 | 162.7536 | 164.2939 | 85.5475 | 89.1797 | 109.1934 | 117.3336 | 130.3062 | 161.6245 | 193.2332 | 221.8002 | 246.5119 | 267.4211 | 286.7129 | 304.3693
Zs-Bellerive | Lindisfarne | 27176 | 47.4757 | 49.9296 | 50.7166 | 52.0317 | 53.5722 | 55.313 | 56.7881 | 58.492 | 59.2629 | 60.0202 | 60.5826 | 61.0606 | 70.5883 | 71.0435 | 71.0291 | 71.9334 | 73.2228 | 74.7558 | 76.0916 | 77.1028 | 77.5841 | 77.9948 | 78.2651 | 79.0058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Bellerive | Lindisfarne | 27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.0428 | 247.7069 | 322.1735 | 346.3725 | 381.2009 | 464.8131 | 548.7279 | 624.1543 | 689.0623 | 743.7146 | 793.9095 | 839.655
Zs-Bellerive | Lindisfarne | 27178 | 50.0802 | 52.6687 | 53.499 | 54.8862 | 56.5112 | 58.3475 | 59.9035 | 61.7009 | 62.5141 | 63.3129 | 63.9061 | 64.4104 | 114.3102 | 115.0473 | 115.024 | 116.4886 | 118.5765 | 121.059 | 123.2223 | 124.8598 | 125.6392 | 126.3042 | 126.7419 | 127.9414 | 139.6121 | 152.361 | 176.7503 | 197.9691 | 216.3228 | 260.4844 | 305.0214 | 345.358 | 380.4316 | 410.3562 | 438.2907 | 464.244
Zs-Cambridge | Mornington | 29481 | 33.0609 | 34.7698 | 35.3179 | 36.2336 | 37.3064 | 38.5186 | 39.5459 | 40.7324 | 41.2693 | 41.7966 | 42.1882 | 42.5211 | 66.5488 | 66.9779 | 66.9644 | 67.817 | 69.0325 | 70.4778 | 71.7372 | 72.6905 | 73.1443 | 73.5314 | 73.7863 | 74.4846 | 5 | 5 | 5 | 16.0003 | 33.0534 | 73.268 | 113.3433 | 149.7796 | 182.3106 | 211.554 | 241.0153 | 271.0536
Zs-Cambridge | Mornington | 29482 | 16.8529 | 17.724 | 18.0034 | 18.4702 | 19.0171 | 19.635 | 20.1587 | 20.7635 | 21.0372 | 21.306 | 21.5056 | 21.6753 | 43.6026 | 43.8838 | 43.8749 | 44.4335 | 45.2299 | 46.1769 | 47.002 | 47.6267 | 47.924 | 48.1776 | 48.3446 | 48.8021 | 734.4957 | 898.9152 | 1021.0324 | 1114.2155 | 1160.5237 | 1269.7349 | 1377.5728 | 1473.0915 | 1553.5189 | 1620.2277 | 1680.9202 | 1735.8307
Zs-Cambridge | Mornington | 29483 | 72.8599 | 76.6258 | 77.8337 | 79.8519 | 82.2161 | 84.8876 | 87.1515 | 89.7664 | 90.9496 | 92.1116 | 92.9747 | 93.7084 | 144.5389 | 145.4709 | 145.4415 | 147.2933 | 149.9333 | 153.0723 | 155.8077 | 157.8783 | 158.8638 | 159.7046 | 160.2581 | 161.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Mornington | 29485 | 81.713 | 85.9364 | 87.2911 | 89.5545 | 92.206 | 95.2021 | 97.741 | 100.6737 | 102.0006 | 103.3039 | 104.2719 | 105.0946 | 95.3524 | 95.9672 | 95.9478 | 97.1695 | 98.9111 | 100.9819 | 102.7864 | 104.1524 | 104.8026 | 105.3572 | 105.7224 | 106.7229 | 0 | 0 | 0 | 8.6718 | 22.1548 | 53.5819 | 83.9052 | 109.9263 | 131.2639 | 148.4711 | 163.8082 | 177.6391
Zs-Cambridge | Mornington | 29486 | 36.6084 | 38.5006 | 39.1075 | 40.1216 | 41.3094 | 42.6517 | 43.7892 | 45.1031 | 45.6976 | 46.2814 | 46.7151 | 47.0837 | 46.6245 | 46.9251 | 46.9157 | 47.513 | 48.3646 | 49.3772 | 50.2595 | 50.9274 | 51.2454 | 51.5166 | 51.6951 | 52.1844 | 28.5242 | 32.0026 | 32.0026 | 39.4264 | 50.7539 | 76.934 | 102.2696 | 124.2725 | 142.5871 | 157.4995 | 170.7365 | 182.3891
Zs-Cambridge | Lindisfarne | 29488 | 164.1279 | 172.6112 | 175.3321 | 179.8784 | 185.2041 | 191.2221 | 196.3217 | 202.2122 | 204.8775 | 207.4953 | 209.4395 | 211.0921 | 228.5126 | 229.9861 | 229.9396 | 232.8673 | 237.0411 | 242.0039 | 246.3284 | 249.6019 | 251.16 | 252.4893 | 253.3643 | 255.7623 | 26.53 | 26.53 | 33.93 | 39.2281 | 47.6352 | 67.9365 | 88.5495 | 107.4331 | 124.1603 | 138.8552 | 153.1901 | 167.347
Zs-Cambridge | Lindisfarne | 29489 | 61.6714 | 64.859 | 65.8814 | 67.5896 | 69.5908 | 71.8521 | 73.7682 | 75.9816 | 76.9831 | 77.9667 | 78.6973 | 79.3183 | 114.4607 | 115.1988 | 115.1755 | 116.642 | 118.7326 | 121.2184 | 123.3845 | 125.0242 | 125.8047 | 126.4705 | 126.9088 | 128.1099 | 313.7326 | 360.7028 | 427.4939 | 452.0797 | 468.0474 | 504.96 | 540.0085 | 570.525 | 596.2242 | 617.4544 | 636.6387 | 653.8956
Zs-Cambridge | Lindisfarne | 29490 | 35.6531 | 37.4959 | 38.087 | 39.0746 | 40.2314 | 41.5387 | 42.6465 | 43.9261 | 44.5051 | 45.0737 | 45.4961 | 45.855 | 66.6859 | 67.1159 | 67.1023 | 67.9567 | 69.1747 | 70.623 | 71.885 | 72.8403 | 73.295 | 73.6829 | 73.9383 | 74.638 | 0 | 0 | 0 | 4.2705 | 11.3112 | 28.7383 | 46.5322 | 62.5493 | 76.1373 | 87.2664 | 97.1214 | 105.7424
Zs-Cambridge | Lindisfarne | 29491 | 59.6291 | 62.7111 | 63.6997 | 65.3514 | 67.2862 | 69.4726 | 71.3254 | 73.4654 | 74.4338 | 75.3848 | 76.0912 | 76.6916 | 86.7783 | 87.3378 | 87.3202 | 88.432 | 90.017 | 91.9016 | 93.5439 | 94.787 | 95.3787 | 95.8835 | 96.2158 | 97.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Lindisfarne | 29492 | 1.9953 | 2.0984 | 2.1315 | 2.1868 | 2.2515 | 2.3247 | 2.3867 | 2.4583 | 2.4907 | 2.5225 | 2.5462 | 2.5662 | 2.2829 | 2.2977 | 2.2972 | 2.3265 | 2.3682 | 2.4177 | 2.4609 | 2.4936 | 2.5092 | 2.5225 | 2.5312 | 2.5552 | 211.3684 | 246.8316 | 285.4581 | 329.8824 | 392.1891 | 553.5592 | 728.8151 | 899.3123 | 1057.7398 | 1201.1545 | 1341.9564 | 1478.211
Zs-Claremont | Creek Road | 21081 | 84.7757 | 89.1574 | 90.5629 | 92.9111 | 95.662 | 98.7704 | 101.4045 | 104.447 | 105.8237 | 107.1759 | 108.1801 | 109.0337 | 153.0747 | 154.0618 | 154.0306 | 155.9918 | 158.7877 | 162.1121 | 165.009 | 167.2019 | 168.2456 | 169.1361 | 169.7222 | 171.3285 | 160.7694 | 180.745 | 213.7437 | 221.922 | 234.9542 | 266.4104 | 298.1477 | 326.817 | 351.6008 | 372.5533 | 391.8645 | 409.5162
Zs-Claremont | Creek Road | 21082 | 18.8166 | 19.7892 | 20.1011 | 20.6224 | 21.2329 | 21.9229 | 22.5075 | 23.1828 | 23.4884 | 23.7885 | 24.0114 | 24.2009 | 42.3993 | 42.6727 | 42.6641 | 43.2073 | 43.9818 | 44.9026 | 45.705 | 46.3123 | 46.6015 | 46.8481 | 47.0104 | 47.4554 | 127.3621 | 149.0161 | 162.5459 | 174.3741 | 190.0995 | 228.054 | 266.3433 | 300.9258 | 330.8147 | 356.0761 | 379.3504 | 400.6156
Zs-Claremont | Creek Road | 21083 | 134.8321 | 141.8012 | 144.0365 | 147.7713 | 152.1463 | 157.0902 | 161.2796 | 166.1186 | 168.3082 | 170.4587 | 172.0559 | 173.4135 | 165.1078 | 166.1724 | 166.1388 | 168.2542 | 171.2699 | 174.8556 | 177.9802 | 180.3455 | 181.4713 | 182.4317 | 183.064 | 184.7965 | 38.5164 | 38.5164 | 38.5164 | 41.9375 | 47.389 | 60.5465 | 73.8202 | 85.8088 | 96.1703 | 104.9276 | 112.996 | 120.3679
Zs-Claremont | Creek Road | 21084 | 118.8152 | 124.9564 | 126.9262 | 130.2173 | 134.0726 | 138.4292 | 142.1209 | 146.3851 | 148.3146 | 150.2096 | 151.6171 | 152.8135 | 137.2986 | 138.184 | 138.156 | 139.9151 | 142.4229 | 145.4047 | 148.003 | 149.9698 | 150.906 | 151.7047 | 152.2304 | 153.6712 | 848.0377 | 1046.5598 | 1184.9272 | 1298.6798 | 1380.5071 | 1577.0676 | 1774.4561 | 1951.9598 | 2104.7454 | 2233.3806 | 2351.473 | 2459.0102
Zs-Claremont | Creek Road | 21085 | 111.5909 | 117.3587 | 119.2087 | 122.2998 | 125.9207 | 130.0124 | 133.4796 | 137.4846 | 139.2967 | 141.0765 | 142.3984 | 143.522 | 237.9602 | 239.4946 | 239.4462 | 242.4949 | 246.8413 | 252.0092 | 256.5125 | 259.9214 | 261.5439 | 262.9282 | 263.8394 | 266.3364 | 259.8792 | 314.0637 | 333.6511 | 360.9251 | 397.8921 | 488.2437 | 580.7375 | 665.6187 | 740.1823 | 804.1942 | 864.0182 | 919.3626
Zs-Claremont | Creek Road | 21086 | 51.354 | 54.0083 | 54.8597 | 56.2822 | 57.9485 | 59.8315 | 61.4271 | 63.2702 | 64.1041 | 64.9232 | 65.5315 | 66.0486 | 127.8221 | 128.6464 | 128.6204 | 130.258 | 132.5927 | 135.3687 | 137.7877 | 139.6188 | 140.4903 | 141.2339 | 141.7233 | 143.0647 | 262.1134 | 282.653 | 349.2671 | 392.1228 | 424.1949 | 501.4619 | 579.2727 | 649.4312 | 709.9702 | 761.0581 | 808.0593 | 850.9439
Zs-Claremont | Creek Road | 21087 | 41.4777 | 43.6215 | 44.3092 | 45.4581 | 46.8039 | 48.3248 | 49.6135 | 51.1022 | 51.7757 | 52.4373 | 52.9286 | 53.3463 | 90.7821 | 91.3675 | 91.349 | 92.5121 | 94.1703 | 96.1419 | 97.8599 | 99.1604 | 99.7794 | 100.3075 | 100.6551 | 101.6077 | 132.6122 | 150.6776 | 180.8977 | 196.1885 | 220.5542 | 279.3651 | 338.6989 | 392.2936 | 438.6208 | 477.7819 | 513.8703 | 546.8519
Zs-Claremont | Creek Road | 21088 | 26.839 | 28.2263 | 28.6712 | 29.4147 | 30.2855 | 31.2696 | 32.1036 | 33.0668 | 33.5026 | 33.9307 | 34.2486 | 34.5189 | 53.4258 | 53.7703 | 53.7594 | 54.4439 | 55.4197 | 56.58 | 57.5911 | 58.3564 | 58.7207 | 59.0315 | 59.2361 | 59.7967 | 323.0615 | 358.7665 | 413.057 | 448.8673 | 492.2481 | 596.9127 | 703.0038 | 799.9111 | 885.2366 | 959.1955 | 1029.3838 | 1093.2519
Zs-Claremont | Creek Road | 21089 | 73.3642 | 77.1562 | 78.3724 | 80.4046 | 82.7851 | 85.4751 | 87.7546 | 90.3877 | 91.579 | 92.7491 | 93.6182 | 94.3569 | 149.0692 | 150.0305 | 150.0001 | 151.91 | 154.6328 | 157.8702 | 160.6913 | 162.8267 | 163.8432 | 164.7103 | 165.2811 | 166.8454 | 0 | 0 | 0 | 2.0655 | 5.2291 | 12.5604 | 19.6734 | 25.8812 | 30.6795 | 34.5136 | 38.0231 | 41.2513
Zs-Derwent Park | Risdon | 17100 | 72.5229 | 76.2714 | 77.4737 | 79.4826 | 81.8358 | 84.495 | 86.7484 | 89.3512 | 90.5289 | 91.6856 | 92.5447 | 93.275 | 120.8939 | 121.6734 | 121.6488 | 123.1977 | 125.4058 | 128.0313 | 130.3192 | 132.0511 | 132.8754 | 133.5786 | 134.0416 | 135.3102 | 193.4983 | 196.9566 | 200.5072 | 217.3664 | 232.4316 | 269.1977 | 307.0857 | 342.2751 | 373.5996 | 400.7787 | 426.3255 | 449.7632
Zs-Derwent Park | Risdon | 17101 | 57.1429 | 60.0964 | 61.0438 | 62.6266 | 64.4808 | 66.576 | 68.3515 | 70.4024 | 71.3303 | 72.2417 | 72.9186 | 73.494 | 121.1395 | 121.9206 | 121.896 | 123.448 | 125.6606 | 128.2915 | 130.584 | 132.3194 | 133.1454 | 133.8501 | 134.3139 | 135.5851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Derwent Park | Risdon | 17102 | 8.5218 | 8.9622 | 9.1035 | 9.3396 | 9.6161 | 9.9285 | 10.1933 | 10.4992 | 10.6375 | 10.7735 | 10.8744 | 10.9602 | 11.8575 | 11.934 | 11.9316 | 12.0835 | 12.3001 | 12.5576 | 12.782 | 12.9519 | 13.0327 | 13.1017 | 13.1471 | 13.2715 | 97.5618 | 122.1237 | 142.0101 | 162.0821 | 194.5287 | 273.9693 | 355.1226 | 429.1022 | 493.3688 | 547.7316 | 597.6844 | 643.0863
Zs-Derwent Park | Risdon | 17103 | 80.4696 | 84.6288 | 85.9629 | 88.1919 | 90.803 | 93.7535 | 96.2538 | 99.1418 | 100.4486 | 101.732 | 102.6853 | 103.4955 | 153.0634 | 154.0503 | 154.0192 | 155.9802 | 158.776 | 162.1001 | 164.9968 | 167.1895 | 168.2331 | 169.1235 | 169.7096 | 171.3158 | 3 | 3 | 3 | 11.4995 | 24.3347 | 54.0306 | 83.4201 | 110.3781 | 135.0433 | 158.0205 | 182.1017 | 207.5627
Zs-Derwent Park | Risdon | 17104 | 67.5468 | 71.038 | 72.1579 | 74.0289 | 76.2207 | 78.6974 | 80.7961 | 83.2203 | 84.3173 | 85.3946 | 86.1948 | 86.8749 | 105.8985 | 106.5814 | 106.5598 | 107.9166 | 109.8508 | 112.1507 | 114.1548 | 115.6718 | 116.3939 | 117.0099 | 117.4154 | 118.5267 | 199.8402 | 232.7474 | 253.1613 | 301.4471 | 351.0692 | 475.2338 | 605.503 | 728.1674 | 838.8845 | 936.6784 | 1030.7956 | 1120.4368
Zs-Derwent Park | Risdon | 17105 | 112.5272 | 118.3434 | 120.209 | 123.3259 | 126.9772 | 131.1032 | 134.5996 | 138.6381 | 140.4655 | 142.2602 | 143.5932 | 144.7263 | 212.3821 | 213.7515 | 213.7083 | 216.4293 | 220.3085 | 224.921 | 228.9402 | 231.9826 | 233.4308 | 234.6662 | 235.4795 | 237.7081 | 128.7419 | 162.1599 | 189.7473 | 206.3381 | 230.7317 | 288.2566 | 344.9657 | 395.0708 | 437.5123 | 472.75 | 504.7287 | 533.5854
Zs-Derwent Park | Risdon | 17106 | 120.6315 | 126.8665 | 128.8664 | 132.2079 | 136.1221 | 140.5453 | 144.2934 | 148.6229 | 150.5818 | 152.5058 | 153.9348 | 155.1495 | 175.8207 | 176.9544 | 176.9187 | 179.1712 | 182.3827 | 186.201 | 189.5284 | 192.0471 | 193.2459 | 194.2687 | 194.9419 | 196.7869 | 5 | 5 | 5 | 12.5357 | 24.271 | 52.1822 | 80.2699 | 105.9419 | 128.709 | 148.6743 | 167.9128 | 186.3889
Zs-Derwent Park | Risdon | 17107 | 72.5039 | 76.2514 | 77.4534 | 79.4618 | 81.8144 | 84.4729 | 86.7256 | 89.3278 | 90.5052 | 91.6616 | 92.5205 | 93.2505 | 108.6762 | 109.377 | 109.3549 | 110.7472 | 112.7322 | 115.0924 | 117.149 | 118.7058 | 119.4469 | 120.0791 | 120.4952 | 121.6356 | 0 | 0 | 0 | 1.6164 | 4.1171 | 10.0641 | 16.1319 | 21.882 | 27.3233 | 32.5676 | 38.2561 | 44.484
Zs-Derwent Park | Risdon | 17108 | 26.9151 | 28.3063 | 28.7525 | 29.498 | 30.3713 | 31.3582 | 32.1945 | 33.1605 | 33.5976 | 34.0268 | 34.3457 | 34.6167 | 28.935 | 29.1216 | 29.1157 | 29.4864 | 30.0149 | 30.6433 | 31.1909 | 31.6054 | 31.8027 | 31.971 | 32.0818 | 32.3854 | 0 | 0 | 0 | 5.2284 | 13.7946 | 35.1306 | 57.5413 | 78.9691 | 99.0618 | 118.0408 | 138.1751 | 159.8581
Zs-Derwent Park | Risdon | 17109 | 40.722 | 42.8268 | 43.5019 | 44.6299 | 45.9512 | 47.4444 | 48.7096 | 50.1711 | 50.8324 | 51.4819 | 51.9643 | 52.3743 | 61.7223 | 62.1203 | 62.1077 | 62.8985 | 64.0258 | 65.3663 | 66.5344 | 67.4186 | 67.8394 | 68.1985 | 68.4348 | 69.0825 | 0 | 0 | 0 | 6.4755 | 19.7044 | 60.256 | 111.46 | 168.2948 | 227.4214 | 286.2548 | 348.6596 | 412.8733
Zs-East Hobart | Risdon | 14060 | 66.33 | 69.7584 | 70.8581 | 72.6954 | 74.8477 | 77.2798 | 79.3407 | 81.7213 | 82.7984 | 83.8564 | 84.6421 | 85.31 | 95.9165 | 96.535 | 96.5155 | 97.7443 | 99.4963 | 101.5794 | 103.3945 | 104.7686 | 105.4226 | 105.9805 | 106.3478 | 107.3543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14061 | 48.393 | 50.8943 | 51.6966 | 53.037 | 54.6073 | 56.3817 | 57.8853 | 59.6221 | 60.408 | 61.1798 | 61.7531 | 62.2404 | 65.9379 | 66.3631 | 66.3496 | 67.1944 | 68.3988 | 69.8308 | 71.0787 | 72.0232 | 72.4728 | 72.8564 | 73.1089 | 73.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14062 | 23.9969 | 25.2372 | 25.635 | 26.2997 | 27.0784 | 27.9583 | 28.7039 | 29.5651 | 29.9548 | 30.3376 | 30.6218 | 30.8634 | 30.3201 | 30.5156 | 30.5094 | 30.8979 | 31.4517 | 32.1102 | 32.684 | 33.1183 | 33.325 | 33.5014 | 33.6175 | 33.9357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14063 | 68.5116 | 72.0527 | 73.1885 | 75.0863 | 77.3094 | 79.8215 | 81.9502 | 84.409 | 85.5216 | 86.6143 | 87.4259 | 88.1158 | 130.9837 | 131.8283 | 131.8017 | 133.4798 | 135.8722 | 138.7169 | 141.1957 | 143.0721 | 143.9652 | 144.7272 | 145.2287 | 146.6032 | 0 | 0 | 0 | 1.2678 | 4.0578 | 13.3494 | 26.1799 | 41.8267 | 59.7578 | 79.4244 | 102.3914 | 128.3175
Zs-East Hobart | Risdon | 14064 | 73.1056 | 76.8842 | 78.0962 | 80.1212 | 82.4934 | 85.1739 | 87.4454 | 90.0691 | 91.2563 | 92.4223 | 93.2883 | 94.0244 | 95.2264 | 95.8404 | 95.821 | 97.041 | 98.7804 | 100.8485 | 102.6506 | 104.0147 | 104.664 | 105.218 | 105.5826 | 106.5819 | 0 | 0 | 0 | 8.3579 | 26.0904 | 82.5839 | 156.7258 | 242.3086 | 335.1281 | 431.9671 | 540.7594 | 660.9575
Zs-East Hobart | Risdon | 14065 | 148.216 | 155.8768 | 158.334 | 162.4395 | 167.2489 | 172.6835 | 177.2887 | 182.6081 | 185.015 | 187.379 | 189.1348 | 190.6271 | 195.8161 | 197.0787 | 197.0389 | 199.5476 | 203.1243 | 207.3769 | 211.0827 | 213.8878 | 215.223 | 216.3621 | 217.1119 | 219.1667 | 0 | 0 | 0 | 1.1038 | 3.0328 | 8.2582 | 14.2716 | 20.5072 | 26.6687 | 32.5448 | 38.5427 | 44.4868
Zs-East Hobart | Risdon | 14066 | 72.6323 | 76.3864 | 77.5905 | 79.6024 | 81.9592 | 84.6224 | 86.8791 | 89.4859 | 90.6654 | 91.8238 | 92.6842 | 93.4156 | 122.7172 | 123.5086 | 123.4836 | 125.0558 | 127.2973 | 129.9624 | 132.2848 | 134.0427 | 134.8795 | 135.5933 | 136.0633 | 137.351 | 0 | 0 | 0 | 3.5251 | 10.8645 | 34.5078 | 66.5597 | 105.1907 | 148.944 | 196.1585 | 250.0348 | 309.0859
Zs-East Hobart | Risdon | 14067 | 34.8903 | 36.6937 | 37.2721 | 38.2385 | 39.3707 | 40.65 | 41.7341 | 42.9862 | 43.5528 | 44.1093 | 44.5226 | 44.8739 | 72.6355 | 73.1039 | 73.0891 | 74.0197 | 75.3464 | 76.9239 | 78.2985 | 79.339 | 79.8343 | 80.2568 | 80.5349 | 81.2971 | 0 | 0 | 0 | 5.6543 | 17.2821 | 53.2421 | 99.1665 | 150.8946 | 205.7468 | 261.6863 | 322.8917 | 388.3049
Zs-East Hobart | Risdon | 14068 | 96.5056 | 101.4936 | 103.0935 | 105.7667 | 108.8981 | 112.4367 | 115.4352 | 118.8988 | 120.4659 | 122.0051 | 123.1484 | 124.1201 | 163.6139 | 164.6689 | 164.6356 | 166.7318 | 169.7202 | 173.2735 | 176.3699 | 178.7137 | 179.8293 | 180.7811 | 181.4076 | 183.1245 | 0 | 0 | 0 | 3.613 | 10.6858 | 31.5333 | 57.035 | 84.8183 | 113.7395 | 143.2471 | 176.2306 | 212.97
Zs-East Hobart | Risdon | 14069 | 128.7771 | 135.4331 | 137.5681 | 141.1351 | 145.3137 | 150.0356 | 154.0368 | 158.6586 | 160.7498 | 162.8037 | 164.3292 | 165.6259 | 144.7347 | 145.668 | 145.6385 | 147.4928 | 150.1365 | 153.2798 | 156.0188 | 158.0922 | 159.0791 | 159.921 | 160.4752 | 161.994 | 0 | 0 | 0 | 7.889 | 22.1492 | 62.0563 | 109.5446 | 160.7257 | 213.8197 | 267.7046 | 327.0784 | 391.3723
Zs-East Hobart | Risdon | 14070 | 120.8874 | 127.1357 | 129.1398 | 132.4884 | 136.411 | 140.8435 | 144.5996 | 148.9382 | 150.9013 | 152.8294 | 154.2614 | 155.4786 | 178.0353 | 179.1833 | 179.1471 | 181.4281 | 184.6799 | 188.5464 | 191.9157 | 194.4661 | 195.68 | 196.7157 | 197.3974 | 199.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-East Hobart | Risdon | 14071 | 136.9709 | 144.0505 | 146.3212 | 150.1153 | 154.5598 | 159.582 | 163.8378 | 168.7537 | 170.978 | 173.1626 | 174.7852 | 176.1643 | 174.0813 | 175.2038 | 175.1684 | 177.3987 | 180.5783 | 184.3589 | 187.6534 | 190.1471 | 191.3341 | 192.3468 | 193.0134 | 194.8401 | 262.8721 | 283.5795 | 312.5971 | 359.2358 | 408.3922 | 527.6802 | 649.1498 | 760.2951 | 857.8753 | 941.7468 | 1020.2917 | 1090.7848
Zs-Geilston Bay | Lindisfarne | 26161 | 77.3565 | 81.3549 | 82.6373 | 84.7801 | 87.2901 | 90.1265 | 92.5301 | 95.3064 | 96.5626 | 97.7964 | 98.7128 | 99.4917 | 141.8981 | 142.8131 | 142.7843 | 144.6022 | 147.194 | 150.2757 | 152.9611 | 154.9938 | 155.9614 | 156.7868 | 157.3302 | 158.8192 | 302.6172 | 356.574 | 412.6309 | 460.9246 | 503.5071 | 604.8903 | 705.7745 | 795.6934 | 872.4566 | 936.6164 | 995.154 | 1048.1878
Zs-Geilston Bay | Lindisfarne | 26162 | 68.9441 | 72.5076 | 73.6506 | 75.5603 | 77.7974 | 80.3254 | 82.4675 | 84.9419 | 86.0615 | 87.1611 | 87.9778 | 88.672 | 162.8617 | 163.9119 | 163.8788 | 165.9653 | 168.94 | 172.477 | 175.5591 | 177.8921 | 179.0026 | 179.95 | 180.5736 | 182.2826 | 249.5069 | 306.0355 | 332.3841 | 378.2432 | 405.7896 | 471.8873 | 538.1979 | 597.7811 | 649.0396 | 692.1851 | 731.796 | 767.8768
Zs-Geilston Bay | Lindisfarne | 26163 | 37.1859 | 39.1079 | 39.7244 | 40.7544 | 41.961 | 43.3245 | 44.4799 | 45.8145 | 46.4184 | 47.0115 | 47.452 | 47.8264 | 93.3469 | 93.9488 | 93.9298 | 95.1257 | 96.8307 | 98.858 | 100.6246 | 101.9618 | 102.5983 | 103.1413 | 103.4987 | 104.4783 | 683.7563 | 788.4756 | 1010.7338 | 1093.3889 | 1157.5405 | 1312.8637 | 1470.6718 | 1614.7299 | 1740.8497 | 1848.8363 | 1949.428 | 2038.1479
Zs-Geilston Bay | Lindisfarne | 26164 | 87.076 | 91.5767 | 93.0203 | 95.4323 | 98.2577 | 101.4505 | 104.156 | 107.2812 | 108.6952 | 110.084 | 111.1155 | 111.9923 | 190.087 | 191.3127 | 191.274 | 193.7094 | 197.1814 | 201.3096 | 204.9069 | 207.63 | 208.9261 | 210.0318 | 210.7597 | 212.7544 | 167.3144 | 184.3136 | 208.9569 | 227.49 | 239.7493 | 268.9243 | 297.9644 | 323.8658 | 345.9944 | 364.5003 | 381.389 | 396.6889
Zs-Geilston Bay | Lindisfarne | 26165 | 57.9319 | 60.9262 | 61.8866 | 63.4913 | 65.3711 | 67.4952 | 69.2952 | 71.3744 | 72.3152 | 73.2391 | 73.9254 | 74.5087 | 129.0392 | 129.8712 | 129.845 | 131.4982 | 133.8551 | 136.6576 | 139.0996 | 140.9481 | 141.828 | 142.5786 | 143.0727 | 144.4268 | 155.2946 | 213.7492 | 310.2872 | 352.1612 | 376.1587 | 433.1704 | 489.8019 | 540.1923 | 583.1258 | 618.9212 | 651.4764 | 680.8565
Zs-Geilston Bay | Lindisfarne | 26166 | 37.2762 | 39.2029 | 39.8209 | 40.8534 | 42.0629 | 43.4297 | 44.588 | 45.9258 | 46.5311 | 47.1257 | 47.5672 | 47.9426 | 81.5109 | 82.0365 | 82.0199 | 83.0642 | 84.553 | 86.3232 | 87.8658 | 89.0335 | 89.5893 | 90.0634 | 90.3755 | 91.2309 | 312.9922 | 371.6944 | 384.5445 | 444.9198 | 486.8686 | 587.3263 | 687.9468 | 778.2541 | 855.89 | 921.2242 | 981.225 | 1035.9256
Zs-Geilston Bay | Lindisfarne | 26167 | 104.5473 | 109.951 | 111.6843 | 114.5802 | 117.9725 | 121.806 | 125.0543 | 128.8065 | 130.5043 | 132.1717 | 133.4102 | 134.4629 | 223.846 | 225.2894 | 225.2438 | 228.1117 | 232.2003 | 237.0617 | 241.2979 | 244.5046 | 246.0309 | 247.333 | 248.1902 | 250.5391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Geilston Bay | Lindisfarne | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292.0394 | 392.6701 | 466.4343 | 502.6159 | 529.9583 | 595.7192 | 661.5659 | 720.3669 | 770.4556 | 812.0922 | 849.7886 | 883.6352
Zs-Howrah | Mornington | 22323 | 46.1197 | 48.5035 | 49.2681 | 50.5456 | 52.0421 | 53.7332 | 55.1662 | 56.8214 | 57.5703 | 58.3059 | 58.8522 | 59.3166 | 97.293 | 97.9204 | 97.9006 | 99.1471 | 100.9242 | 103.0372 | 104.8784 | 106.2721 | 106.9356 | 107.5015 | 107.8741 | 108.895 | 102.2427 | 156.5537 | 168.6242 | 186.6092 | 215.3014 | 284.8247 | 355.4178 | 419.7051 | 475.7632 | 523.5422 | 567.8861 | 608.6468
Zs-Howrah | Mornington | 22324 | 70.6057 | 74.2551 | 75.4256 | 77.3813 | 79.6724 | 82.2612 | 84.455 | 86.989 | 88.1356 | 89.2617 | 90.0981 | 90.8091 | 161.4737 | 162.5149 | 162.482 | 164.5508 | 167.5002 | 171.007 | 174.0628 | 176.3759 | 177.477 | 178.4163 | 179.0346 | 180.729 | 483.4361 | 655.4993 | 752.816 | 822.8176 | 869.3647 | 981.7099 | 1095.0464 | 1197.4104 | 1285.8818 | 1360.6554 | 1429.5474 | 1492.4922
Zs-Howrah | Mornington | 22325 | 66.5173 | 69.9554 | 71.0581 | 72.9006 | 75.059 | 77.498 | 79.5647 | 81.952 | 83.0322 | 84.0931 | 84.8811 | 85.5508 | 144.4633 | 145.3948 | 145.3654 | 147.2163 | 149.8549 | 152.9923 | 155.7262 | 157.7957 | 158.7808 | 159.6211 | 160.1743 | 161.6902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Howrah | Mornington | 22326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.8623 | 441.0173 | 587.415 | 624.9288 | 673.1147 | 789.8751 | 908.0629 | 1015.2409 | 1108.5002 | 1188.2637 | 1263.1892 | 1333.5994
Zs-Howrah | Mornington | 22328 | 100.4917 | 105.6858 | 107.3518 | 110.1354 | 113.3962 | 117.0809 | 120.2033 | 123.8099 | 125.4418 | 127.0446 | 128.235 | 129.2469 | 182.6434 | 183.8211 | 183.7839 | 186.1239 | 189.46 | 193.4265 | 196.883 | 199.4994 | 200.7448 | 201.8072 | 202.5066 | 204.4232 | 574.644 | 718.7111 | 810.0778 | 880.8856 | 934.9104 | 1064.6092 | 1194.7798 | 1311.773 | 1412.4221 | 1497.1202 | 1574.8405 | 1645.583
Zs-Howrah | Mornington | 22329 | 62.8505 | 66.0991 | 67.141 | 68.882 | 70.9214 | 73.2259 | 75.1787 | 77.4344 | 78.455 | 79.4575 | 80.202 | 80.8348 | 179.1736 | 180.329 | 180.2925 | 182.588 | 185.8607 | 189.7519 | 193.1427 | 195.7094 | 196.9311 | 197.9734 | 198.6595 | 200.5397 | 45.4667 | 49.5587 | 54.5145 | 61.1267 | 65.5822 | 76.3359 | 87.1846 | 96.983 | 105.4515 | 112.6089 | 119.2033 | 125.2284
Zs-Howrah | Mornington | 22330 | 6.345 | 6.6729 | 6.7781 | 6.9539 | 7.1598 | 7.3924 | 7.5896 | 7.8173 | 7.9203 | 8.0215 | 8.0967 | 8.1606 | 13.168 | 13.253 | 13.2503 | 13.419 | 13.6595 | 13.9455 | 14.1947 | 14.3833 | 14.4731 | 14.5497 | 14.6001 | 14.7383 | 880.6274 | 1068.3141 | 1229.0017 | 1329.0829 | 1390.4975 | 1538.0907 | 1686.3777 | 1819.7927 | 1934.6848 | 2031.4604 | 2120.341 | 2201.3066
Zs-Howrah | Mornington | 22331 | 92.6881 | 97.4789 | 99.0155 | 101.5829 | 104.5905 | 107.9891 | 110.869 | 114.1955 | 115.7007 | 117.179 | 118.277 | 119.2103 | 205.127 | 206.4497 | 206.408 | 209.036 | 212.7827 | 217.2376 | 221.1195 | 224.058 | 225.4567 | 226.65 | 227.4354 | 229.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-New Town | Risdon | 16091 | 84.0009 | 88.3427 | 89.7353 | 92.0621 | 94.7878 | 97.8678 | 100.4778 | 103.4926 | 104.8567 | 106.1965 | 107.1915 | 108.0373 | 188.7947 | 190.012 | 189.9736 | 192.3924 | 195.8408 | 199.941 | 203.5138 | 206.2184 | 207.5057 | 208.6039 | 209.3269 | 211.308 | 263.276 | 297.6028 | 349.6252 | 401.6825 | 466.2134 | 621.3268 | 778.1337 | 921.0659 | 1046.5855 | 1154.9363 | 1257.194 | 1352.9366
Zs-New Town | Risdon | 16092 | 64.8662 | 68.2189 | 69.2943 | 71.0911 | 73.1959 | 75.5743 | 77.5897 | 79.9178 | 80.9711 | 82.0057 | 82.7741 | 83.4273 | 120.7435 | 121.522 | 121.4975 | 123.0444 | 125.2498 | 127.8721 | 130.1571 | 131.8868 | 132.7101 | 133.4125 | 133.8748 | 135.1419 | 200.7433 | 249.302 | 281.7691 | 342.7424 | 379.1378 | 465.2527 | 550.4139 | 625.8741 | 689.9539 | 743.2702 | 791.736 | 835.5216
Zs-New Town | Risdon | 16093 | 81.8669 | 86.0984 | 87.4556 | 89.7233 | 92.3797 | 95.3815 | 97.9252 | 100.8634 | 102.1928 | 103.4986 | 104.4684 | 105.2927 | 125.2901 | 126.098 | 126.0725 | 127.6777 | 129.9662 | 132.6872 | 135.0583 | 136.8531 | 137.7074 | 138.4362 | 138.916 | 140.2307 | 4.6 | 4.6 | 11.776 | 32.9314 | 69.8039 | 166.3925 | 270.8259 | 370.3586 | 459.6409 | 536.7245 | 608.3044 | 673.5094
Zs-New Town | Risdon | 16094 | 51.4918 | 54.1533 | 55.0069 | 56.4332 | 58.104 | 59.9921 | 61.592 | 63.44 | 64.2762 | 65.0975 | 65.7074 | 66.2259 | 113.4375 | 114.169 | 114.1459 | 115.5992 | 117.6712 | 120.1348 | 122.2815 | 123.9066 | 124.68 | 125.3399 | 125.7743 | 126.9647 | 261.8119 | 296.0549 | 361.2152 | 409.2214 | 453.1564 | 558.6151 | 664.4365 | 759.5228 | 841.3026 | 910.0993 | 973.2041 | 1030.618
Zs-New Town | Risdon | 16095 | 118.8057 | 124.9464 | 126.916 | 130.2069 | 134.0619 | 138.4181 | 142.1095 | 146.3734 | 148.3027 | 150.1976 | 151.605 | 152.8012 | 164.9405 | 166.0041 | 165.9705 | 168.0837 | 171.0964 | 174.6785 | 177.7999 | 180.1628 | 181.2874 | 182.2469 | 182.8785 | 184.6093 | 61.338 | 66.5598 | 79.2232 | 95.2792 | 123.5345 | 202.4049 | 296.3088 | 397.45 | 501.6324 | 605.5136 | 716.547 | 831.8707
Zs-New Town | Risdon | 16096 | 85.1987 | 89.6023 | 91.0148 | 93.3747 | 96.1393 | 99.2632 | 101.9104 | 104.9682 | 106.3517 | 107.7106 | 108.7199 | 109.5778 | 205.969 | 207.2972 | 207.2553 | 209.8941 | 213.6562 | 218.1293 | 222.0272 | 224.9778 | 226.3822 | 227.5803 | 228.369 | 230.5304 | 342.4872 | 426.5533 | 507.6712 | 567.8775 | 624.6751 | 762.5873 | 903.3392 | 1032.9779 | 1148.4352 | 1250.2285 | 1349.3097 | 1446.0083
Zs-New Town | Risdon | 16097 | 39.9187 | 41.982 | 42.6438 | 43.7496 | 45.0448 | 46.5085 | 47.7488 | 49.1815 | 49.8298 | 50.4664 | 50.9393 | 51.3413 | 52.1529 | 52.4892 | 52.4786 | 53.1468 | 54.0994 | 55.232 | 56.219 | 56.9661 | 57.3217 | 57.6251 | 57.8248 | 58.3721 | 54.1133 | 61.5407 | 67.3642 | 76.9215 | 91.7705 | 126.6453 | 160.854 | 190.9104 | 216.221 | 237.1135 | 255.9681 | 272.8925
Zs-New Town | Risdon | 16098 | 78.7634 | 82.8344 | 84.1402 | 86.3219 | 88.8776 | 91.7656 | 94.2129 | 97.0397 | 98.3187 | 99.5749 | 100.508 | 101.301 | 200.8805 | 202.1759 | 202.135 | 204.7086 | 208.3778 | 212.7404 | 216.542 | 219.4197 | 220.7894 | 221.9579 | 222.7271 | 224.8351 | 416.2477 | 524.4815 | 567.857 | 611.1558 | 670.9983 | 819.5162 | 974.5635 | 1120.2138 | 1251.5274 | 1367.3468 | 1478.4971 | 1583.8921
Zs-Rosny Park | Mornington | 23340 | 74.4455 | 78.2933 | 79.5275 | 81.5896 | 84.0052 | 86.7349 | 89.048 | 91.7198 | 92.9287 | 94.1161 | 94.998 | 95.7476 | 73.3294 | 73.8023 | 73.7874 | 74.7268 | 76.0662 | 77.6588 | 79.0465 | 80.097 | 80.597 | 81.0235 | 81.3043 | 82.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Mornington | 23341 | 53.7389 | 56.5165 | 57.4074 | 58.896 | 60.6397 | 62.6102 | 64.2799 | 66.2085 | 67.0812 | 67.9383 | 68.5749 | 69.116 | 111.8376 | 112.5588 | 112.536 | 113.9689 | 116.0116 | 118.4405 | 120.5569 | 122.159 | 122.9216 | 123.5722 | 124.0004 | 125.174 | 287.312 | 469.842 | 494.7493 | 532.3506 | 568.4817 | 654.7139 | 740.7461 | 817.606 | 883.3264 | 938.2908 | 988.4197 | 1033.7764
Zs-Rosny Park | Mornington | 23342 | 79.7849 | 83.9087 | 85.2314 | 87.4415 | 90.0303 | 92.9558 | 95.4348 | 98.2982 | 99.5939 | 100.8664 | 101.8115 | 102.6149 | 190.9463 | 192.1776 | 192.1387 | 194.5851 | 198.0728 | 202.2197 | 205.8333 | 208.5686 | 209.8706 | 210.9814 | 211.7126 | 213.7163 | 403.3243 | 516.201 | 640.8588 | 710.1046 | 751.3135 | 850.7794 | 951.1321 | 1041.7811 | 1120.1414 | 1186.3845 | 1247.4344 | 1303.2335
Zs-Rosny Park | Mornington | 23343 | 110.2007 | 115.8967 | 117.7236 | 120.7762 | 124.352 | 128.3927 | 131.8167 | 135.7718 | 137.5614 | 139.319 | 140.6245 | 141.7341 | 176.8009 | 177.941 | 177.905 | 180.1701 | 183.3995 | 187.2392 | 190.585 | 193.1178 | 194.3233 | 195.3518 | 196.0288 | 197.8841 | 150.8688 | 167.1103 | 195.0728 | 226.8008 | 260.6104 | 342.2124 | 424.5346 | 498.8868 | 563.1481 | 617.46 | 667.4998 | 713.2198
Zs-Rosny Park | Mornington | 23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Mornington | 23347 | 58.4119 | 61.431 | 62.3994 | 64.0174 | 65.9128 | 68.0545 | 69.8694 | 71.9658 | 72.9144 | 73.846 | 74.538 | 75.1261 | 121.247 | 122.0288 | 122.0041 | 123.5575 | 125.7721 | 128.4053 | 130.6999 | 132.4368 | 133.2635 | 133.9688 | 134.4331 | 135.7054 | 392.7866 | 480.3851 | 577.7174 | 623.8692 | 652.4556 | 722.048 | 792.8371 | 857.2424 | 913.2408 | 960.7819 | 1004.7162 | 1044.9274
Zs-Rosny Park | Mornington | 23348 | 64.4551 | 67.7866 | 68.8551 | 70.6405 | 72.732 | 75.0953 | 77.098 | 79.4113 | 80.458 | 81.486 | 82.2495 | 82.8985 | 141.8518 | 142.7665 | 142.7376 | 144.555 | 147.146 | 150.2266 | 152.9111 | 154.9432 | 155.9104 | 156.7356 | 157.2788 | 158.7673 | 418.4606 | 472.1844 | 532.6808 | 588.2025 | 629.0391 | 727.2215 | 825.9433 | 914.8948 | 991.7049 | 1056.7198 | 1116.9437 | 1172.6108
Zs-Sandy Bay | Creek Road | 12017 | 64.4336 | 67.764 | 68.8322 | 70.617 | 72.7078 | 75.0703 | 77.0724 | 79.3849 | 80.4312 | 81.4589 | 82.2222 | 82.871 | 145.5777 | 146.5165 | 146.4868 | 148.3519 | 151.011 | 154.1726 | 156.9276 | 159.013 | 160.0057 | 160.8525 | 161.4099 | 162.9376 | 658.6955 | 749.3254 | 884.4896 | 953.9563 | 1007.2855 | 1137.9241 | 1272.3069 | 1396.5565 | 1506.8086 | 1602.6637 | 1693.659 | 1779.5215
Zs-Sandy Bay | Creek Road | 12018 | 52.1292 | 54.8236 | 55.6878 | 57.1317 | 58.8232 | 60.7346 | 62.3543 | 64.2252 | 65.0718 | 65.9032 | 66.5207 | 67.0456 | 137.2119 | 138.0967 | 138.0688 | 139.8267 | 142.3329 | 145.3128 | 147.9095 | 149.8751 | 150.8107 | 151.6089 | 152.1343 | 153.5741 | 617.042 | 731.4658 | 799.7585 | 853.2282 | 900.5093 | 1014.6256 | 1129.749 | 1233.7268 | 1323.593 | 1399.5455 | 1469.5236 | 1533.4608
Zs-Sandy Bay | Creek Road | 12019 | 80.4429 | 84.6008 | 85.9344 | 88.1626 | 90.7729 | 93.7224 | 96.2219 | 99.1089 | 100.4153 | 101.6983 | 102.6512 | 103.4612 | 188.0644 | 189.2771 | 189.2388 | 191.6483 | 195.0833 | 199.1676 | 202.7267 | 205.4208 | 206.7031 | 207.7971 | 208.5172 | 210.4907 | 247.1879 | 277.8928 | 322.9747 | 401.4028 | 459.5006 | 607.7568 | 766.3211 | 918.0887 | 1056.6367 | 1179.6497 | 1297.9289 | 1409.9312
Zs-Sandy Bay | Creek Road | 12030 | 53.968 | 56.7575 | 57.6522 | 59.1471 | 60.8982 | 62.8771 | 64.5539 | 66.4908 | 67.3672 | 68.2279 | 68.8673 | 69.4107 | 168.3557 | 169.4413 | 169.407 | 171.5639 | 174.639 | 178.2953 | 181.4813 | 183.8931 | 185.041 | 186.0204 | 186.665 | 188.4317 | 585.0962 | 722.3401 | 826.5732 | 881.6612 | 929.4422 | 1046.6964 | 1168.1474 | 1282.0144 | 1385.3256 | 1477.9642 | 1569.3788 | 1659.5627
Zs-Sandy Bay | Creek Road | 12031 | 83.7367 | 88.0648 | 89.453 | 91.7725 | 94.4896 | 97.5599 | 100.1617 | 103.167 | 104.5268 | 105.8624 | 106.8543 | 107.6975 | 201.2524 | 202.5501 | 202.5091 | 205.0875 | 208.7635 | 213.1342 | 216.9428 | 219.8258 | 221.1981 | 222.3688 | 223.1394 | 225.2513 | 225.3937 | 256.4387 | 303.0667 | 325.4465 | 342.1567 | 381.9271 | 421.5068 | 456.7938 | 486.9205 | 512.0918 | 535.0359 | 555.7913
Zs-Sandy Bay | Creek Road | 12032 | 48.8274 | 51.3511 | 52.1606 | 53.5131 | 55.0975 | 56.8878 | 58.4049 | 60.1573 | 60.9502 | 61.729 | 62.3074 | 62.7991 | 107.9795 | 108.6758 | 108.6538 | 110.0372 | 112.0095 | 114.3546 | 116.398 | 117.9449 | 118.6811 | 119.3093 | 119.7227 | 120.8558 | 362.6905 | 467.7855 | 559.9177 | 607.5644 | 639.0806 | 714.8755 | 791.2108 | 860.2406 | 920.2281 | 971.5024 | 1019.6371 | 1064.8435
Zs-Sandy Bay | Creek Road | 12033 | 21.0376 | 22.1249 | 22.4737 | 23.0565 | 23.7391 | 24.5105 | 25.1641 | 25.9192 | 26.2608 | 26.5963 | 26.8455 | 27.0574 | 57.5051 | 57.8759 | 57.8642 | 58.601 | 59.6513 | 60.9002 | 61.9885 | 62.8122 | 63.2044 | 63.5389 | 63.7591 | 64.3625 | 384.9888 | 427.8192 | 478.7081 | 510.1204 | 526.3085 | 565.3028 | 604.5659 | 639.9627 | 670.5024 | 696.271 | 719.9756 | 741.6015
Zs-Sandy Bay | Creek Road | 12034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Sandy Bay | Creek Road | 12035 | 58.7712 | 61.8089 | 62.7832 | 64.4112 | 66.3182 | 68.4731 | 70.2992 | 72.4085 | 73.3629 | 74.3003 | 74.9965 | 75.5882 | 157.2855 | 158.2997 | 158.2677 | 160.2828 | 163.1557 | 166.5715 | 169.5481 | 171.8012 | 172.8737 | 173.7887 | 174.3909 | 176.0414 | 403.6917 | 510.5496 | 581.994 | 640.1492 | 687.8948 | 803.1384 | 919.4094 | 1024.4377 | 1115.2281 | 1191.9793 | 1262.7138 | 1327.3646
Zs-Sandy Bay | Creek Road | 12036 | 108.5881 | 114.2007 | 116.0009 | 119.0088 | 122.5323 | 126.5138 | 129.8878 | 133.785 | 135.5483 | 137.2803 | 138.5666 | 139.66 | 195.062 | 196.3199 | 196.2802 | 198.7792 | 202.3421 | 206.5784 | 210.2699 | 213.0642 | 214.3942 | 215.5289 | 216.2759 | 218.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Sandy Bay | Creek Road | 12037 | 92.3744 | 97.149 | 98.6804 | 101.2391 | 104.2365 | 107.6236 | 110.4938 | 113.809 | 115.3091 | 116.7825 | 117.8767 | 118.8068 | 166.2192 | 167.291 | 167.2572 | 169.3868 | 172.4228 | 176.0327 | 179.1783 | 181.5595 | 182.6929 | 183.6598 | 184.2963 | 186.0405 | 48.8007 | 61.2619 | 73.4623 | 82.3892 | 92.2866 | 115.7664 | 139.0549 | 159.7594 | 177.4078 | 192.1545 | 205.6252 | 217.8628
Zs-Sandy Bay | Creek Road | 12038 | 70.7616 | 74.419 | 75.5921 | 77.5522 | 79.8483 | 82.4429 | 84.6415 | 87.1811 | 88.3302 | 89.4588 | 90.2971 | 91.0096 | 147.6519 | 148.604 | 148.5739 | 150.4656 | 153.1625 | 156.3691 | 159.1634 | 161.2785 | 162.2853 | 163.1442 | 163.7096 | 165.259 | 411.6235 | 466.1309 | 541.4237 | 600.8215 | 630.901 | 703.4874 | 776.7516 | 843.0071 | 900.3906 | 949.0338 | 994.0276 | 1035.3399
Zs-Sandy Bay | Creek Road | 12039 | 88.3902 | 92.9588 | 94.4241 | 96.8725 | 99.7406 | 102.9816 | 105.728 | 108.9003 | 110.3356 | 111.7454 | 112.7925 | 113.6825 | 172.7451 | 173.859 | 173.8239 | 176.037 | 179.1923 | 182.9439 | 186.213 | 188.6876 | 189.8655 | 190.8704 | 191.5319 | 193.3446 | 121.4641 | 165.033 | 194.8722 | 236.7798 | 301.3295 | 459.4418 | 620.5668 | 766.7151 | 892.8158 | 998.6677 | 1095.1823 | 1182.2651
Zs-Summerleas | Kingston 33kV | 32374 | 84.115 | 88.4627 | 89.8572 | 92.1871 | 94.9165 | 98.0007 | 100.6143 | 103.6331 | 104.9991 | 106.3407 | 107.3371 | 108.184 | 197.9145 | 199.1907 | 199.1504 | 201.686 | 205.301 | 209.5992 | 213.3447 | 216.1798 | 217.5293 | 218.6806 | 219.4385 | 221.5153 | 813.9135 | 914.9937 | 1054.4874 | 1173.5565 | 1233.9229 | 1379.6113 | 1526.5909 | 1659.3625 | 1774.1499 | 1871.2096 | 1960.691 | 2042.5139
Zs-Summerleas | Kingston 33kV | 32377 | 100.5597 | 105.7573 | 107.4244 | 110.2099 | 113.4729 | 117.1601 | 120.2846 | 123.8936 | 125.5266 | 127.1305 | 128.3217 | 129.3343 | 146.4642 | 147.4086 | 147.3788 | 149.2553 | 151.9305 | 155.1113 | 157.8831 | 159.9813 | 160.98 | 161.832 | 162.3928 | 163.9297 | 9.54 | 14.3112 | 21.4241 | 34.1218 | 57.7163 | 123.9598 | 200.8418 | 279.3254 | 354.3464 | 422.8898 | 489.7429 | 553.2691
Zs-Summerleas | Kingston 33kV | 32379 | 108.0263 | 113.6099 | 115.4008 | 118.3931 | 121.8984 | 125.8593 | 129.2158 | 133.0928 | 134.8471 | 136.5701 | 137.8497 | 138.9375 | 247.4669 | 249.0626 | 249.0123 | 252.1828 | 256.7028 | 262.0772 | 266.7604 | 270.3055 | 271.9928 | 273.4324 | 274.38 | 276.9768 | 1031.628 | 1188.4558 | 1355.3893 | 1481.5198 | 1563.0361 | 1757.7429 | 1952.3698 | 2126.7614 | 2276.4503 | 2402.1913 | 2517.393 | 2622.0871
Zs-Trial Harbour | Rosebery 44kV | 99981 | 25.1962 | 26.4985 | 26.9162 | 27.6142 | 28.4317 | 29.3556 | 30.1385 | 31.0427 | 31.4519 | 31.8538 | 32.1523 | 32.406 | 44.781 | 45.0697 | 45.0606 | 45.6343 | 46.4523 | 47.4248 | 48.2723 | 48.9138 | 49.2191 | 49.4796 | 49.6511 | 50.121 | 88.8022 | 96.7338 | 112.1165 | 136.8403 | 167.8976 | 246.7371 | 330.8126 | 411.4757 | 485.9638 | 553.7069 | 621.365 | 688.743
Zs-Trial Harbour | Rosebery 44kV | 99982 | 17.6328 | 18.5441 | 18.8365 | 19.3249 | 19.897 | 20.5436 | 21.0914 | 21.7243 | 22.0106 | 22.2918 | 22.5007 | 22.6783 | 25.3663 | 25.5299 | 25.5247 | 25.8497 | 26.313 | 26.8639 | 27.344 | 27.7074 | 27.8803 | 28.0279 | 28.125 | 28.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Rosebery 44kV | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-West Hobart | Creek Road | 13043 | 28.0795 | 29.5309 | 29.9964 | 30.7742 | 31.6853 | 32.7149 | 33.5874 | 34.5951 | 35.0511 | 35.499 | 35.8316 | 36.1143 | 72.9473 | 73.4177 | 73.4029 | 74.3374 | 75.6699 | 77.2541 | 78.6346 | 79.6796 | 80.177 | 80.6013 | 80.8807 | 81.6461 | 100.6974 | 113.3564 | 139.7779 | 157.6201 | 179.3728 | 231.4577 | 283.581 | 330.2947 | 370.3802 | 404.0435 | 434.8883 | 462.9395
Zs-West Hobart | Creek Road | 13044 | 91.5674 | 96.3002 | 97.8183 | 100.3547 | 103.3259 | 106.6833 | 109.5284 | 112.8148 | 114.3017 | 115.7622 | 116.8469 | 117.7689 | 94.3343 | 94.9425 | 94.9233 | 96.1319 | 97.855 | 99.9037 | 101.6889 | 103.0403 | 103.6835 | 104.2323 | 104.5935 | 105.5834 | 6.5664 | 6.5664 | 6.5664 | 21.8666 | 49.226 | 123.7986 | 208.6751 | 294.509 | 376.5427 | 452.0602 | 526.6742 | 598.7117
Zs-West Hobart | Creek Road | 13045 | 96.8905 | 101.8985 | 103.5048 | 106.1886 | 109.3326 | 112.8852 | 115.8957 | 119.3731 | 120.9465 | 122.4918 | 123.6396 | 124.6152 | 229.0613 | 230.5384 | 230.4918 | 233.4264 | 237.6103 | 242.585 | 246.9199 | 250.2012 | 251.7631 | 253.0956 | 253.9727 | 256.3764 | 926.1013 | 1119.8395 | 1303.2469 | 1403.6228 | 1481.9648 | 1672.3433 | 1866.9181 | 2046.2648 | 2205.7104 | 2345.4009 | 2479.688 | 2608.2661
Zs-West Hobart | Creek Road | 13046 | 43.1839 | 45.416 | 46.1319 | 47.3281 | 48.7293 | 50.3127 | 51.6545 | 53.2043 | 53.9056 | 54.5944 | 55.1059 | 55.5407 | 63.5932 | 64.0033 | 63.9903 | 64.8051 | 65.9666 | 67.3477 | 68.5512 | 69.4622 | 69.8958 | 70.2657 | 70.5093 | 71.1766 | 0 | 0 | 0 | 0.26548 | 0.69025 | 1.7256 | 2.7875 | 3.7698 | 4.6459 | 5.4158 | 6.1592 | 6.8759
Zs-West Hobart | Creek Road | 13047 | 46.4396 | 48.8399 | 49.6098 | 50.8962 | 52.403 | 54.1058 | 55.5488 | 57.2155 | 57.9696 | 58.7103 | 59.2604 | 59.728 | 50.3429 | 50.6675 | 50.6573 | 51.3023 | 52.2218 | 53.3151 | 54.2679 | 54.989 | 55.3323 | 55.6252 | 55.8179 | 56.3462 | 0 | 0 | 0 | 11.2783 | 29.2117 | 72.9185 | 118.0417 | 160.2582 | 198.3707 | 232.1357 | 264.7276 | 295.8069
Zs-West Hobart | Creek Road | 13048 | 60.7693 | 63.9102 | 64.9177 | 66.601 | 68.5729 | 70.8011 | 72.6892 | 74.8702 | 75.857 | 76.8263 | 77.5462 | 78.158 | 117.6061 | 118.3644 | 118.3405 | 119.8472 | 121.9953 | 124.5495 | 126.7751 | 128.4599 | 129.2618 | 129.9459 | 130.3962 | 131.6303 | 34.67 | 34.67 | 34.67 | 54.0978 | 87.9007 | 177.6926 | 277.4413 | 375.9439 | 467.783 | 550.0792 | 629.0341 | 702.8741
Zs-West Hobart | Creek Road | 13049 | 59.486 | 62.5607 | 63.5469 | 65.1946 | 67.1248 | 69.306 | 71.1543 | 73.2892 | 74.2552 | 75.204 | 75.9086 | 76.5076 | 147.3615 | 148.3117 | 148.2817 | 150.1697 | 152.8613 | 156.0616 | 158.8504 | 160.9614 | 161.9662 | 162.8234 | 163.3877 | 164.934 | 250.8377 | 286.8219 | 374.9651 | 417.8176 | 471.5336 | 605.6522 | 747.7778 | 884.9633 | 1013.8163 | 1133.7468 | 1256.3392 | 1380.6887
Zs-West Hobart | Creek Road | 13050 | 34.2201 | 35.9889 | 36.5562 | 37.5041 | 38.6145 | 39.8692 | 40.9325 | 42.1606 | 42.7163 | 43.2621 | 43.6675 | 44.012 | 70.3568 | 70.8105 | 70.7962 | 71.6976 | 72.9827 | 74.5107 | 75.8421 | 76.85 | 77.3298 | 77.739 | 78.0084 | 78.7467 | 88.3163 | 95.1455 | 119.7654 | 130.7865 | 144.9675 | 179.1979 | 213.7357 | 244.937 | 271.9123 | 294.7203 | 315.7449 | 334.9663
Zs-West Hobart | Creek Road | 13052 | 134.1762 | 141.1114 | 143.3358 | 147.0525 | 151.4062 | 156.326 | 160.495 | 165.3106 | 167.4895 | 169.6295 | 171.219 | 172.57 | 197.2235 | 198.4953 | 198.4551 | 200.9819 | 204.5843 | 208.8675 | 212.5998 | 215.4251 | 216.7699 | 217.9172 | 218.6724 | 220.742 | 110.0848 | 122.3229 | 143.3479 | 171.4534 | 209.0968 | 302.2672 | 399.8996 | 493.0671 | 580.0492 | 661.6722 | 747.8121 | 840.7462
Zs-West Hobart | Creek Road | 13053 | 61.3301 | 64.5001 | 65.5168 | 67.2156 | 69.2057 | 71.4545 | 73.3601 | 75.5612 | 76.5571 | 77.5353 | 78.2618 | 78.8794 | 134.613 | 135.481 | 135.4536 | 137.1782 | 139.637 | 142.5605 | 145.108 | 147.0363 | 147.9542 | 148.7373 | 149.2527 | 150.6653 | 38.0058 | 40.5913 | 51.4034 | 86.1973 | 133.9272 | 262.3044 | 408.6106 | 559.4182 | 709.0649 | 854.5234 | 1008.3124 | 1168.6095
Zs-West Hobart | Creek Road | 13054 | 47.3759 | 49.8246 | 50.61 | 51.9223 | 53.4596 | 55.1967 | 56.6687 | 58.369 | 59.1384 | 59.894 | 60.4552 | 60.9322 | 76.3237 | 76.8158 | 76.8003 | 77.7782 | 79.1722 | 80.8298 | 82.2742 | 83.3675 | 83.888 | 84.332 | 84.6242 | 85.4251 | 0 | 0 | 0 | 3.985 | 12.0628 | 36.7919 | 68.1771 | 103.3684 | 140.4572 | 177.8671 | 218.0428 | 259.8162
Zs-West Hobart | Creek Road | 13055 | 81.0741 | 85.2645 | 86.6086 | 88.8544 | 91.4851 | 94.4578 | 96.9768 | 99.8866 | 101.2031 | 102.4962 | 103.4566 | 104.273 | 179.5229 | 180.6805 | 180.6439 | 182.9439 | 186.223 | 190.1218 | 193.5192 | 196.0909 | 197.315 | 198.3593 | 199.0467 | 200.9306 | 326.0837 | 439.3662 | 516.6037 | 557.0249 | 614.3729 | 757.8377 | 907.4285 | 1046.5014 | 1169.6476 | 1275.7847 | 1375.091 | 1466.9073
Zs-West Hobart | Creek Road | 13056 | 33.0082 | 34.7143 | 35.2615 | 36.1758 | 37.2469 | 38.4572 | 39.4828 | 40.6674 | 41.2034 | 41.7299 | 42.1209 | 42.4533 | 84.3856 | 84.9298 | 84.9126 | 85.9937 | 87.5351 | 89.3677 | 90.9647 | 92.1735 | 92.7489 | 93.2398 | 93.5629 | 94.4484 | 52.1514 | 60.2982 | 81.947 | 104.277 | 132.202 | 198.338 | 263.7859 | 321.8023 | 371.0779 | 412.076 | 449.3376 | 482.9906
Zs-West Hobart | Creek Road | 13057 | 92.4799 | 97.2599 | 98.7931 | 101.3548 | 104.3556 | 107.7465 | 110.62 | 113.939 | 115.4408 | 116.9158 | 118.0114 | 118.9425 | 187.2575 | 188.465 | 188.4268 | 190.8259 | 194.2463 | 198.313 | 201.8568 | 204.5393 | 205.8162 | 206.9055 | 207.6225 | 209.5875 | 521.7969 | 588.9074 | 684.7019 | 749.4315 | 804.5854 | 936.0348 | 1068.0228 | 1187.7194 | 1292.4599 | 1382.655 | 1467.6087 | 1542.4398
Zs-West Hobart | Creek Road | 13058 | 45.2942 | 47.6353 | 48.3862 | 49.6408 | 51.1105 | 52.7713 | 54.1787 | 55.8042 | 56.5398 | 57.2622 | 57.7988 | 58.2548 | 30.5806 | 30.7778 | 30.7716 | 31.1634 | 31.7219 | 32.3861 | 32.9648 | 33.4029 | 33.6114 | 33.7893 | 33.9064 | 34.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Information
TRANSMISSION - DISTRIBUTION |  | 2025 (Actuals) | 2026 (Actuals) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Load transfer point | Peaking season | General info
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Notes (see chapter 4.9 of the APR)
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Arthurs Lake (DL) | Central | Distribution lines | 110/6.6 kV | 1 | Summer
Arthurs Lake (DL) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Avoca | Eastern | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Maximum demand (peak season) (MW) | 0.020573 | 0.020706 | 0.020701 | 0.020965 | 0.021341 | 0.021788 | 0.022177 | 0.022472 | 0.022612 | 0.022732 | 0.02281 | 0.023026 |  |  | Bridgewater | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.043915 | 0.044199 | 0.04419 | 0.044752 | 0.045555 | 0.046508 | 0.047339 | 0.047968 | 0.048268 | 0.048523 | 0.048691 | 0.049152 |  |  | Burnie | North West | Distribution lines | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Burnie Substation supply transformers (2033)
Arthurs Lake (DL) | Maximum demand (peak season) (MVA) | 0.048496 | 0.048808 | 0.048798 | 0.04942 | 0.050306 | 0.051359 | 0.052276 | 0.052971 | 0.053302 | 0.053584 | 0.05377 | 0.054279 |  |  | Chapel Street | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Maximum demand (peak season) Power factor (coincident) | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 | 0.42422 |  |  | Creek Road | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter
Arthurs Lake (DL) | Maximum demand (non-peak season) (MW) | 0.017402 | 0.018301 | 0.01859 | 0.019072 | 0.019637 | 0.020275 | 0.020815 | 0.02144 | 0.021723 | 0.022 | 0.022206 | 0.022381 |  | 0.018301 | Derby | Northern | Distribution lines | 110/22 kV | 1 | Winter
Arthurs Lake (DL) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.044451 | 0.046748 | 0.047485 | 0.048717 | 0.050159 | 0.051789 | 0.05317 | 0.054765 | 0.055487 | 0.056196 | 0.056723 | 0.05717 |  |  | Derwent Bridge | Central | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Maximum demand (non-peak season) (MVA) | 0.047736 | 0.050203 | 0.050994 | 0.052317 | 0.053866 | 0.055616 | 0.057099 | 0.058812 | 0.059588 | 0.060349 | 0.060914 | 0.061395 |  |  | Devonport | North West | Distribution lines | 110/22 kV | 3 | Winter
Arthurs Lake (DL) | Hours exceeding 95% of maximum demand | 1226 | [13 empty] | Electrona | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Hours exceeding Firm capacity (continuous rating) | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 |  |  | Emu Bay (RT) | North West | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Hours exceeding Firm capacity (short-term rating) | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 | 8753.5 |  |  | George Town | Northern | Distribution lines | 110/22 kV | 2 | Winter
Arthurs Lake (DL) | Regional Diversity Factor (Summer) | 0.79208 | [13 empty] | Hadspen | Northern | Distribution lines | 110/22 kV | 2 | Winter
Arthurs Lake (DL) | Regional Diversity Factor (Winter) | 0.91429 | [13 empty] | Huon River | Kingston-South | Distribution lines | 110/11 kV | 1 | Summer
Arthurs Lake (DL) | Load transfer capacity (MVA)1 | 0.1 | [11 empty] | Waddmana |  | Kermandie | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Arthurs Lake (DL) | Load transfer capacity (MVA)2 | [14 empty] | Kingston 11kV | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Proposed retirement/ replacement of Kingston Substation 110 kV circuit breakers (2033)
Arthurs Lake (DL) | Load transfer capacity (MVA)3 | [14 empty] | Kingston 33kV | Kingston-South | Sub-transmission lines | 110/33 kV | 2 | Winter | Proposed retirement/ replacement of Kingston Substation 110 kV circuit breakers (2033)
Arthurs Lake (DL) | Load transfer capacity (MVA)4 | [14 empty] | Knights Road | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Proposed retirement/ replacement of Knights Road Substation 11 kV switchgear (2032)
Arthurs Lake (DL) | Load transfer capacity (MVA)5 | [14 empty] | Lindisfarne | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Arthurs Lake (DL) | Embedded generation capacity (MVA) Units less than 100 kVA | 0.012 | [13 empty] | Meadowbank | Central | Distribution lines | 110/22 kV | 1 | Summer
Arthurs Lake (DL) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0 | [13 empty] | Mornington | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Total | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | Summer | Mowbray | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | New Norfolk | Central | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Newton | West Cost | Distribution lines | 110/22 kV | 1 | Winter
Avoca | Maximum demand (peak season) (MW) | 8.9186 | 9.3796 | 9.5275 | 9.7745 | 10.0639 | 10.3909 | 10.668 | 10.9881 | 11.1329 | 11.2752 | 11.3808 | 11.4706 |  |  | North Hobart | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Avoca | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.846 | 1.9414 | 1.972 | 2.0232 | 2.0831 | 2.1507 | 2.2081 | 2.2744 | 2.3043 | 2.3338 | 2.3556 | 2.3742 |  |  | Norwood | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (peak season) (MVA) | 9.1077 | 9.5784 | 9.7294 | 9.9817 | 10.2772 | 10.6112 | 10.8941 | 11.221 | 11.3689 | 11.5142 | 11.6221 | 11.7138 |  |  | Palmerston | Northern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Maximum demand (peak season) Power factor (coincident) | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 | 0.97924 |  |  | Port Latta (RT) | North West | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Summer
Avoca | Maximum demand (non-peak season) (MW) | 8.0203 | 8.072 | 8.0704 | 8.1731 | 8.3196 | 8.4938 | 8.6456 | 8.7605 | 8.8151 | 8.8618 | 8.8925 | 8.9767 |  | 0.018301 | Queenstown | West Coast | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.64984 | 0.65403 | 0.6539 | 0.66222 | 0.67409 | 0.6882 | 0.7005 | 0.70981 | 0.71424 | 0.71802 | 0.72051 | 0.72733 |  |  | Railton | North West | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Maximum demand (non-peak season) (MVA) | 8.0466 | 8.0984 | 8.0968 | 8.1999 | 8.3469 | 8.5216 | 8.6739 | 8.7892 | 8.844 | 8.8908 | 8.9217 | 9.0061 |  |  | Risdon 33kV | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter
Avoca | Hours exceeding 95% of maximum demand | 3.5 | [13 empty] | Rokeby | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Avoca | Hours exceeding Firm capacity (continuous rating) | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 |  |  | Rosebery 22kV | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Proposed retirement/ replacement of Rosebery supply transformers and associated asset replacement (2028)
Avoca | Hours exceeding Firm capacity (short-term rating) | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 | 8308.5 |  |  | Rosebery 44kV | West Coast | Distribution lines and transmission-connected customer | 110/44 kV | 2 | Winter
Avoca | Regional Diversity Factor (Summer) | 0.56211 | [13 empty] | Savage River DL | West Coast | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Savage River Substation supply transformers (2032)
Avoca | Regional Diversity Factor (Winter) | 0.83413 | [13 empty] | Scottsdale | Northern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)1 | 4.6 | [11 empty] | St Marys |  | Sheffield | North West | Distribution lines | 110/22 kV | 1 | Winter | Proposed retirement/ replacement of network transformer T1 (2027)
Avoca | Load transfer capacity (MVA)2 | 4.6 | [11 empty] | Palmerston |  | Smithton | North West | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)3 | [14 empty] | Sorell | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Avoca | Load transfer capacity (MVA)4 | [14 empty] | St Leonards | Northern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Load transfer capacity (MVA)5 | [14 empty] | St Marys | Eastern | Distribution lines | 110/22 kV | 2 | Summer
Avoca | Embedded generation capacity (MVA) Units less than 100 kVA | 3.267 | [13 empty] | Trevallyn | Northern | Distribution lines | 110/22 kV | 3 | Winter
Avoca | Embedded generation capacity (MVA) Units greater than 100 kVA | 0 | [13 empty] | Triabunna (RT) | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter | Tungatinah | Central | Distribution lines | 110/22 kV | 1 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | Ulverstone | North West | Distribution lines | 110/22 kV | 2 | Winter
Bridgewater | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  |  | Waddamana | Central | Distribution lines | 110/22 kV | 1 | Winter | Proposed retirement/ replacement of Waddamana supply transformer (2030)
Bridgewater | Maximum demand (peak season) (MW) | 36.056 | 36.2885 | 36.2811 | 36.7431 | 37.4016 | 38.1847 | 38.867 | 39.3835 | 39.6294 | 39.8391 | 39.9772 | 40.3556 |  |  | Wesley Vale | North West | Distribution lines | 110/22 kV | 2 | Winter | Proposed retirement/ replacement of Wesley Vale supply transformers (2033)
Bridgewater | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.4926 | 1.5022 | 1.5019 | 1.521 | 1.5483 | 1.5807 | 1.6089 | 1.6303 | 1.6405 | 1.6492 | 1.6549 | 1.6706 |  |  | Zs-Bellerive | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | 1) Proposed retirement/ replacement of Lindisfarne-Bellerive 33 kV sub-transmission cable (2032). 2) Proposed retirement/ replacement of Bellerive Substation supply transformers (2301)
Bridgewater | Maximum demand (peak season) (MVA) | 36.0868 | 36.3195 | 36.3122 | 36.7745 | 37.4337 | 38.2174 | 38.9003 | 39.4173 | 39.6633 | 39.8733 | 40.0114 | 40.3901 |  |  | Zs-Cambridge | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter
Bridgewater | Maximum demand (peak season) Power factor (coincident) | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99914 |  |  | Zs-Claremont | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Claremont 33 kV sub-transmission cable (2030)
Bridgewater | Maximum demand (non-peak season) (MW) | 18.418 | 19.3699 | 19.6753 | 20.1854 | 20.7831 | 21.4584 | 22.0307 | 22.6917 | 22.9908 | 23.2845 | 23.5027 | 23.6882 |  | 0.018301 | Zs-Derwent Park | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Derwent Park Substation supply transformers (2030)
Bridgewater | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.03268 | 0.034369 | 0.034911 | 0.035816 | 0.036877 | 0.038075 | 0.03909 | 0.040263 | 0.040794 | 0.041315 | 0.041702 | 0.042031 |  |  | Zs-East Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Proposed retirement/ replacement of East Hobart 33 kV sub-transmission cable (2027)
Bridgewater | Maximum demand (non-peak season) (MVA) | 18.418 | 19.37 | 19.6753 | 20.1855 | 20.7831 | 21.4584 | 22.0307 | 22.6917 | 22.9908 | 23.2846 | 23.5027 | 23.6882 |  |  | Zs-Geilston Bay | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Geilston Bay Substation supply transformers (2033)
Bridgewater | Hours exceeding 95% of maximum demand | 4.5 | [13 empty] | Zs-Howrah | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter
Bridgewater | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 |  |  | Zs-New Town | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Proposed retirement/ replacement of Newtown 33 kV sub-transmission cable (2031)
Bridgewater | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 |  |  | Zs-Rosny Park | Greater Hobart | Distribution lines | 33/11 kV | 1 | Winter
Bridgewater | Regional Diversity Factor (Summer) | 0.9735 | [13 empty] | Zs-Sandy Bay | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Proposed retirement/ replacement of Sandy Bay 33 kV sub-transmission cable (2032)
Bridgewater | Regional Diversity Factor (Winter) | 0.96741 | [13 empty] | Zs-Summerleas | Kingston-South | Distribution lines | 33/11 kV | 1 | Winter
Bridgewater | Load transfer capacity (MVA)1 | [14 empty] | Zs-Trial Harbour | West Coast | Distribution lines | 44/22 kV | 2 | Winter
Bridgewater | Load transfer capacity (MVA)2 | [14 empty] | Zs-West Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter
Bridgewater | Load transfer capacity (MVA)3
Bridgewater | Load transfer capacity (MVA)4
Bridgewater | Load transfer capacity (MVA)5
Bridgewater | Embedded generation capacity (MVA) Units less than 100 kVA | 21.781
Bridgewater | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Burnie | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Burnie | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Burnie | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Burnie | Maximum demand (peak season) (MW) | 61.7219 | 62.1198 | 62.1073 | 62.8981 | 64.0254 | 65.3659 | 66.5339 | 67.4181 | 67.839 | 68.198 | 68.4344 | 69.082
Burnie | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.6359 | 2.6529 | 2.6524 | 2.6861 | 2.7343 | 2.7915 | 2.8414 | 2.8792 | 2.8972 | 2.9125 | 2.9226 | 2.9502
Burnie | Maximum demand (peak season) (MVA) | 61.7781 | 62.1765 | 62.1639 | 62.9554 | 64.0838 | 65.4255 | 66.5946 | 67.4796 | 67.9008 | 68.2602 | 68.4967 | 69.145
Burnie | Maximum demand (peak season) Power factor (coincident) | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909 | 0.99909
Burnie | Maximum demand (non-peak season) (MW) | 34.0843 | 35.846 | 36.4111 | 37.3552 | 38.4612 | 39.7109 | 40.77 | 41.9932 | 42.5467 | 43.0904 | 43.4941 | 43.8373 |  | 0.018301
Burnie | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.9657 | 3.119 | 3.1681 | 3.2503 | 3.3465 | 3.4553 | 3.5474 | 3.6538 | 3.702 | 3.7493 | 3.7844 | 3.8143
Burnie | Maximum demand (non-peak season) (MVA) | 34.2131 | 35.9814 | 36.5486 | 37.4963 | 38.6065 | 39.861 | 40.924 | 42.1519 | 42.7075 | 43.2532 | 43.6585 | 44.0029
Burnie | Hours exceeding 95% of maximum demand | 3.5
Burnie | Hours exceeding Firm capacity (continuous rating) | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096 | 7096
Burnie | Hours exceeding Firm capacity (short-term rating) | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5 | 6031.5
Burnie | Regional Diversity Factor (Summer) | 0.93786
Burnie | Regional Diversity Factor (Winter) | 0.9684
Burnie | Load transfer capacity (MVA)1 | 8.8 | [11 empty] | Port Latta
Burnie | Load transfer capacity (MVA)2 | 8.8 | [11 empty] | Ulverstone
Burnie | Load transfer capacity (MVA)3
Burnie | Load transfer capacity (MVA)4
Burnie | Load transfer capacity (MVA)5
Burnie | Embedded generation capacity (MVA) Units less than 100 kVA | 32.961
Burnie | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.003
Creek Road | Substation capacity (winter and summer) (MVA) Total | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | Winter
Creek Road | Substation capacity (winter and summer) (MVA) Firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Creek Road | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Creek Road | Maximum demand (peak season) (MW) | 88.6872 | 89.259 | 89.241 | 90.3772 | 91.9971 | 93.9232 | 95.6016 | 96.872 | 97.4768 | 97.9927 | 98.3323 | 99.2629
Creek Road | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 11.9114 | 11.9882 | 11.9857 | 12.1383 | 12.3559 | 12.6146 | 12.84 | 13.0106 | 13.0919 | 13.1612 | 13.2068 | 13.3318
Creek Road | Maximum demand (peak season) (MVA) | 89.4835 | 90.0605 | 90.0423 | 91.1887 | 92.8232 | 94.7665 | 96.46 | 97.7419 | 98.352 | 98.8725 | 99.2152 | 100.1542
Creek Road | Maximum demand (peak season) Power factor (coincident) | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911 | 0.9911
Creek Road | Maximum demand (non-peak season) (MW) | 41.0703 | 43.1931 | 43.874 | 45.0116 | 46.3443 | 47.8502 | 49.1263 | 50.6003 | 51.2673 | 51.9223 | 52.4088 | 52.8224 |  | 0.018301
Creek Road | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.1917 | 1.2533 | 1.2731 | 1.3061 | 1.3447 | 1.3884 | 1.4255 | 1.4682 | 1.4876 | 1.5066 | 1.5207 | 1.5327
Creek Road | Maximum demand (non-peak season) (MVA) | 41.0876 | 43.2113 | 43.8925 | 45.0306 | 46.3638 | 47.8704 | 49.147 | 50.6216 | 51.2888 | 51.9442 | 52.4309 | 52.8446
Creek Road | Hours exceeding 95% of maximum demand | 10
Creek Road | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Creek Road | Hours exceeding Firm capacity (short-term rating) | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087 | 5087
Creek Road | Regional Diversity Factor (Summer) | 0.96484
Creek Road | Regional Diversity Factor (Winter) | 1
Creek Road | Load transfer capacity (MVA)1
Creek Road | Load transfer capacity (MVA)2
Creek Road | Load transfer capacity (MVA)3
Creek Road | Load transfer capacity (MVA)4
Creek Road | Load transfer capacity (MVA)5
Creek Road | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Creek Road | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Chapel Street | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Chapel Street | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Chapel Street | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Chapel Street | Maximum demand (peak season) (MW) | 36.972 | 37.2104 | 37.2029 | 37.6765 | 38.3518 | 39.1548 | 39.8545 | 40.3841 | 40.6362 | 40.8513 | 40.9928 | 41.3808
Chapel Street | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.12836 | 0.12918 | 0.12916 | 0.1308 | 0.13315 | 0.13593 | 0.13836 | 0.1402 | 0.14108 | 0.14182 | 0.14232 | 0.14366
Chapel Street | Maximum demand (peak season) (MVA) | 36.9722 | 37.2106 | 37.2031 | 37.6768 | 38.3521 | 39.155 | 39.8547 | 40.3843 | 40.6364 | 40.8515 | 40.9931 | 41.3811
Chapel Street | Maximum demand (peak season) Power factor (coincident) | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
Chapel Street | Maximum demand (non-peak season) (MW) | 17.7188 | 18.6347 | 18.9284 | 19.4192 | 19.9942 | 20.6439 | 21.1944 | 21.8303 | 22.1181 | 22.4007 | 22.6106 | 22.789 |  | 0.018301
Chapel Street | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.34083 | 0.35845 | 0.3641 | 0.37354 | 0.3846 | 0.3971 | 0.40769 | 0.41992 | 0.42545 | 0.43089 | 0.43493 | 0.43836
Chapel Street | Maximum demand (non-peak season) (MVA) | 17.7221 | 18.6381 | 18.9319 | 19.4228 | 19.9979 | 20.6477 | 21.1983 | 21.8344 | 22.1222 | 22.4048 | 22.6148 | 22.7932
Chapel Street | Hours exceeding 95% of maximum demand | 8.5
Chapel Street | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Chapel Street | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Chapel Street | Regional Diversity Factor (Summer) | 0.96596
Chapel Street | Regional Diversity Factor (Winter) | 1
Chapel Street | Load transfer capacity (MVA)1
Chapel Street | Load transfer capacity (MVA)2
Chapel Street | Load transfer capacity (MVA)3
Chapel Street | Load transfer capacity (MVA)4
Chapel Street | Load transfer capacity (MVA)5
Chapel Street | Embedded generation capacity (MVA) Units less than 100 kVA | 20.875
Chapel Street | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Derwent Bridge | Substation capacity (winter and summer) (MVA) Total | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | Summer
Derwent Bridge | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derwent Bridge | Maximum demand (peak season) (MW) | 0.23429 | 0.2464 | 0.25029 | 0.25678 | 0.26438 | 0.27297 | 0.28025 | 0.28866 | 0.29246 | 0.2962 | 0.29898 | 0.30133
Derwent Bridge | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.045707 | 0.048069 | 0.048827 | 0.050093 | 0.051576 | 0.053252 | 0.054672 | 0.056313 | 0.057055 | 0.057784 | 0.058326 | 0.058786
Derwent Bridge | Maximum demand (peak season) (MVA) | 0.23871 | 0.25105 | 0.25501 | 0.26162 | 0.26936 | 0.27812 | 0.28553 | 0.2941 | 0.29798 | 0.30178 | 0.30461 | 0.30702
Derwent Bridge | Maximum demand (peak season) Power factor (coincident) | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815 | 0.9815
Derwent Bridge | Maximum demand (non-peak season) (MW) | 0.31649 | 0.31853 | 0.31847 | 0.32252 | 0.3283 | 0.33518 | 0.34116 | 0.3457 | 0.34786 | 0.3497 | 0.35091 | 0.35423 |  | 0.018301
Derwent Bridge | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.051218 | 0.051548 | 0.051538 | 0.052194 | 0.053129 | 0.054242 | 0.055211 | 0.055945 | 0.056294 | 0.056592 | 0.056788 | 0.057326
Derwent Bridge | Maximum demand (non-peak season) (MVA) | 0.32061 | 0.32267 | 0.32261 | 0.32672 | 0.33257 | 0.33954 | 0.3456 | 0.3502 | 0.35238 | 0.35425 | 0.35548 | 0.35884
Derwent Bridge | Hours exceeding 95% of maximum demand | 8.5
Derwent Bridge | Hours exceeding Firm capacity (continuous rating) | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5
Derwent Bridge | Hours exceeding Firm capacity (short-term rating) | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5 | 8657.5
Derwent Bridge | Regional Diversity Factor (Summer) | 0.49386
Derwent Bridge | Regional Diversity Factor (Winter) | 0.75693
Derwent Bridge | Load transfer capacity (MVA)1
Derwent Bridge | Load transfer capacity (MVA)2
Derwent Bridge | Load transfer capacity (MVA)3
Derwent Bridge | Load transfer capacity (MVA)4
Derwent Bridge | Load transfer capacity (MVA)5
Derwent Bridge | Embedded generation capacity (MVA) Units less than 100 kVA | 0.055
Derwent Bridge | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Derby | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Derby | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby | Maximum demand (peak season) (MW) | 3.4247 | 3.4468 | 3.4461 | 3.4899 | 3.5525 | 3.6269 | 3.6917 | 3.7407 | 3.7641 | 3.784 | 3.7971 | 3.8331
Derby | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.74914 | 0.75397 | 0.75382 | 0.76342 | 0.7771 | 0.79337 | 0.80755 | 0.81828 | 0.82339 | 0.82774 | 0.83061 | 0.83847
Derby | Maximum demand (peak season) (MVA) | 3.5057 | 3.5283 | 3.5275 | 3.5725 | 3.6365 | 3.7126 | 3.779 | 3.8292 | 3.8531 | 3.8735 | 3.8869 | 3.9237
Derby | Maximum demand (peak season) Power factor (coincident) | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769 | 0.9769
Derby | Maximum demand (non-peak season) (MW) | 5.6047 | 5.8944 | 5.9874 | 6.1426 | 6.3245 | 6.53 | 6.7041 | 6.9053 | 6.9963 | 7.0857 | 7.1521 | 7.2085 |  | 0.018301
Derby | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.76499 | 0.80453 | 0.81721 | 0.8384 | 0.86323 | 0.89128 | 0.91505 | 0.9425 | 0.95492 | 0.96712 | 0.97619 | 0.98389
Derby | Maximum demand (non-peak season) (MVA) | 5.6567 | 5.9491 | 6.0429 | 6.1996 | 6.3831 | 6.5905 | 6.7663 | 6.9693 | 7.0612 | 7.1514 | 7.2184 | 7.2753
Derby | Hours exceeding 95% of maximum demand | 0.5
Derby | Hours exceeding Firm capacity (continuous rating) | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5
Derby | Hours exceeding Firm capacity (short-term rating) | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5 | 8723.5
Derby | Regional Diversity Factor (Summer) | 0.78267
Derby | Regional Diversity Factor (Winter) | 0.69464
Derby | Load transfer capacity (MVA)1 | 5.3 | [11 empty] | Scottsdale
Derby | Load transfer capacity (MVA)2
Derby | Load transfer capacity (MVA)3
Derby | Load transfer capacity (MVA)4
Derby | Load transfer capacity (MVA)5
Derby | Embedded generation capacity (MVA) Units less than 100 kVA | 2.841
Derby | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Devonport | Substation capacity (winter and summer) (MVA) Total | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | Winter
Devonport | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Devonport | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Devonport | Maximum demand (peak season) (MW) | 57.4129 | 57.7831 | 57.7714 | 58.507 | 59.5556 | 60.8025 | 61.889 | 62.7115 | 63.103 | 63.4369 | 63.6568 | 64.2593
Devonport | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 4.2688 | 4.2964 | 4.2955 | 4.3502 | 4.4282 | 4.5209 | 4.6016 | 4.6628 | 4.6919 | 4.7167 | 4.7331 | 4.7779
Devonport | Maximum demand (peak season) (MVA) | 57.5714 | 57.9426 | 57.9309 | 58.6685 | 59.72 | 60.9703 | 62.0599 | 62.8846 | 63.2772 | 63.612 | 63.8325 | 64.4366
Devonport | Maximum demand (peak season) Power factor (coincident) | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725 | 0.99725
Devonport | Maximum demand (non-peak season) (MW) | 28.8693 | 30.3615 | 30.8401 | 31.6398 | 32.5765 | 33.6351 | 34.5321 | 35.5682 | 36.037 | 36.4974 | 36.8394 | 37.1301 |  | 0.018301
Devonport | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 3.8871 | 4.088 | 4.1524 | 4.2601 | 4.3862 | 4.5287 | 4.6495 | 4.789 | 4.8521 | 4.9141 | 4.9602 | 4.9993
Devonport | Maximum demand (non-peak season) (MVA) | 29.1298 | 30.6355 | 31.1184 | 31.9253 | 32.8705 | 33.9386 | 34.8437 | 35.8891 | 36.3622 | 36.8268 | 37.1718 | 37.4651
Devonport | Hours exceeding 95% of maximum demand | 2
Devonport | Hours exceeding Firm capacity (continuous rating) | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825 | 4825
Devonport | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Devonport | Regional Diversity Factor (Summer) | 0.85864
Devonport | Regional Diversity Factor (Winter) | 0.98848
Devonport | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Railton
Devonport | Load transfer capacity (MVA)2 | 6.3 | [11 empty] | Ulverstone
Devonport | Load transfer capacity (MVA)3
Devonport | Load transfer capacity (MVA)4
Devonport | Load transfer capacity (MVA)5
Devonport | Embedded generation capacity (MVA) Units less than 100 kVA | 24.972
Devonport | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.013
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Total | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | Winter
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Emu Bay (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Emu Bay (RT) | Maximum demand (peak season) (MW) | 9.0186 | 9.0768 | 9.0749 | 9.1905 | 9.3552 | 9.5511 | 9.7217 | 9.8509 | 9.9124 | 9.9649 | 9.9994 | 10.0941
Emu Bay (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.7959 | 1.8075 | 1.8071 | 1.8301 | 1.8629 | 1.9019 | 1.9359 | 1.9617 | 1.9739 | 1.9844 | 1.9912 | 2.0101
Emu Bay (RT) | Maximum demand (peak season) (MVA) | 9.1957 | 9.255 | 9.2531 | 9.3709 | 9.5389 | 9.7386 | 9.9126 | 10.0443 | 10.107 | 10.1605 | 10.1958 | 10.2922
Emu Bay (RT) | Maximum demand (peak season) Power factor (coincident) | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074 | 0.98074
Emu Bay (RT) | Maximum demand (non-peak season) (MW) | 6.5005 | 6.8364 | 6.9442 | 7.1243 | 7.3352 | 7.5736 | 7.7755 | 8.0088 | 8.1144 | 8.2181 | 8.2951 | 8.3605 |  | 0.018301
Emu Bay (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.3502 | 1.4199 | 1.4423 | 1.4797 | 1.5235 | 1.573 | 1.615 | 1.6634 | 1.6854 | 1.7069 | 1.7229 | 1.7365
Emu Bay (RT) | Maximum demand (non-peak season) (MVA) | 6.6392 | 6.9824 | 7.0924 | 7.2763 | 7.4918 | 7.7352 | 7.9415 | 8.1798 | 8.2876 | 8.3935 | 8.4721 | 8.539
Emu Bay (RT) | Hours exceeding 95% of maximum demand | 4
Emu Bay (RT) | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Emu Bay (RT) | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Emu Bay (RT) | Regional Diversity Factor (Summer) | 0.42035
Emu Bay (RT) | Regional Diversity Factor (Winter) | 0.79298
Emu Bay (RT) | Load transfer capacity (MVA)1
Emu Bay (RT) | Load transfer capacity (MVA)2
Emu Bay (RT) | Load transfer capacity (MVA)3
Emu Bay (RT) | Load transfer capacity (MVA)4
Emu Bay (RT) | Load transfer capacity (MVA)5
Emu Bay (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Emu Bay (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Electrona | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Electrona | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Electrona | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Electrona | Maximum demand (peak season) (MW) | 15.4347 | 15.5342 | 15.5311 | 15.7288 | 16.0108 | 16.346 | 16.6381 | 16.8592 | 16.9644 | 17.0542 | 17.1133 | 17.2753
Electrona | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.67474 | 0.67909 | 0.67896 | 0.6876 | 0.69993 | 0.71458 | 0.72735 | 0.73702 | 0.74162 | 0.74554 | 0.74813 | 0.75521
Electrona | Maximum demand (peak season) (MVA) | 15.4495 | 15.5491 | 15.5459 | 15.7439 | 16.0261 | 16.3616 | 16.654 | 16.8753 | 16.9806 | 17.0705 | 17.1297 | 17.2918
Electrona | Maximum demand (peak season) Power factor (coincident) | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905 | 0.99905
Electrona | Maximum demand (non-peak season) (MW) | 8.8817 | 9.3407 | 9.488 | 9.734 | 10.0222 | 10.3479 | 10.6238 | 10.9426 | 11.0868 | 11.2285 | 11.3337 | 11.4231 |  | 0.018301
Electrona | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.66712 | 0.7016 | 0.71266 | 0.73114 | 0.75279 | 0.77725 | 0.79798 | 0.82192 | 0.83275 | 0.84339 | 0.8513 | 0.85801
Electrona | Maximum demand (non-peak season) (MVA) | 8.9067 | 9.367 | 9.5147 | 9.7614 | 10.0504 | 10.377 | 10.6537 | 10.9734 | 11.118 | 11.2601 | 11.3656 | 11.4553
Electrona | Hours exceeding 95% of maximum demand | 12.5
Electrona | Hours exceeding Firm capacity (continuous rating) | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5 | 4736.5
Electrona | Hours exceeding Firm capacity (short-term rating) | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732 | 4732
Electrona | Regional Diversity Factor (Summer) | 0.99316
Electrona | Regional Diversity Factor (Winter) | 0.96119
Electrona | Load transfer capacity (MVA)1 | 8 | [11 empty] | Kingston
Electrona | Load transfer capacity (MVA)2 | 3 | [11 empty] | Knights Road
Electrona | Load transfer capacity (MVA)3
Electrona | Load transfer capacity (MVA)4
Electrona | Load transfer capacity (MVA)5
Electrona | Embedded generation capacity (MVA) Units less than 100 kVA | 20.258
Electrona | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
George Town | Substation capacity (winter and summer) (MVA) Total | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | Winter
George Town | Substation capacity (winter and summer) (MVA) Firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
George Town | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
George Town | Maximum demand (peak season) (MW) | 18.8071 | 18.9284 | 18.9246 | 19.1655 | 19.5091 | 19.9175 | 20.2734 | 20.5428 | 20.6711 | 20.7805 | 20.8525 | 21.0498
George Town | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.44915 | 0.45205 | 0.45196 | 0.45771 | 0.46592 | 0.47567 | 0.48417 | 0.49061 | 0.49367 | 0.49628 | 0.498 | 0.50272
George Town | Maximum demand (peak season) (MVA) | 18.8125 | 18.9338 | 18.93 | 19.171 | 19.5146 | 19.9232 | 20.2792 | 20.5487 | 20.677 | 20.7864 | 20.8584 | 21.0559
George Town | Maximum demand (peak season) Power factor (coincident) | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971
George Town | Maximum demand (non-peak season) (MW) | 10.8329 | 11.3928 | 11.5724 | 11.8725 | 12.224 | 12.6212 | 12.9578 | 13.3466 | 13.5225 | 13.6953 | 13.8236 | 13.9327 |  | 0.018301
George Town | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.92754 | 0.97548 | 0.99086 | 1.0165 | 1.0466 | 1.0807 | 1.1095 | 1.1428 | 1.1578 | 1.1726 | 1.1836 | 1.1929
George Town | Maximum demand (non-peak season) (MVA) | 10.8725 | 11.4345 | 11.6148 | 11.9159 | 12.2687 | 12.6674 | 13.0052 | 13.3954 | 13.572 | 13.7454 | 13.8742 | 13.9836
George Town | Hours exceeding 95% of maximum demand | 4
George Town | Hours exceeding Firm capacity (continuous rating) | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713
George Town | Hours exceeding Firm capacity (short-term rating) | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713 | 4713
George Town | Regional Diversity Factor (Summer) | 0.884
George Town | Regional Diversity Factor (Winter) | 0.98843
George Town | Load transfer capacity (MVA)1 | 2.1 | [11 empty] | Scottsdale
George Town | Load transfer capacity (MVA)2 | 2.1 | [11 empty] | Trevallyn
George Town | Load transfer capacity (MVA)3 | 2.1 | [11 empty] | Mowbray
George Town | Load transfer capacity (MVA)4
George Town | Load transfer capacity (MVA)5
George Town | Embedded generation capacity (MVA) Units less than 100 kVA | 18.704
George Town | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Hadspen | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Hadspen | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hadspen | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hadspen | Maximum demand (peak season) (MW) | 56.613 | 56.978 | 56.9665 | 57.6918 | 58.7259 | 59.9554 | 61.0268 | 61.8377 | 62.2238 | 62.5531 | 62.7699 | 63.3639
Hadspen | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.3238 | 1.3323 | 1.3321 | 1.349 | 1.3732 | 1.402 | 1.427 | 1.446 | 1.455 | 1.4627 | 1.4678 | 1.4817
Hadspen | Maximum demand (peak season) (MVA) | 56.6285 | 56.9936 | 56.9821 | 57.7076 | 58.7419 | 59.9718 | 61.0434 | 61.8547 | 62.2408 | 62.5702 | 62.787 | 63.3813
Hadspen | Maximum demand (peak season) Power factor (coincident) | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973
Hadspen | Maximum demand (non-peak season) (MW) | 34.3141 | 36.0877 | 36.6565 | 37.607 | 38.7205 | 39.9786 | 41.0448 | 42.2763 | 42.8336 | 43.3809 | 43.7873 | 44.1329 |  | 0.018301
Hadspen | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.356 | 1.4261 | 1.4485 | 1.4861 | 1.5301 | 1.5798 | 1.6219 | 1.6706 | 1.6926 | 1.7143 | 1.7303 | 1.744
Hadspen | Maximum demand (non-peak season) (MVA) | 34.3409 | 36.1158 | 36.6852 | 37.6364 | 38.7507 | 40.0098 | 41.0769 | 42.3093 | 42.867 | 43.4147 | 43.8215 | 44.1673
Hadspen | Hours exceeding 95% of maximum demand | 1.5
Hadspen | Hours exceeding Firm capacity (continuous rating) | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5 | 4916.5
Hadspen | Hours exceeding Firm capacity (short-term rating) | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827 | 4827
Hadspen | Regional Diversity Factor (Summer) | 1
Hadspen | Regional Diversity Factor (Winter) | 0.99582
Hadspen | Load transfer capacity (MVA)1 | 26.7 | [11 empty] | Trevallyn
Hadspen | Load transfer capacity (MVA)2 | 13.4 | [11 empty] | Norwood
Hadspen | Load transfer capacity (MVA)3 | 5.3 | [11 empty] | Palmerston
Hadspen | Load transfer capacity (MVA)4
Hadspen | Load transfer capacity (MVA)5
Hadspen | Embedded generation capacity (MVA) Units less than 100 kVA | 32.642
Hadspen | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.043
Huon River | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Huon River | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Huon River | Maximum demand (peak season) (MW) | 0.71774 | 0.72237 | 0.72222 | 0.73142 | 0.74453 | 0.76012 | 0.7737 | 0.78398 | 0.78887 | 0.79305 | 0.7958 | 0.80333
Huon River | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.80537 | 0.81057 | 0.8104 | 0.82072 | 0.83543 | 0.85292 | 0.86816 | 0.8797 | 0.88519 | 0.88988 | 0.89296 | 0.90141
Huon River | Maximum demand (peak season) (MVA) | 1.0788 | 1.0857 | 1.0855 | 1.0993 | 1.119 | 1.1425 | 1.1629 | 1.1783 | 1.1857 | 1.192 | 1.1961 | 1.2074
Huon River | Maximum demand (peak season) Power factor (coincident) | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532 | 0.66532
Huon River | Maximum demand (non-peak season) (MW) | 0.61083 | 0.6424 | 0.65253 | 0.66945 | 0.68927 | 0.71167 | 0.73064 | 0.75257 | 0.76249 | 0.77223 | 0.77946 | 0.78561 |  | 0.018301
Huon River | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.73141 | 0.76922 | 0.78134 | 0.8016 | 0.82534 | 0.85215 | 0.87488 | 0.90113 | 0.91301 | 0.92467 | 0.93334 | 0.9407
Huon River | Maximum demand (non-peak season) (MVA) | 0.95293 | 1.0022 | 1.018 | 1.0444 | 1.0753 | 1.1102 | 1.1398 | 1.174 | 1.1895 | 1.2047 | 1.216 | 1.2256
Huon River | Hours exceeding 95% of maximum demand | 52.5
Huon River | Hours exceeding Firm capacity (continuous rating) | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748
Huon River | Hours exceeding Firm capacity (short-term rating) | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748 | 8748
Huon River | Regional Diversity Factor (Summer) | 0.83697
Huon River | Regional Diversity Factor (Winter) | 0.75717
Huon River | Load transfer capacity (MVA)1
Huon River | Load transfer capacity (MVA)2
Huon River | Load transfer capacity (MVA)3
Huon River | Load transfer capacity (MVA)4
Huon River | Load transfer capacity (MVA)5
Huon River | Embedded generation capacity (MVA) Units less than 100 kVA | 0.012
Huon River | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Kermandie | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Kermandie | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Kermandie | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Kermandie | Maximum demand (peak season) (MW) | 8.5108 | 8.5657 | 8.564 | 8.673 | 8.8285 | 9.0133 | 9.1744 | 9.2963 | 9.3543 | 9.4038 | 9.4364 | 9.5257
Kermandie | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.0946 | 1.1017 | 1.1014 | 1.1155 | 1.1355 | 1.1592 | 1.18 | 1.1956 | 1.2031 | 1.2095 | 1.2137 | 1.2251
Kermandie | Maximum demand (peak season) (MVA) | 8.581 | 8.6363 | 8.6345 | 8.7445 | 8.9012 | 9.0876 | 9.25 | 9.3729 | 9.4314 | 9.4813 | 9.5142 | 9.6042
Kermandie | Maximum demand (peak season) Power factor (coincident) | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183 | 0.99183
Kermandie | Maximum demand (non-peak season) (MW) | 6.6328 | 6.9756 | 7.0856 | 7.2693 | 7.4845 | 7.7277 | 7.9338 | 8.1719 | 8.2796 | 8.3854 | 8.464 | 8.5307 |  | 0.018301
Kermandie | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.3702 | 1.441 | 1.4637 | 1.5017 | 1.5461 | 1.5964 | 1.639 | 1.6881 | 1.7104 | 1.7322 | 1.7485 | 1.7623
Kermandie | Maximum demand (non-peak season) (MVA) | 6.7728 | 7.1229 | 7.2352 | 7.4228 | 7.6426 | 7.8909 | 8.1013 | 8.3444 | 8.4544 | 8.5624 | 8.6427 | 8.7109
Kermandie | Hours exceeding 95% of maximum demand | 11.5
Kermandie | Hours exceeding Firm capacity (continuous rating) | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811
Kermandie | Hours exceeding Firm capacity (short-term rating) | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811 | 4811
Kermandie | Regional Diversity Factor (Summer) | 0.96533
Kermandie | Regional Diversity Factor (Winter) | 0.96604
Kermandie | Load transfer capacity (MVA)1 | 4.4 | [11 empty] | Knights Road
Kermandie | Load transfer capacity (MVA)2
Kermandie | Load transfer capacity (MVA)3
Kermandie | Load transfer capacity (MVA)4
Kermandie | Load transfer capacity (MVA)5
Kermandie | Embedded generation capacity (MVA) Units less than 100 kVA | 8.18
Kermandie | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Kingston 11kV | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Kingston 11kV | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Kingston 11kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Kingston 11kV | Maximum demand (peak season) (MW) | 26.3672 | 26.5372 | 26.5319 | 26.8697 | 27.3513 | 27.9239 | 28.4229 | 28.8006 | 28.9804 | 29.1338 | 29.2348 | 29.5115
Kingston 11kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.14537 | 0.14631 | 0.14628 | 0.14814 | 0.1508 | 0.15395 | 0.15671 | 0.15879 | 0.15978 | 0.16063 | 0.16118 | 0.16271
Kingston 11kV | Maximum demand (peak season) (MVA) | 26.3676 | 26.5376 | 26.5323 | 26.8701 | 27.3517 | 27.9243 | 28.4233 | 28.8011 | 28.9809 | 29.1342 | 29.2352 | 29.5119
Kingston 11kV | Maximum demand (peak season) Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Kingston 11kV | Maximum demand (non-peak season) (MW) | 12.2529 | 12.8862 | 13.0893 | 13.4287 | 13.8263 | 14.2756 | 14.6563 | 15.096 | 15.295 | 15.4904 | 15.6356 | 15.759 |  | 0.018301
Kingston 11kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.87672 | 0.92204 | 0.93657 | 0.96085 | 0.9893 | 1.0214 | 1.0487 | 1.0802 | 1.0944 | 1.1084 | 1.1188 | 1.1276
Kingston 11kV | Maximum demand (non-peak season) (MVA) | 12.2842 | 12.9191 | 13.1228 | 13.463 | 13.8616 | 14.3121 | 14.6937 | 15.1346 | 15.3341 | 15.53 | 15.6756 | 15.7992
Kingston 11kV | Hours exceeding 95% of maximum demand | 4
Kingston 11kV | Hours exceeding Firm capacity (continuous rating) | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5 | 4805.5
Kingston 11kV | Hours exceeding Firm capacity (short-term rating) | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804 | 4804
Kingston 11kV | Regional Diversity Factor (Summer) | 0.93731
Kingston 11kV | Regional Diversity Factor (Winter) | 1
Kingston 11kV | Load transfer capacity (MVA)1
Kingston 11kV | Load transfer capacity (MVA)2
Kingston 11kV | Load transfer capacity (MVA)3
Kingston 11kV | Load transfer capacity (MVA)4
Kingston 11kV | Load transfer capacity (MVA)5
Kingston 11kV | Embedded generation capacity (MVA) Units less than 100 kVA | 22.799
Kingston 11kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.005
Kingston 33kV | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Kingston 33kV | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kingston 33kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Kingston 33kV | Maximum demand (peak season) (MW) | 10.9108 | 10.9811 | 10.9789 | 11.1187 | 11.318 | 11.5549 | 11.7614 | 11.9177 | 11.9921 | 12.0556 | 12.0974 | 12.2119
Kingston 33kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.93225 | 0.93827 | 0.93808 | 0.95002 | 0.96705 | 0.98729 | 1.0049 | 1.0183 | 1.0246 | 1.0301 | 1.0336 | 1.0434
Kingston 33kV | Maximum demand (peak season) (MVA) | 10.9505 | 11.0211 | 11.0189 | 11.1592 | 11.3592 | 11.5971 | 11.8043 | 11.9612 | 12.0358 | 12.0995 | 12.1415 | 12.2564
Kingston 33kV | Maximum demand (peak season) Power factor (coincident) | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637 | 0.99637
Kingston 33kV | Maximum demand (non-peak season) (MW) | 4.8757 | 5.1277 | 5.2085 | 5.3436 | 5.5018 | 5.6806 | 5.8321 | 6.007 | 6.0862 | 6.164 | 6.2217 | 6.2708 |  | 0.018301
Kingston 33kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.13295 | 0.13982 | 0.14202 | 0.1457 | 0.15002 | 0.15489 | 0.15902 | 0.16379 | 0.16595 | 0.16807 | 0.16965 | 0.17099
Kingston 33kV | Maximum demand (non-peak season) (MVA) | 4.8775 | 5.1296 | 5.2105 | 5.3456 | 5.5038 | 5.6827 | 5.8342 | 6.0093 | 6.0885 | 6.1663 | 6.2241 | 6.2732
Kingston 33kV | Hours exceeding 95% of maximum demand | 7
Kingston 33kV | Hours exceeding Firm capacity (continuous rating) | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5
Kingston 33kV | Hours exceeding Firm capacity (short-term rating) | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823 | 4823
Kingston 33kV | Regional Diversity Factor (Summer) | 0.9369
Kingston 33kV | Regional Diversity Factor (Winter) | 0.94758
Kingston 33kV | Load transfer capacity (MVA)1
Kingston 33kV | Load transfer capacity (MVA)2
Kingston 33kV | Load transfer capacity (MVA)3
Kingston 33kV | Load transfer capacity (MVA)4
Kingston 33kV | Load transfer capacity (MVA)5
Kingston 33kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Kingston 33kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Knights Road | Substation capacity (winter and summer) (MVA) Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Knights Road | Substation capacity (winter and summer) (MVA) Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Knights Road | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Knights Road | Maximum demand (peak season) (MW) | 19.5009 | 19.6267 | 19.6227 | 19.8726 | 20.2288 | 20.6523 | 21.0213 | 21.3007 | 21.4336 | 21.5471 | 21.6218 | 21.8264
Knights Road | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9971 | 2.01 | 2.0096 | 2.0352 | 2.0716 | 2.115 | 2.1528 | 2.1814 | 2.195 | 2.2067 | 2.2143 | 2.2353
Knights Road | Maximum demand (peak season) (MVA) | 19.6029 | 19.7293 | 19.7254 | 19.9765 | 20.3346 | 20.7603 | 21.1313 | 21.4121 | 21.5457 | 21.6598 | 21.7348 | 21.9405
Knights Road | Maximum demand (peak season) Power factor (coincident) | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948 | 0.9948
Knights Road | Maximum demand (non-peak season) (MW) | 13.1525 | 13.8323 | 14.0504 | 14.4147 | 14.8415 | 15.3237 | 15.7324 | 16.2044 | 16.418 | 16.6278 | 16.7836 | 16.916 |  | 0.018301
Knights Road | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.237 | 2.3526 | 2.3897 | 2.4516 | 2.5242 | 2.6062 | 2.6758 | 2.756 | 2.7924 | 2.828 | 2.8545 | 2.8771
Knights Road | Maximum demand (non-peak season) (MVA) | 13.3414 | 14.031 | 14.2521 | 14.6217 | 15.0546 | 15.5438 | 15.9583 | 16.4371 | 16.6538 | 16.8666 | 17.0246 | 17.1589
Knights Road | Hours exceeding 95% of maximum demand | 17
Knights Road | Hours exceeding Firm capacity (continuous rating) | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859 | 4859
Knights Road | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Knights Road | Regional Diversity Factor (Summer) | 0.95494
Knights Road | Regional Diversity Factor (Winter) | 1
Knights Road | Load transfer capacity (MVA)1 | 1.7 | [11 empty] | Electrona
Knights Road | Load transfer capacity (MVA)2 | 3.4 | [11 empty] | Kermandie
Knights Road | Load transfer capacity (MVA)3 | 1.7 | [11 empty] | Kingston
Knights Road | Load transfer capacity (MVA)4
Knights Road | Load transfer capacity (MVA)5
Knights Road | Embedded generation capacity (MVA) Units less than 100 kVA | 16.562
Knights Road | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Lindisfarne | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Lindisfarne | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Lindisfarne | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Lindisfarne | Maximum demand (peak season) (MW) | 37.1821 | 37.4219 | 37.4143 | 37.8907 | 38.5698 | 39.3774 | 40.081 | 40.6137 | 40.8672 | 41.0835 | 41.2259 | 41.616
Lindisfarne | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9724 | 1.9852 | 1.9848 | 2.01 | 2.0461 | 2.0889 | 2.1262 | 2.1545 | 2.1679 | 2.1794 | 2.187 | 2.2077
Lindisfarne | Maximum demand (peak season) (MVA) | 37.2344 | 37.4745 | 37.4669 | 37.944 | 38.6241 | 39.4327 | 40.1374 | 40.6708 | 40.9246 | 41.1412 | 41.2838 | 41.6745
Lindisfarne | Maximum demand (peak season) Power factor (coincident) | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986
Lindisfarne | Maximum demand (non-peak season) (MW) | 18.2318 | 19.1742 | 19.4764 | 19.9814 | 20.573 | 21.2415 | 21.808 | 22.4623 | 22.7584 | 23.0492 | 23.2652 | 23.4487 |  | 0.018301
Lindisfarne | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.33228 | 0.34945 | 0.35496 | 0.36416 | 0.37495 | 0.38713 | 0.39745 | 0.40938 | 0.41478 | 0.42008 | 0.42401 | 0.42736
Lindisfarne | Maximum demand (non-peak season) (MVA) | 18.2348 | 19.1773 | 19.4796 | 19.9847 | 20.5764 | 21.245 | 21.8116 | 22.4661 | 22.7622 | 23.053 | 23.269 | 23.4526
Lindisfarne | Hours exceeding 95% of maximum demand | 9.5
Lindisfarne | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Lindisfarne | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Lindisfarne | Regional Diversity Factor (Summer) | 1
Lindisfarne | Regional Diversity Factor (Winter) | 1
Lindisfarne | Load transfer capacity (MVA)1
Lindisfarne | Load transfer capacity (MVA)2
Lindisfarne | Load transfer capacity (MVA)3
Lindisfarne | Load transfer capacity (MVA)4
Lindisfarne | Load transfer capacity (MVA)5
Lindisfarne | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Lindisfarne | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Meadowbank | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Summer
Meadowbank | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | Maximum demand (peak season) (MW) | 6.6837 | 7.0291 | 15.7316 | 16.1395 | 16.6173 | 17.1573 | 17.6148 | 18.1434 | 18.3825 | 18.6174 | 18.7918 | 18.9401
Meadowbank | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.0035 | 2.107 | 4.7156 | 4.8379 | 4.9811 | 5.143 | 5.2801 | 5.4385 | 5.5102 | 5.5806 | 5.6329 | 5.6774
Meadowbank | Maximum demand (peak season) (MVA) | 6.9775 | 7.3381 | 16.4231 | 16.849 | 17.3478 | 17.9115 | 18.3892 | 18.9409 | 19.1906 | 19.4358 | 19.6179 | 19.7727
Meadowbank | Maximum demand (peak season) Power factor (coincident) | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789 | 0.95789
Meadowbank | Maximum demand (non-peak season) (MW) | 4.423 | 4.4515 | 13.6996 | 13.874 | 14.1227 | 14.4183 | 14.676 | 14.871 | 14.9638 | 15.043 | 15.0952 | 15.238 |  | 0.018301
Meadowbank | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.30471 | 0.30667 | 0.94379 | 0.9558 | 0.97294 | 0.99331 | 1.0111 | 1.0245 | 1.0309 | 1.0363 | 1.0399 | 1.0498
Meadowbank | Maximum demand (non-peak season) (MVA) | 4.4335 | 4.4621 | 13.732 | 13.9069 | 14.1561 | 14.4525 | 14.7108 | 14.9063 | 14.9993 | 15.0787 | 15.131 | 15.2742
Meadowbank | Hours exceeding 95% of maximum demand | 17.5
Meadowbank | Hours exceeding Firm capacity (continuous rating) | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681
Meadowbank | Hours exceeding Firm capacity (short-term rating) | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681 | 8681
Meadowbank | Regional Diversity Factor (Summer) | 0.80781
Meadowbank | Regional Diversity Factor (Winter) | 0.76365
Meadowbank | Load transfer capacity (MVA)1 | 3.4 | [11 empty] | New Norfolk
Meadowbank | Load transfer capacity (MVA)2 | 0.5 | [11 empty] | Wayatinah Zone
Meadowbank | Load transfer capacity (MVA)3
Meadowbank | Load transfer capacity (MVA)4
Meadowbank | Load transfer capacity (MVA)5
Meadowbank | Embedded generation capacity (MVA) Units less than 100 kVA | 1.743
Meadowbank | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Mornington | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Mornington | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Mornington | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Mornington | Maximum demand (peak season) (MW) | 40.4191 | 40.6797 | 40.6715 | 41.1893 | 41.9276 | 42.8054 | 43.5703 | 44.1493 | 44.4249 | 44.6601 | 44.8148 | 45.239
Mornington | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.2332 | 2.2476 | 2.2471 | 2.2757 | 2.3165 | 2.365 | 2.4073 | 2.4393 | 2.4545 | 2.4675 | 2.476 | 2.4995
Mornington | Maximum demand (peak season) (MVA) | 40.4807 | 40.7418 | 40.7335 | 41.2521 | 41.9915 | 42.8707 | 43.6368 | 44.2167 | 44.4927 | 44.7282 | 44.8832 | 45.308
Mornington | Maximum demand (peak season) Power factor (coincident) | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848 | 0.99848
Mornington | Maximum demand (non-peak season) (MW) | 19.7185 | 20.7377 | 21.0646 | 21.6108 | 22.2506 | 22.9736 | 23.5863 | 24.294 | 24.6142 | 24.9287 | 25.1623 | 25.3608 |  | 0.018301
Mornington | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.2343 | 1.2981 | 1.3186 | 1.3528 | 1.3928 | 1.4381 | 1.4764 | 1.5207 | 1.5408 | 1.5605 | 1.5751 | 1.5875
Mornington | Maximum demand (non-peak season) (MVA) | 19.7571 | 20.7783 | 21.1058 | 21.6531 | 22.2942 | 23.0186 | 23.6325 | 24.3415 | 24.6624 | 24.9775 | 25.2115 | 25.4105
Mornington | Hours exceeding 95% of maximum demand | 3.5
Mornington | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Mornington | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Mornington | Regional Diversity Factor (Summer) | 1
Mornington | Regional Diversity Factor (Winter) | 1
Mornington | Load transfer capacity (MVA)1
Mornington | Load transfer capacity (MVA)2
Mornington | Load transfer capacity (MVA)3
Mornington | Load transfer capacity (MVA)4
Mornington | Load transfer capacity (MVA)5
Mornington | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Mornington | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Mowbray | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Mowbray | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Mowbray | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Mowbray | Maximum demand (peak season) (MW) | 37.7013 | 37.9444 | 37.9367 | 38.4197 | 39.1084 | 39.9272 | 40.6406 | 41.1807 | 41.4378 | 41.6571 | 41.8015 | 42.1971
Mowbray | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.827 | 2.8452 | 2.8447 | 2.8809 | 2.9325 | 2.9939 | 3.0474 | 3.0879 | 3.1072 | 3.1236 | 3.1345 | 3.1641
Mowbray | Maximum demand (peak season) (MVA) | 37.8071 | 38.0509 | 38.0432 | 38.5276 | 39.2182 | 40.0392 | 40.7547 | 41.2963 | 41.5541 | 41.774 | 41.9188 | 42.3156
Mowbray | Maximum demand (peak season) Power factor (coincident) | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972 | 0.9972
Mowbray | Maximum demand (non-peak season) (MW) | 17.7798 | 18.6987 | 18.9935 | 19.486 | 20.0629 | 20.7148 | 21.2673 | 21.9054 | 22.1941 | 22.4777 | 22.6883 | 22.8673 |  | 0.018301
Mowbray | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 2.5834 | 2.717 | 2.7598 | 2.8314 | 2.9152 | 3.0099 | 3.0902 | 3.1829 | 3.2249 | 3.2661 | 3.2967 | 3.3227
Mowbray | Maximum demand (non-peak season) (MVA) | 17.9665 | 18.8951 | 19.193 | 19.6906 | 20.2736 | 20.9324 | 21.4906 | 22.1354 | 22.4272 | 22.7137 | 22.9266 | 23.1075
Mowbray | Hours exceeding 95% of maximum demand | 3.5
Mowbray | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Mowbray | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Mowbray | Regional Diversity Factor (Summer) | 0.93537
Mowbray | Regional Diversity Factor (Winter) | 0.97894
Mowbray | Load transfer capacity (MVA)1 | 31.4 | [11 empty] | Trevallyn
Mowbray | Load transfer capacity (MVA)2 | 6.3 | [11 empty] | Norwood
Mowbray | Load transfer capacity (MVA)3
Mowbray | Load transfer capacity (MVA)4
Mowbray | Load transfer capacity (MVA)5
Mowbray | Embedded generation capacity (MVA) Units less than 100 kVA | 12.604
Mowbray | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
North Hobart | Substation capacity (winter and summer) (MVA) Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
North Hobart | Substation capacity (winter and summer) (MVA) Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
North Hobart | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
North Hobart | Maximum demand (peak season) (MW) | 36.7547 | 36.9917 | 36.9843 | 37.4552 | 38.1265 | 38.9247 | 39.6203 | 40.1468 | 40.3974 | 40.6112 | 40.752 | 41.1377
North Hobart | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9572 | 1.9698 | 1.9694 | 1.9945 | 2.0302 | 2.0727 | 2.1098 | 2.1378 | 2.1511 | 2.1625 | 2.17 | 2.1905
North Hobart | Maximum demand (peak season) (MVA) | 36.8068 | 37.0442 | 37.0367 | 37.5082 | 38.1805 | 38.9799 | 39.6764 | 40.2037 | 40.4547 | 40.6688 | 40.8097 | 41.1959
North Hobart | Maximum demand (peak season) Power factor (coincident) | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859 | 0.99859
North Hobart | Maximum demand (non-peak season) (MW) | 16.7929 | 17.6608 | 17.9392 | 18.4044 | 18.9493 | 19.565 | 20.0868 | 20.6895 | 20.9622 | 21.23 | 21.4289 | 21.598 |  | 8.072
North Hobart | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.9783 | 2.0805 | 2.1133 | 2.1681 | 2.2323 | 2.3048 | 2.3663 | 2.4373 | 2.4694 | 2.501 | 2.5244 | 2.5443
North Hobart | Maximum demand (non-peak season) (MVA) | 16.909 | 17.7829 | 18.0633 | 18.5316 | 19.0803 | 19.7003 | 20.2257 | 20.8325 | 21.1071 | 21.3768 | 21.5771 | 21.7474
North Hobart | Hours exceeding 95% of maximum demand | 7
North Hobart | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
North Hobart | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
North Hobart | Regional Diversity Factor (Summer) | 0.88363
North Hobart | Regional Diversity Factor (Winter) | 1
North Hobart | Load transfer capacity (MVA)1
North Hobart | Load transfer capacity (MVA)2
North Hobart | Load transfer capacity (MVA)3
North Hobart | Load transfer capacity (MVA)4
North Hobart | Load transfer capacity (MVA)5
North Hobart | Embedded generation capacity (MVA) Units less than 100 kVA | 14.614
North Hobart | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.06
New Norfolk | Substation capacity (winter and summer) (MVA) Total | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Winter
New Norfolk | Substation capacity (winter and summer) (MVA) Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
New Norfolk | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
New Norfolk | Maximum demand (peak season) (MW) | 17.7724 | 17.887 | 17.8834 | 18.1111 | 18.4357 | 18.8217 | 19.158 | 19.4126 | 19.5338 | 19.6372 | 19.7052 | 19.8917
New Norfolk | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.19372 | 0.19497 | 0.19493 | 0.19741 | 0.20095 | 0.20516 | 0.20882 | 0.2116 | 0.21292 | 0.21404 | 0.21479 | 0.21682
New Norfolk | Maximum demand (peak season) (MVA) | 17.7735 | 17.8881 | 17.8844 | 18.1122 | 18.4368 | 18.8228 | 19.1591 | 19.4138 | 19.5349 | 19.6383 | 19.7064 | 19.8929
New Norfolk | Maximum demand (peak season) Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
New Norfolk | Maximum demand (non-peak season) (MW) | 12.0862 | 12.7109 | 12.9113 | 13.2461 | 13.6382 | 14.0814 | 14.4569 | 14.8907 | 15.087 | 15.2797 | 15.4229 | 15.5446 |  | 9.3796
New Norfolk | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.99735 | 1.0489 | 1.0654 | 1.0931 | 1.1254 | 1.162 | 1.193 | 1.2288 | 1.245 | 1.2609 | 1.2727 | 1.2827
New Norfolk | Maximum demand (non-peak season) (MVA) | 12.1273 | 12.7541 | 12.9552 | 13.2911 | 13.6846 | 14.1293 | 14.5061 | 14.9413 | 15.1383 | 15.3317 | 15.4753 | 15.5974
New Norfolk | Hours exceeding 95% of maximum demand | 19
New Norfolk | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
New Norfolk | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
New Norfolk | Regional Diversity Factor (Summer) | 0.98903
New Norfolk | Regional Diversity Factor (Winter) | 0.90236
New Norfolk | Load transfer capacity (MVA)1 | 6.6 | [11 empty] | Meadowbank
New Norfolk | Load transfer capacity (MVA)2
New Norfolk | Load transfer capacity (MVA)3
New Norfolk | Load transfer capacity (MVA)4
New Norfolk | Load transfer capacity (MVA)5
New Norfolk | Embedded generation capacity (MVA) Units less than 100 kVA | 5.83
New Norfolk | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Newton | Substation capacity (winter and summer) (MVA) Total | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 |  | Winter
Newton | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Newton | Maximum demand (peak season) (MW) | 4.1058 | 4.1323 | 4.1315 | 4.1841 | 4.2591 | 4.3482 | 4.4259 | 4.4847 | 4.5127 | 4.5366 | 4.5524 | 4.5954
Newton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.056548 | 0.056913 | 0.056901 | 0.057626 | 0.058659 | 0.059887 | 0.060957 | 0.061767 | 0.062153 | 0.062482 | 0.062698 | 0.063292
Newton | Maximum demand (peak season) (MVA) | 4.1062 | 4.1327 | 4.1319 | 4.1845 | 4.2595 | 4.3486 | 4.4264 | 4.4852 | 4.5132 | 4.5371 | 4.5528 | 4.5959
Newton | Maximum demand (peak season) Power factor (coincident) | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99991
Newton | Maximum demand (non-peak season) (MW) | 3.3228 | 3.4946 | 3.5497 | 3.6417 | 3.7495 | 3.8714 | 3.9746 | 4.0939 | 4.1478 | 4.2008 | 4.2402 | 4.2737 |  | 9.3796
Newton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.24665 | 0.2594 | 0.26348 | 0.27032 | 0.27832 | 0.28736 | 0.29503 | 0.30388 | 0.30788 | 0.31182 | 0.31474 | 0.31722
Newton | Maximum demand (non-peak season) (MVA) | 3.332 | 3.5042 | 3.5594 | 3.6517 | 3.7599 | 3.882 | 3.9856 | 4.1051 | 4.1592 | 4.2124 | 4.2519 | 4.2854
Newton | Hours exceeding 95% of maximum demand | 1.5
Newton | Hours exceeding Firm capacity (continuous rating) | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5
Newton | Hours exceeding Firm capacity (short-term rating) | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5 | 8745.5
Newton | Regional Diversity Factor (Summer) | 0.85116
Newton | Regional Diversity Factor (Winter) | 0.88727
Newton | Load transfer capacity (MVA)1
Newton | Load transfer capacity (MVA)2
Newton | Load transfer capacity (MVA)3
Newton | Load transfer capacity (MVA)4
Newton | Load transfer capacity (MVA)5
Newton | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Newton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Norwood | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Norwood | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Norwood | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Norwood | Maximum demand (peak season) (MW) | 30.7146 | 30.9127 | 30.9065 | 31.3 | 31.861 | 32.528 | 33.1093 | 33.5493 | 33.7587 | 33.9374 | 34.055 | 34.3773
Norwood | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.20101 | 0.20231 | 0.20226 | 0.20484 | 0.20851 | 0.21288 | 0.21668 | 0.21956 | 0.22093 | 0.2221 | 0.22287 | 0.22498
Norwood | Maximum demand (peak season) (MVA) | 30.7153 | 30.9134 | 30.9071 | 31.3006 | 31.8617 | 32.5287 | 33.11 | 33.55 | 33.7594 | 33.9381 | 34.0557 | 34.378
Norwood | Maximum demand (peak season) Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Norwood | Maximum demand (non-peak season) (MW) | 16.2809 | 17.1224 | 17.3923 | 17.8433 | 18.3716 | 18.9686 | 19.4744 | 20.0588 | 20.3231 | 20.5828 | 20.7757 | 20.9396 |  | 9.3796
Norwood | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.028232 | 0.029691 | 0.030159 | 0.030941 | 0.031857 | 0.032892 | 0.033769 | 0.034782 | 0.035241 | 0.035691 | 0.036026 | 0.03631
Norwood | Maximum demand (non-peak season) (MVA) | 16.2809 | 17.1225 | 17.3924 | 17.8433 | 18.3716 | 18.9686 | 19.4745 | 20.0588 | 20.3232 | 20.5828 | 20.7757 | 20.9396
Norwood | Hours exceeding 95% of maximum demand | 1
Norwood | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Norwood | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Norwood | Regional Diversity Factor (Summer) | 1
Norwood | Regional Diversity Factor (Winter) | 0.96163
Norwood | Load transfer capacity (MVA)1 | 16.2 | [11 empty] | Trevallyn
Norwood | Load transfer capacity (MVA)2 | 10.8 | [11 empty] | Mowbray
Norwood | Load transfer capacity (MVA)3 | 27 | [11 empty] | St Leonards
Norwood | Load transfer capacity (MVA)4 | 16.2 | [11 empty] | Hadspen
Norwood | Load transfer capacity (MVA)5
Norwood | Embedded generation capacity (MVA) Units less than 100 kVA | 17.898
Norwood | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.035
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Port Latta (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5
Port Latta (RT) | Maximum demand (peak season) (MW) | 8.6584 | 9.1059 | 9.2494 | 9.4893 | 9.7702 | 10.0877 | 10.3567 | 10.6675 | 10.8081 | 10.9462 | 11.0487 | 11.1359
Port Latta (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 2.944 | 3.0961 | 3.1449 | 3.2265 | 3.322 | 3.43 | 3.5214 | 3.6271 | 3.6749 | 3.7219 | 3.7567 | 3.7864
Port Latta (RT) | Maximum demand (peak season) (MVA) | 9.1452 | 9.6179 | 9.7695 | 10.0228 | 10.3196 | 10.6549 | 10.939 | 11.2672 | 11.4158 | 11.5616 | 11.67 | 11.762
Port Latta (RT) | Maximum demand (peak season) Power factor (coincident) | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677 | 0.94677
Port Latta (RT) | Maximum demand (non-peak season) (MW) | 7.45 | 7.4981 | 7.4965 | 7.592 | 7.7281 | 7.8899 | 8.0309 | 8.1376 | 8.1884 | 8.2317 | 8.2602 | 8.3384 |  | 9.3796
Port Latta (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.28063 | 0.28244 | 0.28238 | 0.28598 | 0.2911 | 0.2972 | 0.30251 | 0.30653 | 0.30844 | 0.31008 | 0.31115 | 0.3141
Port Latta (RT) | Maximum demand (non-peak season) (MVA) | 7.4553 | 7.5034 | 7.5019 | 7.5974 | 7.7336 | 7.8955 | 8.0366 | 8.1434 | 8.1942 | 8.2376 | 8.2661 | 8.3443
Port Latta (RT) | Hours exceeding 95% of maximum demand | 26
Port Latta (RT) | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Port Latta (RT) | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Port Latta (RT) | Regional Diversity Factor (Summer) | 0.76875
Port Latta (RT) | Regional Diversity Factor (Winter) | 0.96743
Port Latta (RT) | Load transfer capacity (MVA)1 | 3.9 | [11 empty] | Burnie
Port Latta (RT) | Load transfer capacity (MVA)2 | 3.9 | [11 empty] | Smithton
Port Latta (RT) | Load transfer capacity (MVA)3
Port Latta (RT) | Load transfer capacity (MVA)4
Port Latta (RT) | Load transfer capacity (MVA)5
Port Latta (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Port Latta (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Palmerston | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Summer
Palmerston | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Palmerston | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Palmerston | Maximum demand (peak season) (MW) | 12.9431 | 13.6121 | 13.8267 | 14.1852 | 14.6052 | 15.0798 | 15.4819 | 15.9465 | 16.1567 | 16.3631 | 16.5164 | 16.6467
Palmerston | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 4.1938 | 4.4106 | 4.4801 | 4.5963 | 4.7324 | 4.8862 | 5.0165 | 5.167 | 5.2351 | 5.302 | 5.3516 | 5.3939
Palmerston | Maximum demand (peak season) (MVA) | 13.6056 | 14.3089 | 14.5344 | 14.9113 | 15.3528 | 15.8516 | 16.2744 | 16.7627 | 16.9836 | 17.2006 | 17.3618 | 17.4988
Palmerston | Maximum demand (peak season) Power factor (coincident) | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131 | 0.95131
Palmerston | Maximum demand (non-peak season) (MW) | 9.3818 | 9.4423 | 9.4404 | 9.5606 | 9.7319 | 9.9357 | 10.1132 | 10.2476 | 10.3116 | 10.3662 | 10.4021 | 10.5005 |  | 9.3796
Palmerston | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.92844 | 0.93443 | 0.93424 | 0.94613 | 0.96309 | 0.98325 | 1.0008 | 1.0141 | 1.0205 | 1.0259 | 1.0294 | 1.0392
Palmerston | Maximum demand (non-peak season) (MVA) | 9.4276 | 9.4884 | 9.4865 | 9.6073 | 9.7795 | 9.9842 | 10.1626 | 10.2977 | 10.362 | 10.4168 | 10.4529 | 10.5518
Palmerston | Hours exceeding 95% of maximum demand | 13.5
Palmerston | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Palmerston | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Palmerston | Regional Diversity Factor (Summer) | 0.8283
Palmerston | Regional Diversity Factor (Winter) | 0.78234
Palmerston | Load transfer capacity (MVA)1 | 2 | [11 empty] | Norwood
Palmerston | Load transfer capacity (MVA)2 | 5 | [11 empty] | Hadspen
Palmerston | Load transfer capacity (MVA)3
Palmerston | Load transfer capacity (MVA)4
Palmerston | Load transfer capacity (MVA)5
Palmerston | Embedded generation capacity (MVA) Units less than 100 kVA | 2.801
Palmerston | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Queenstown | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Queenstown | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Queenstown | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Queenstown | Maximum demand (peak season) (MW) | 5.9564 | 5.9948 | 5.9936 | 6.0699 | 6.1787 | 6.3081 | 6.4208 | 6.5061 | 6.5467 | 6.5814 | 6.6042 | 6.6667
Queenstown | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.066404 | 0.066832 | 0.066818 | 0.067669 | 0.068882 | 0.070324 | 0.071581 | 0.072532 | 0.072985 | 0.073371 | 0.073625 | 0.074322
Queenstown | Maximum demand (peak season) (MVA) | 5.9568 | 5.9952 | 5.994 | 6.0703 | 6.1791 | 6.3085 | 6.4212 | 6.5065 | 6.5472 | 6.5818 | 6.6046 | 6.6671
Queenstown | Maximum demand (peak season) Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Queenstown | Maximum demand (non-peak season) (MW) | 3.4436 | 3.6216 | 3.6786 | 3.774 | 3.8858 | 4.012 | 4.119 | 4.2426 | 4.2985 | 4.3535 | 4.3943 | 4.4289 |  | 9.3796
Queenstown | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.090683 | 0.095371 | 0.096874 | 0.099386 | 0.10233 | 0.10565 | 0.10847 | 0.11173 | 0.1132 | 0.11464 | 0.11572 | 0.11663
Queenstown | Maximum demand (non-peak season) (MVA) | 3.4448 | 3.6228 | 3.6799 | 3.7753 | 3.8871 | 4.0134 | 4.1205 | 4.2441 | 4.3 | 4.355 | 4.3958 | 4.4305
Queenstown | Hours exceeding 95% of maximum demand | 22.5
Queenstown | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Queenstown | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Queenstown | Regional Diversity Factor (Summer) | 0.92005
Queenstown | Regional Diversity Factor (Winter) | 0.87538
Queenstown | Load transfer capacity (MVA)1
Queenstown | Load transfer capacity (MVA)2
Queenstown | Load transfer capacity (MVA)3
Queenstown | Load transfer capacity (MVA)4
Queenstown | Load transfer capacity (MVA)5
Queenstown | Embedded generation capacity (MVA) Units less than 100 kVA | 2.329
Queenstown | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Railton | Substation capacity (winter and summer) (MVA) Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | Winter
Railton | Substation capacity (winter and summer) (MVA) Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Railton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Railton | Maximum demand (peak season) (MW) | 53.5273 | 53.8724 | 53.8616 | 54.5473 | 55.525 | 56.6875 | 57.7005 | 58.4673 | 58.8323 | 59.1436 | 59.3486 | 59.9103
Railton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 10.514 | 10.5818 | 10.5797 | 10.7144 | 10.9064 | 11.1348 | 11.3338 | 11.4844 | 11.5561 | 11.6172 | 11.6575 | 11.7678
Railton | Maximum demand (peak season) (MVA) | 54.5501 | 54.9019 | 54.8908 | 55.5897 | 56.586 | 57.7707 | 58.8031 | 59.5845 | 59.9565 | 60.2738 | 60.4827 | 61.0551
Railton | Maximum demand (peak season) Power factor (coincident) | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125 | 0.98125
Railton | Maximum demand (non-peak season) (MW) | 35.9498 | 37.8079 | 38.4039 | 39.3997 | 40.5662 | 41.8844 | 43.0014 | 44.2916 | 44.8754 | 45.4488 | 45.8746 | 46.2366 |  | 9.3796
Railton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 7.4669 | 7.8528 | 7.9766 | 8.1834 | 8.4257 | 8.6995 | 8.9315 | 9.1995 | 9.3207 | 9.4398 | 9.5283 | 9.6035
Railton | Maximum demand (non-peak season) (MVA) | 36.7171 | 38.6148 | 39.2236 | 40.2406 | 41.432 | 42.7783 | 43.9191 | 45.2369 | 45.8332 | 46.4188 | 46.8537 | 47.2234
Railton | Hours exceeding 95% of maximum demand | 17.5
Railton | Hours exceeding Firm capacity (continuous rating) | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5 | 4830.5
Railton | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Railton | Regional Diversity Factor (Summer) | 0.78059
Railton | Regional Diversity Factor (Winter) | 1
Railton | Load transfer capacity (MVA)1 | 8.7 | [11 empty] | Devonport
Railton | Load transfer capacity (MVA)2 | 4.4 | [11 empty] | Ulverstone
Railton | Load transfer capacity (MVA)3
Railton | Load transfer capacity (MVA)4
Railton | Load transfer capacity (MVA)5
Railton | Embedded generation capacity (MVA) Units less than 100 kVA | 21.624
Railton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.042
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Total | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | Winter
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Rosebery 22kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Rosebery 22kV | Maximum demand (peak season) (MW) | 2.3944 | 2.4099 | 2.4094 | 2.4401 | 2.4838 | 2.5358 | 2.5811 | 2.6154 | 2.6317 | 2.6457 | 2.6548 | 2.68
Rosebery 22kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV | Maximum demand (peak season) (MVA) | 2.3944 | 2.4099 | 2.4094 | 2.4401 | 2.4838 | 2.5358 | 2.5811 | 2.6154 | 2.6317 | 2.6457 | 2.6548 | 2.68
Rosebery 22kV | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2027 to 2036
Rosebery 22kV | Maximum demand (non-peak season) (MW) | 1.2321 | 1.2958 | 1.3163 | 1.3504 | 1.3904 | 1.4355 | 1.4738 | 1.5181 | 1.5381 | 1.5577 | 1.5723 | 1.5847 |  | 9.3796
Rosebery 22kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rosebery 22kV | Maximum demand (non-peak season) (MVA) | 1.2321 | 1.2958 | 1.3163 | 1.3504 | 1.3904 | 1.4355 | 1.4738 | 1.5181 | 1.5381 | 1.5577 | 1.5723 | 1.5847
Rosebery 22kV | Hours exceeding 95% of maximum demand | 2.5
Rosebery 22kV | Hours exceeding Firm capacity (continuous rating) | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5
Rosebery 22kV | Hours exceeding Firm capacity (short-term rating) | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5 | 8752.5
Rosebery 22kV | Regional Diversity Factor (Summer) | 0.58328
Rosebery 22kV | Regional Diversity Factor (Winter) | 0.96808
Rosebery 22kV | Load transfer capacity (MVA)1
Rosebery 22kV | Load transfer capacity (MVA)2
Rosebery 22kV | Load transfer capacity (MVA)3
Rosebery 22kV | Load transfer capacity (MVA)4
Rosebery 22kV | Load transfer capacity (MVA)5
Rosebery 22kV | Embedded generation capacity (MVA) Units less than 100 kVA | 1.195
Rosebery 22kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Total | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | Winter
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Firm delivery | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Rosebery 44kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Rosebery 44kV | Maximum demand (peak season) (MW) | 17.0539 | 17.1639 | 17.1604 | 17.3789 | 17.6904 | 18.0608 | 18.3835 | 18.6278 | 18.7441 | 18.8433 | 18.9086 | 19.0876
Rosebery 44kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 9.7172 | 9.7798 | 9.7779 | 9.9023 | 10.0798 | 10.2909 | 10.4748 | 10.614 | 10.6802 | 10.7367 | 10.774 | 10.8759
Rosebery 44kV | Maximum demand (peak season) (MVA) | 19.6281 | 19.7546 | 19.7506 | 20.0021 | 20.3606 | 20.7869 | 21.1583 | 21.4395 | 21.5733 | 21.6875 | 21.7627 | 21.9687
Rosebery 44kV | Maximum demand (peak season) Power factor (coincident) | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886 | 0.86886
Rosebery 44kV | Maximum demand (non-peak season) (MW) | 13.9079 | 14.6267 | 14.8573 | 15.2425 | 15.6938 | 16.2038 | 16.6359 | 17.1351 | 17.3609 | 17.5827 | 17.7475 | 17.8875 |  | 9.3796
Rosebery 44kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 7.3865 | 7.7683 | 7.8908 | 8.0954 | 8.335 | 8.6059 | 8.8354 | 9.1005 | 9.2204 | 9.3382 | 9.4258 | 9.5001
Rosebery 44kV | Maximum demand (non-peak season) (MVA) | 15.7477 | 16.5616 | 16.8227 | 17.2589 | 17.7699 | 18.3473 | 18.8366 | 19.4018 | 19.6575 | 19.9087 | 20.0952 | 20.2538
Rosebery 44kV | Hours exceeding 95% of maximum demand | 523
Rosebery 44kV | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Rosebery 44kV | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Rosebery 44kV | Regional Diversity Factor (Summer) | 0.81631
Rosebery 44kV | Regional Diversity Factor (Winter) | 0.83391
Rosebery 44kV | Load transfer capacity (MVA)1
Rosebery 44kV | Load transfer capacity (MVA)2
Rosebery 44kV | Load transfer capacity (MVA)3
Rosebery 44kV | Load transfer capacity (MVA)4
Rosebery 44kV | Load transfer capacity (MVA)5
Rosebery 44kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Rosebery 44kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Risdon 33kV | Substation capacity (winter and summer) (MVA) Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Winter
Risdon 33kV | Substation capacity (winter and summer) (MVA) Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Risdon 33kV | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Risdon 33kV | Maximum demand (peak season) (MW) | 67.9432 | 68.3813 | 68.3675 | 69.238 | 70.479 | 71.9545 | 73.2403 | 74.2136 | 74.6769 | 75.0721 | 75.3323 | 76.0453
Risdon 33kV | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 12.1724 | 12.2509 | 12.2485 | 12.4044 | 12.6267 | 12.8911 | 13.1215 | 13.2958 | 13.3788 | 13.4496 | 13.4962 | 13.624
Risdon 33kV | Maximum demand (peak season) (MVA) | 69.025 | 69.4701 | 69.456 | 70.3403 | 71.6011 | 73.1002 | 74.4064 | 75.3952 | 75.8659 | 76.2674 | 76.5317 | 77.256
Risdon 33kV | Maximum demand (peak season) Power factor (coincident) | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433 | 0.98433
Risdon 33kV | Maximum demand (non-peak season) (MW) | 38.7052 | 40.7058 | 41.3474 | 42.4196 | 43.6755 | 45.0947 | 46.2973 | 47.6864 | 48.3149 | 48.9323 | 49.3908 | 49.7805 |  | 9.3796
Risdon 33kV | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 8.2666 | 8.6938 | 8.8309 | 9.0599 | 9.3281 | 9.6312 | 9.8881 | 10.1847 | 10.319 | 10.4508 | 10.5488 | 10.632
Risdon 33kV | Maximum demand (non-peak season) (MVA) | 39.5781 | 41.6238 | 42.28 | 43.3763 | 44.6605 | 46.1117 | 47.3414 | 48.7619 | 49.4046 | 50.0358 | 50.5047 | 50.9032
Risdon 33kV | Hours exceeding 95% of maximum demand | 5.5
Risdon 33kV | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Risdon 33kV | Hours exceeding Firm capacity (short-term rating) | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925 | 4925
Risdon 33kV | Regional Diversity Factor (Summer) | 0.7858
Risdon 33kV | Regional Diversity Factor (Winter) | 0.95396
Risdon 33kV | Load transfer capacity (MVA)1
Risdon 33kV | Load transfer capacity (MVA)2
Risdon 33kV | Load transfer capacity (MVA)3
Risdon 33kV | Load transfer capacity (MVA)4
Risdon 33kV | Load transfer capacity (MVA)5
Risdon 33kV | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Risdon 33kV | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Rokeby | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Rokeby | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Rokeby | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Rokeby | Maximum demand (peak season) (MW) | 23.1812 | 23.3307 | 23.326 | 23.6229 | 24.0464 | 24.5498 | 24.9885 | 25.3206 | 25.4786 | 25.6135 | 25.7022 | 25.9455
Rokeby | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.045289 | 0.045581 | 0.045572 | 0.046152 | 0.046979 | 0.047963 | 0.04882 | 0.049469 | 0.049778 | 0.050041 | 0.050214 | 0.05069
Rokeby | Maximum demand (peak season) (MVA) | 23.1812 | 23.3307 | 23.326 | 23.623 | 24.0464 | 24.5498 | 24.9885 | 25.3206 | 25.4787 | 25.6135 | 25.7023 | 25.9455
Rokeby | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2027 to 2036
Rokeby | Maximum demand (non-peak season) (MW) | 11.1132 | 11.6876 | 11.8718 | 12.1796 | 12.5402 | 12.9477 | 13.293 | 13.6919 | 13.8723 | 14.0496 | 14.1812 | 14.2931 |  | 9.3796
Rokeby | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.68748 | 0.72302 | 0.73441 | 0.75346 | 0.77576 | 0.80097 | 0.82233 | 0.84701 | 0.85817 | 0.86914 | 0.87728 | 0.8842
Rokeby | Maximum demand (non-peak season) (MVA) | 11.1344 | 11.7099 | 11.8945 | 12.2029 | 12.5642 | 12.9725 | 13.3184 | 13.718 | 13.8989 | 14.0764 | 14.2083 | 14.3205
Rokeby | Hours exceeding 95% of maximum demand | 4
Rokeby | Hours exceeding Firm capacity (continuous rating) | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698 | 4698
Rokeby | Hours exceeding Firm capacity (short-term rating) | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693 | 4693
Rokeby | Regional Diversity Factor (Summer) | 0.99563
Rokeby | Regional Diversity Factor (Winter) | 0.96359
Rokeby | Load transfer capacity (MVA)1 | 4.8 | [11 empty] | Howrah Zone
Rokeby | Load transfer capacity (MVA)2 | 4.8 | [11 empty] | Cambridge Zone
Rokeby | Load transfer capacity (MVA)3
Rokeby | Load transfer capacity (MVA)4
Rokeby | Load transfer capacity (MVA)5
Rokeby | Embedded generation capacity (MVA) Units less than 100 kVA | 20.966
Rokeby | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Scottsdale | Substation capacity (winter and summer) (MVA) Total | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 |  | Winter
Scottsdale | Substation capacity (winter and summer) (MVA) Firm delivery | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5
Scottsdale | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
Scottsdale | Maximum demand (peak season) (MW) | 12.4193 | 12.4994 | 12.4969 | 12.656 | 12.8828 | 13.1525 | 13.3876 | 13.5655 | 13.6501 | 13.7224 | 13.7699 | 13.9003
Scottsdale | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.59216 | 0.59598 | 0.59586 | 0.60344 | 0.61426 | 0.62712 | 0.63832 | 0.64681 | 0.65085 | 0.65429 | 0.65656 | 0.66277
Scottsdale | Maximum demand (peak season) (MVA) | 12.4334 | 12.5136 | 12.511 | 12.6703 | 12.8974 | 13.1675 | 13.4028 | 13.5809 | 13.6657 | 13.738 | 13.7856 | 13.9161
Scottsdale | Maximum demand (peak season) Power factor (coincident) | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887 | 0.99887
Scottsdale | Maximum demand (non-peak season) (MW) | 9.7165 | 10.2187 | 10.3798 | 10.6489 | 10.9642 | 11.3205 | 11.6224 | 11.9711 | 12.1289 | 12.2838 | 12.3989 | 12.4968 |  | 9.3796
Scottsdale | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.4352 | 1.5094 | 1.5332 | 1.5729 | 1.6195 | 1.6721 | 1.7167 | 1.7682 | 1.7915 | 1.8144 | 1.8314 | 1.8459
Scottsdale | Maximum demand (non-peak season) (MVA) | 9.8219 | 10.3296 | 10.4924 | 10.7644 | 11.0832 | 11.4433 | 11.7485 | 12.101 | 12.2605 | 12.4171 | 12.5335 | 12.6324
Scottsdale | Hours exceeding 95% of maximum demand | 18
Scottsdale | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Scottsdale | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Scottsdale | Regional Diversity Factor (Summer) | 0.89632
Scottsdale | Regional Diversity Factor (Winter) | 0.99022
Scottsdale | Load transfer capacity (MVA)1 | 4.8 | [11 empty] | Derby
Scottsdale | Load transfer capacity (MVA)2 | 3.2 | [11 empty] | George Town
Scottsdale | Load transfer capacity (MVA)3
Scottsdale | Load transfer capacity (MVA)4
Scottsdale | Load transfer capacity (MVA)5
Scottsdale | Embedded generation capacity (MVA) Units less than 100 kVA | 9.851
Scottsdale | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
Sheffield | Substation capacity (winter and summer) (MVA) Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Sheffield | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sheffield | Maximum demand (peak season) (MW) | 3.0579 | 3.0776 | 3.077 | 3.1162 | 3.172 | 3.2384 | 3.2963 | 3.3401 | 3.361 | 3.3788 | 3.3905 | 3.4226
Sheffield | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.36723 | 0.3696 | 0.36952 | 0.37423 | 0.38094 | 0.38891 | 0.39586 | 0.40112 | 0.40363 | 0.40576 | 0.40717 | 0.41102
Sheffield | Maximum demand (peak season) (MVA) | 3.0799 | 3.0997 | 3.0991 | 3.1386 | 3.1948 | 3.2617 | 3.32 | 3.3641 | 3.3851 | 3.403 | 3.4148 | 3.4471
Sheffield | Maximum demand (peak season) Power factor (coincident) | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287 | 0.99287
Sheffield | Maximum demand (non-peak season) (MW) | 6.1049 | 6.4204 | 6.5216 | 6.6907 | 6.8888 | 7.1127 | 7.3024 | 7.5215 | 7.6206 | 7.718 | 7.7903 | 7.8517 |  | 9.3796
Sheffield | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.048935 | 0.051464 | 0.052275 | 0.053631 | 0.055219 | 0.057013 | 0.058533 | 0.06029 | 0.061084 | 0.061865 | 0.062444 | 0.062937
Sheffield | Maximum demand (non-peak season) (MVA) | 6.1051 | 6.4206 | 6.5218 | 6.6909 | 6.889 | 7.1129 | 7.3026 | 7.5217 | 7.6208 | 7.7182 | 7.7905 | 7.852
Sheffield | Hours exceeding 95% of maximum demand | 2
Sheffield | Hours exceeding Firm capacity (continuous rating) | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5
Sheffield | Hours exceeding Firm capacity (short-term rating) | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5 | 8749.5
Sheffield | Regional Diversity Factor (Summer) | 0.61158
Sheffield | Regional Diversity Factor (Winter) | 0.80394
Sheffield | Load transfer capacity (MVA)1
Sheffield | Load transfer capacity (MVA)2
Sheffield | Load transfer capacity (MVA)3
Sheffield | Load transfer capacity (MVA)4
Sheffield | Load transfer capacity (MVA)5
Sheffield | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Sheffield | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
St Leonards | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Summer
St Leonards | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
St Leonards | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
St Leonards | Maximum demand (peak season) (MW) | 15.8781 | 16.6988 | 16.9621 | 17.4019 | 17.9171 | 18.4993 | 18.9927 | 19.5625 | 19.8204 | 20.0736 | 20.2617 | 20.4216
St Leonards | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.71897 | 0.75613 | 0.76805 | 0.78796 | 0.81129 | 0.83765 | 0.85999 | 0.88579 | 0.89747 | 0.90894 | 0.91745 | 0.92469
St Leonards | Maximum demand (peak season) (MVA) | 15.8944 | 16.7159 | 16.9795 | 17.4197 | 17.9355 | 18.5183 | 19.0121 | 19.5826 | 19.8407 | 20.0942 | 20.2825 | 20.4425
St Leonards | Maximum demand (peak season) Power factor (coincident) | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898 | 0.99898
St Leonards | Maximum demand (non-peak season) (MW) | 29.9459 | 30.139 | 30.1329 | 30.5166 | 31.0636 | 31.7139 | 32.2806 | 32.7096 | 32.9138 | 33.088 | 33.2027 | 33.5169 |  | 9.3796
St Leonards | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.13127 | 0.13212 | 0.13209 | 0.13377 | 0.13617 | 0.13902 | 0.1415 | 0.14338 | 0.14428 | 0.14504 | 0.14555 | 0.14692
St Leonards | Maximum demand (non-peak season) (MVA) | 29.9462 | 30.1393 | 30.1332 | 30.5169 | 31.0639 | 31.7142 | 32.281 | 32.7099 | 32.9141 | 33.0883 | 33.203 | 33.5172
St Leonards | Hours exceeding 95% of maximum demand | 2.5
St Leonards | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
St Leonards | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
St Leonards | Regional Diversity Factor (Summer) | 1
St Leonards | Regional Diversity Factor (Winter) | 0.96901
St Leonards | Load transfer capacity (MVA)1 | 3 | [11 empty] | Trevallyn
St Leonards | Load transfer capacity (MVA)2 | 3 | [11 empty] | Mowbray
St Leonards | Load transfer capacity (MVA)3 | 10 | [11 empty] | Norwood
St Leonards | Load transfer capacity (MVA)4
St Leonards | Load transfer capacity (MVA)5
St Leonards | Embedded generation capacity (MVA) Units less than 100 kVA | 15.206
St Leonards | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.012
St Marys | Substation capacity (winter and summer) (MVA) Total | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | Winter
St Marys | Substation capacity (winter and summer) (MVA) Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
St Marys | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
St Marys | Maximum demand (peak season) (MW) | 16.3642 | 16.4697 | 16.4664 | 16.676 | 16.9749 | 17.3303 | 17.64 | 17.8744 | 17.986 | 18.0812 | 18.1438 | 18.3156
St Marys | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.27344 | 0.2752 | 0.27515 | 0.27865 | 0.28365 | 0.28958 | 0.29476 | 0.29868 | 0.30054 | 0.30213 | 0.30318 | 0.30605
St Marys | Maximum demand (peak season) (MVA) | 16.3664 | 16.472 | 16.4687 | 16.6783 | 16.9773 | 17.3327 | 17.6424 | 17.8769 | 17.9885 | 18.0837 | 18.1464 | 18.3181
St Marys | Maximum demand (peak season) Power factor (coincident) | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986 | 0.99986
St Marys | Maximum demand (non-peak season) (MW) | 9.0396 | 9.5068 | 9.6567 | 9.9071 | 10.2004 | 10.5318 | 10.8127 | 11.1371 | 11.2839 | 11.4281 | 11.5352 | 11.6262 |  | 9.3796
St Marys | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.015692 | 0.016503 | 0.016763 | 0.017198 | 0.017707 | 0.018282 | 0.01877 | 0.019333 | 0.019588 | 0.019838 | 0.020024 | 0.020182
St Marys | Maximum demand (non-peak season) (MVA) | 9.0396 | 9.5068 | 9.6567 | 9.9071 | 10.2004 | 10.5318 | 10.8127 | 11.1371 | 11.2839 | 11.4281 | 11.5352 | 11.6262
St Marys | Hours exceeding 95% of maximum demand | 2.5
St Marys | Hours exceeding Firm capacity (continuous rating) | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333 | 5333
St Marys | Hours exceeding Firm capacity (short-term rating) | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5 | 4951.5
St Marys | Regional Diversity Factor (Summer) | 0.72187
St Marys | Regional Diversity Factor (Winter) | 0.98284
St Marys | Load transfer capacity (MVA)1 | 2.8 | [11 empty] | Avoca
St Marys | Load transfer capacity (MVA)2 | 4.5 | [11 empty] | Triabunna
St Marys | Load transfer capacity (MVA)3 | 4 | [11 empty] | Derby
St Marys | Load transfer capacity (MVA)4
St Marys | Load transfer capacity (MVA)5
St Marys | Embedded generation capacity (MVA) Units less than 100 kVA | 15.463
St Marys | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Sorell | Substation capacity (winter and summer) (MVA) Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | Winter
Sorell | Substation capacity (winter and summer) (MVA) Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Sorell | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Sorell | Maximum demand (peak season) (MW) | 37.1113 | 37.3506 | 37.3431 | 37.8185 | 38.4964 | 39.3024 | 40.0047 | 40.5363 | 40.7893 | 41.0052 | 41.1473 | 41.5368
Sorell | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.9682 | 1.9809 | 1.9805 | 2.0057 | 2.0417 | 2.0844 | 2.1217 | 2.1499 | 2.1633 | 2.1748 | 2.1823 | 2.2029
Sorell | Maximum demand (peak season) (MVA) | 37.1635 | 37.4031 | 37.3956 | 37.8717 | 38.5505 | 39.3576 | 40.0609 | 40.5933 | 40.8467 | 41.0629 | 41.2052 | 41.5951
Sorell | Maximum demand (peak season) Power factor (coincident) | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986
Sorell | Maximum demand (non-peak season) (MW) | 19.1532 | 20.1432 | 20.4607 | 20.9912 | 21.6127 | 22.315 | 22.9101 | 23.5975 | 23.9085 | 24.214 | 24.4409 | 24.6338 |  | 9.3796
Sorell | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.056 | 1.1106 | 1.1281 | 1.1574 | 1.1916 | 1.2304 | 1.2632 | 1.3011 | 1.3182 | 1.3351 | 1.3476 | 1.3582
Sorell | Maximum demand (non-peak season) (MVA) | 19.1823 | 20.1737 | 20.4918 | 21.0231 | 21.6455 | 22.3489 | 22.9449 | 23.6333 | 23.9448 | 24.2508 | 24.478 | 24.6712
Sorell | Hours exceeding 95% of maximum demand | 16
Sorell | Hours exceeding Firm capacity (continuous rating) | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5 | 4820.5
Sorell | Hours exceeding Firm capacity (short-term rating) | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5 | 4819.5
Sorell | Regional Diversity Factor (Summer) | 1
Sorell | Regional Diversity Factor (Winter) | 0.90758
Sorell | Load transfer capacity (MVA)1 | 1.5 | [11 empty] | Avoca
Sorell | Load transfer capacity (MVA)2 | 1.5 | [11 empty] | Triabunna
Sorell | Load transfer capacity (MVA)3 | 1.5 | [11 empty] | Meadowbank
Sorell | Load transfer capacity (MVA)4
Sorell | Load transfer capacity (MVA)5
Sorell | Embedded generation capacity (MVA) Units less than 100 kVA | 32.257
Sorell | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.022
Savage River DL | Substation capacity (winter and summer) (MVA) Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Savage River DL | Substation capacity (winter and summer) (MVA) Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Savage River DL | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Savage River DL | Maximum demand (peak season) (MW) | 1.1492 | 1.1566 | 1.1564 | 1.1711 | 1.1921 | 1.2171 | 1.2388 | 1.2553 | 1.2631 | 1.2698 | 1.2742 | 1.2863
Savage River DL | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River DL | Maximum demand (peak season) (MVA) | 1.1492 | 1.1566 | 1.1564 | 1.1711 | 1.1921 | 1.2171 | 1.2388 | 1.2553 | 1.2631 | 1.2698 | 1.2742 | 1.2863
Savage River DL | Maximum demand (peak season) Power factor (coincident) | 1 | 1 | bar: 2027 to 2036
Savage River DL | Maximum demand (non-peak season) (MW) | 0.75017 | 0.78895 | 0.80138 | 0.82216 | 0.84651 | 0.87401 | 0.89732 | 0.92424 | 0.93643 | 0.94839 | 0.95728 | 0.96483 |  | 9.3796
Savage River DL | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Savage River DL | Maximum demand (non-peak season) (MVA) | 0.75017 | 0.78895 | 0.80138 | 0.82216 | 0.84651 | 0.87401 | 0.89732 | 0.92424 | 0.93643 | 0.94839 | 0.95728 | 0.96483
Savage River DL | Hours exceeding 95% of maximum demand | 805
Savage River DL | Hours exceeding Firm capacity (continuous rating) | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5
Savage River DL | Hours exceeding Firm capacity (short-term rating) | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5 | 4794.5
Savage River DL | Regional Diversity Factor (Summer) | 0.54092
Savage River DL | Regional Diversity Factor (Winter) | 0.8085
Savage River DL | Load transfer capacity (MVA)1
Savage River DL | Load transfer capacity (MVA)2
Savage River DL | Load transfer capacity (MVA)3
Savage River DL | Load transfer capacity (MVA)4
Savage River DL | Load transfer capacity (MVA)5
Savage River DL | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Savage River DL | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Smithton | Substation capacity (winter and summer) (MVA) Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Winter
Smithton | Substation capacity (winter and summer) (MVA) Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Smithton | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Smithton | Maximum demand (peak season) (MW) | 21.6235 | 21.7629 | 21.7585 | 22.0355 | 22.4305 | 22.9001 | 23.3093 | 23.6191 | 23.7665 | 23.8923 | 23.9751 | 24.202
Smithton | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 3.2716 | 3.2927 | 3.2921 | 3.334 | 3.3937 | 3.4648 | 3.5267 | 3.5736 | 3.5959 | 3.6149 | 3.6274 | 3.6618
Smithton | Maximum demand (peak season) (MVA) | 21.8696 | 22.0106 | 22.0061 | 22.2863 | 22.6858 | 23.1607 | 23.5746 | 23.8879 | 24.037 | 24.1642 | 24.248 | 24.4775
Smithton | Maximum demand (peak season) Power factor (coincident) | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875 | 0.98875
Smithton | Maximum demand (non-peak season) (MW) | 19.4177 | 20.4213 | 20.7433 | 21.2811 | 21.9112 | 22.6232 | 23.2265 | 23.9234 | 24.2387 | 24.5484 | 24.7785 | 24.974 |  | 9.3796
Smithton | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 6.713 | 7.0599 | 7.1712 | 7.3572 | 7.575 | 7.8211 | 8.0297 | 8.2706 | 8.3797 | 8.4867 | 8.5662 | 8.6338
Smithton | Maximum demand (non-peak season) (MVA) | 20.5453 | 21.6073 | 21.9479 | 22.517 | 23.1836 | 23.937 | 24.5753 | 25.3127 | 25.6463 | 25.974 | 26.2174 | 26.4243
Smithton | Hours exceeding 95% of maximum demand | 15.5
Smithton | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Smithton | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Smithton | Regional Diversity Factor (Summer) | 0.80678
Smithton | Regional Diversity Factor (Winter) | 0.89408
Smithton | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Port Latta
Smithton | Load transfer capacity (MVA)2
Smithton | Load transfer capacity (MVA)3
Smithton | Load transfer capacity (MVA)4
Smithton | Load transfer capacity (MVA)5
Smithton | Embedded generation capacity (MVA) Units less than 100 kVA | 6.168
Smithton | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Triabunna (RT) | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Triabunna (RT) | Maximum demand (peak season) (MW) | 7.5785 | 7.6273 | 7.6258 | 7.7229 | 7.8613 | 8.0259 | 8.1693 | 8.2779 | 8.3296 | 8.3736 | 8.4027 | 8.4822
Triabunna (RT) | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.063606 | 0.064016 | 0.064003 | 0.064818 | 0.06598 | 0.067361 | 0.068565 | 0.069476 | 0.06991 | 0.07028 | 0.070524 | 0.071191
Triabunna (RT) | Maximum demand (peak season) (MVA) | 7.5787 | 7.6276 | 7.6261 | 7.7232 | 7.8616 | 8.0262 | 8.1696 | 8.2782 | 8.3299 | 8.3739 | 8.403 | 8.4825
Triabunna (RT) | Maximum demand (peak season) Power factor (coincident) | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
Triabunna (RT) | Maximum demand (non-peak season) (MW) | 4.5504 | 4.7856 | 4.8611 | 4.9871 | 5.1348 | 5.3016 | 5.443 | 5.6063 | 5.6802 | 5.7528 | 5.8067 | 5.8525 |  | 9.3796
Triabunna (RT) | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.46882 | 0.49305 | 0.50082 | 0.51381 | 0.52902 | 0.54621 | 0.56077 | 0.5776 | 0.58521 | 0.59269 | 0.59824 | 0.60296
Triabunna (RT) | Maximum demand (non-peak season) (MVA) | 4.5745 | 4.811 | 4.8868 | 5.0135 | 5.1619 | 5.3297 | 5.4718 | 5.636 | 5.7103 | 5.7832 | 5.8374 | 5.8835
Triabunna (RT) | Hours exceeding 95% of maximum demand | 2
Triabunna (RT) | Hours exceeding Firm capacity (continuous rating) | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
Triabunna (RT) | Hours exceeding Firm capacity (short-term rating) | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800
Triabunna (RT) | Regional Diversity Factor (Summer) | 0.70509
Triabunna (RT) | Regional Diversity Factor (Winter) | 0.84397
Triabunna (RT) | Load transfer capacity (MVA)1 | 3 | [11 empty] | St Marys
Triabunna (RT) | Load transfer capacity (MVA)2 | 1.8 | [11 empty] | Sorell
Triabunna (RT) | Load transfer capacity (MVA)3
Triabunna (RT) | Load transfer capacity (MVA)4
Triabunna (RT) | Load transfer capacity (MVA)5
Triabunna (RT) | Embedded generation capacity (MVA) Units less than 100 kVA | 0
Triabunna (RT) | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Trevallyn | Substation capacity (winter and summer) (MVA) Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | Winter
Trevallyn | Substation capacity (winter and summer) (MVA) Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Trevallyn | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
Trevallyn | Maximum demand (peak season) (MW) | 73.613 | 74.0877 | 74.0727 | 75.0158 | 76.3604 | 77.9591 | 79.3522 | 80.4067 | 80.9087 | 81.3369 | 81.6187 | 82.3912
Trevallyn | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 1.3335 | 1.3421 | 1.3418 | 1.3589 | 1.3832 | 1.4122 | 1.4374 | 1.4565 | 1.4656 | 1.4734 | 1.4785 | 1.4925
Trevallyn | Maximum demand (peak season) (MVA) | 73.6251 | 74.0998 | 74.0849 | 75.0281 | 76.3729 | 77.9719 | 79.3652 | 80.4199 | 80.9219 | 81.3502 | 81.6321 | 82.4047
Trevallyn | Maximum demand (peak season) Power factor (coincident) | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984 | 0.99984
Trevallyn | Maximum demand (non-peak season) (MW) | 38.3144 | 40.2948 | 40.93 | 41.9913 | 43.2345 | 44.6394 | 45.8298 | 47.2049 | 47.8271 | 48.4382 | 48.8921 | 49.2779 |  | 9.3796
Trevallyn | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.63923 | 0.67227 | 0.68287 | 0.70058 | 0.72132 | 0.74476 | 0.76462 | 0.78756 | 0.79794 | 0.80814 | 0.81571 | 0.82214
Trevallyn | Maximum demand (non-peak season) (MVA) | 38.3197 | 40.3004 | 40.9357 | 41.9971 | 43.2405 | 44.6456 | 45.8362 | 47.2115 | 47.8338 | 48.4449 | 48.8989 | 49.2847
Trevallyn | Hours exceeding 95% of maximum demand | 2
Trevallyn | Hours exceeding Firm capacity (continuous rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Trevallyn | Hours exceeding Firm capacity (short-term rating) | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824 | 4824
Trevallyn | Regional Diversity Factor (Summer) | 1
Trevallyn | Regional Diversity Factor (Winter) | 0.95866
Trevallyn | Load transfer capacity (MVA)1 | 3.6 | [11 empty] | George Town
Trevallyn | Load transfer capacity (MVA)2 | 36.1 | [11 empty] | Mowbray
Trevallyn | Load transfer capacity (MVA)3 | 21.7 | [11 empty] | Norwood
Trevallyn | Load transfer capacity (MVA)4 | 21.7 | [11 empty] | St Leonards
Trevallyn | Load transfer capacity (MVA)5 | 14.4 | [11 empty] | Hadspen
Trevallyn | Embedded generation capacity (MVA) Units less than 100 kVA | 46.227
Trevallyn | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.06
Tungatinah | Substation capacity (winter and summer) (MVA) Total | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | Winter
Tungatinah | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | Maximum demand (peak season) (MW) | 0.97194 | 0.97821 | 0.97801 | 0.99046 | 1.0082 | 1.0293 | 1.0477 | 1.0616 | 1.0683 | 1.0739 | 1.0776 | 1.0878
Tungatinah | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.030992 | 0.031192 | 0.031185 | 0.031582 | 0.032148 | 0.032821 | 0.033408 | 0.033852 | 0.034063 | 0.034244 | 0.034362 | 0.034687
Tungatinah | Maximum demand (peak season) (MVA) | 0.97244 | 0.97871 | 0.97851 | 0.99097 | 1.0087 | 1.0298 | 1.0483 | 1.0622 | 1.0688 | 1.0745 | 1.0782 | 1.0884
Tungatinah | Maximum demand (peak season) Power factor (coincident) | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949 | 0.99949
Tungatinah | Maximum demand (non-peak season) (MW) | 0.60813 | 0.63957 | 0.64965 | 0.66649 | 0.68623 | 0.70853 | 0.72742 | 0.74925 | 0.75912 | 0.76882 | 0.77603 | 0.78215 |  | 9.3796
Tungatinah | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.026127 | 0.027477 | 0.02791 | 0.028634 | 0.029482 | 0.03044 | 0.031252 | 0.032189 | 0.032613 | 0.03303 | 0.03334 | 0.033603
Tungatinah | Maximum demand (non-peak season) (MVA) | 0.6087 | 0.64016 | 0.65025 | 0.66711 | 0.68686 | 0.70918 | 0.72809 | 0.74994 | 0.75982 | 0.76953 | 0.77674 | 0.78287
Tungatinah | Hours exceeding 95% of maximum demand | 2.5
Tungatinah | Hours exceeding Firm capacity (continuous rating) | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5
Tungatinah | Hours exceeding Firm capacity (short-term rating) | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5 | 8760.5
Tungatinah | Regional Diversity Factor (Summer) | 0.58677
Tungatinah | Regional Diversity Factor (Winter) | 0.89714
Tungatinah | Load transfer capacity (MVA)1
Tungatinah | Load transfer capacity (MVA)2
Tungatinah | Load transfer capacity (MVA)3
Tungatinah | Load transfer capacity (MVA)4
Tungatinah | Load transfer capacity (MVA)5
Tungatinah | Embedded generation capacity (MVA) Units less than 100 kVA | 0.228
Tungatinah | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Ulverstone | Substation capacity (winter and summer) (MVA) Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Ulverstone | Substation capacity (winter and summer) (MVA) Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Ulverstone | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
Ulverstone | Maximum demand (peak season) (MW) | 31.0919 | 31.2924 | 31.2861 | 31.6844 | 32.2524 | 32.9276 | 33.516 | 33.9614 | 34.1734 | 34.3543 | 34.4733 | 34.7996
Ulverstone | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.72353 | 0.7282 | 0.72805 | 0.73732 | 0.75053 | 0.76625 | 0.77994 | 0.7903 | 0.79524 | 0.79945 | 0.80222 | 0.80981
Ulverstone | Maximum demand (peak season) (MVA) | 31.1004 | 31.3009 | 31.2946 | 31.693 | 32.2611 | 32.9365 | 33.5251 | 33.9706 | 34.1827 | 34.3636 | 34.4827 | 34.809
Ulverstone | Maximum demand (peak season) Power factor (coincident) | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973
Ulverstone | Maximum demand (non-peak season) (MW) | 15.1241 | 15.9058 | 16.1566 | 16.5755 | 17.0662 | 17.6208 | 18.0907 | 18.6335 | 18.8791 | 19.1203 | 19.2995 | 19.4518 |  | 19.3699
Ulverstone | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.1558 | 1.2155 | 1.2347 | 1.2667 | 1.3042 | 1.3466 | 1.3825 | 1.424 | 1.4427 | 1.4612 | 1.4749 | 1.4865
Ulverstone | Maximum demand (non-peak season) (MVA) | 15.1682 | 15.9522 | 16.2037 | 16.6238 | 17.116 | 17.6722 | 18.1435 | 18.6878 | 18.9342 | 19.1761 | 19.3558 | 19.5085
Ulverstone | Hours exceeding 95% of maximum demand | 1.5
Ulverstone | Hours exceeding Firm capacity (continuous rating) | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5
Ulverstone | Hours exceeding Firm capacity (short-term rating) | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5 | 4823.5
Ulverstone | Regional Diversity Factor (Summer) | 0.92286
Ulverstone | Regional Diversity Factor (Winter) | 0.93687
Ulverstone | Load transfer capacity (MVA)1 | 6.8 | [11 empty] | Burnie
Ulverstone | Load transfer capacity (MVA)2 | 10.3 | [11 empty] | Devonport
Ulverstone | Load transfer capacity (MVA)3 | 3.4 | [11 empty] | Railton
Ulverstone | Load transfer capacity (MVA)4
Ulverstone | Load transfer capacity (MVA)5
Ulverstone | Embedded generation capacity (MVA) Units less than 100 kVA | 23.656
Ulverstone | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.024
Waddamana | Substation capacity (winter and summer) (MVA) Total | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | Winter
Waddamana | Substation capacity (winter and summer) (MVA) Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waddamana | Maximum demand (peak season) (MW) | 0.67308 | 0.67742 | 0.67729 | 0.68591 | 0.6982 | 0.71282 | 0.72556 | 0.7352 | 0.73979 | 0.74371 | 0.74628 | 0.75335
Waddamana | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.067683 | 0.06812 | 0.068106 | 0.068973 | 0.070209 | 0.071679 | 0.07296 | 0.07393 | 0.074391 | 0.074785 | 0.075044 | 0.075754
Waddamana | Maximum demand (peak season) (MVA) | 0.67648 | 0.68084 | 0.6807 | 0.68937 | 0.70173 | 0.71642 | 0.72922 | 0.73891 | 0.74352 | 0.74746 | 0.75005 | 0.75715
Waddamana | Maximum demand (peak season) Power factor (coincident) | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498 | 0.99498
Waddamana | Maximum demand (non-peak season) (MW) | 0.40619 | 0.42719 | 0.43392 | 0.44517 | 0.45835 | 0.47325 | 0.48587 | 0.50045 | 0.50704 | 0.51352 | 0.51833 | 0.52242 |  | 19.3699
Waddamana | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 0.10506 | 0.11049 | 0.11223 | 0.11514 | 0.11855 | 0.1224 | 0.12566 | 0.12943 | 0.13114 | 0.13281 | 0.13406 | 0.13512
Waddamana | Maximum demand (non-peak season) (MVA) | 0.41956 | 0.44124 | 0.4482 | 0.45982 | 0.47344 | 0.48882 | 0.50186 | 0.51691 | 0.52373 | 0.53042 | 0.53539 | 0.53961
Waddamana | Hours exceeding 95% of maximum demand | 4
Waddamana | Hours exceeding Firm capacity (continuous rating) | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732
Waddamana | Hours exceeding Firm capacity (short-term rating) | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732 | 8732
Waddamana | Regional Diversity Factor (Summer) | 0.55644
Waddamana | Regional Diversity Factor (Winter) | 0.58751
Waddamana | Load transfer capacity (MVA)1 | 0.9 | [11 empty] | Arthurs Lake
Waddamana | Load transfer capacity (MVA)2
Waddamana | Load transfer capacity (MVA)3
Waddamana | Load transfer capacity (MVA)4
Waddamana | Load transfer capacity (MVA)5
Waddamana | Embedded generation capacity (MVA) Units less than 100 kVA | 0.791
Waddamana | Embedded generation capacity (MVA) Units greater than 100 kVA | 0
Wesley Vale | Substation capacity (winter and summer) (MVA) Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Wesley Vale | Substation capacity (winter and summer) (MVA) Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Wesley Vale | Substation capacity (winter and summer) (MVA) Short-term firm delivery | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Wesley Vale | Maximum demand (peak season) (MW) | 11.0843 | 11.1558 | 11.1535 | 11.2956 | 11.498 | 11.7387 | 11.9485 | 12.1073 | 12.1829 | 12.2474 | 12.2898 | 12.4061
Wesley Vale | Maximum demand (peak season) Reactive power (coincident) (MVAr) | 0.26594 | 0.26765 | 0.2676 | 0.271 | 0.27586 | 0.28164 | 0.28667 | 0.29048 | 0.29229 | 0.29384 | 0.29486 | 0.29765
Wesley Vale | Maximum demand (peak season) (MVA) | 11.0875 | 11.159 | 11.1568 | 11.2988 | 11.5013 | 11.7421 | 11.9519 | 12.1108 | 12.1864 | 12.2509 | 12.2933 | 12.4097
Wesley Vale | Maximum demand (peak season) Power factor (coincident) | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971 | 0.99971
Wesley Vale | Maximum demand (non-peak season) (MW) | 9.6106 | 10.1073 | 10.2666 | 10.5328 | 10.8447 | 11.1971 | 11.4957 | 11.8406 | 11.9967 | 12.1499 | 12.2638 | 12.3606 |  | 19.3699
Wesley Vale | Maximum demand (non-peak season) Reactive power (coincident) (MVAr) | 1.3537 | 1.4237 | 1.4462 | 1.4837 | 1.5276 | 1.5772 | 1.6193 | 1.6679 | 1.6899 | 1.7114 | 1.7275 | 1.7411
Wesley Vale | Maximum demand (non-peak season) (MVA) | 9.7054 | 10.2071 | 10.368 | 10.6368 | 10.9517 | 11.3076 | 11.6092 | 11.9575 | 12.1151 | 12.2699 | 12.3849 | 12.4826
Wesley Vale | Hours exceeding 95% of maximum demand | 2.5
Wesley Vale | Hours exceeding Firm capacity (continuous rating) | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834
Wesley Vale | Hours exceeding Firm capacity (short-term rating) | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834 | 2834
Wesley Vale | Regional Diversity Factor (Summer) | 0.88063
Wesley Vale | Regional Diversity Factor (Winter) | 0.99692
Wesley Vale | Load transfer capacity (MVA)1
Wesley Vale | Load transfer capacity (MVA)2
Wesley Vale | Load transfer capacity (MVA)3
Wesley Vale | Load transfer capacity (MVA)4
Wesley Vale | Load transfer capacity (MVA)5
Wesley Vale | Embedded generation capacity (MVA) Units less than 100 kVA | 10.335
Wesley Vale | Embedded generation capacity (MVA) Units greater than 100 kVA | 0.019
ZONE |  | 2025 (Actuals) | 2026 (Actuals) | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Load transfer point | Peaking season
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Bellerive | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Bellerive | Sub-transmission lines capacityTotal (winter) | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683
Zs-Bellerive | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Bellerive | Sub-transmission lines capacityTotal (summer) | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071 | 27.2071
Zs-Bellerive | Sub-transmission lines capacityFirm delivery (summer) | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035 | 13.6035
Zs-Bellerive | Maximum demand forecast(peak season)Maximum demand (MVA) | 9.7518 | 9.8147 | 9.8127 | 9.9376 | 10.1158 | 10.3275 | 10.5121 | 10.6518 | 10.7183 | 10.775 | 10.8124 | 10.9147
Zs-Bellerive | Maximum demand forecast(peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Zs-Bellerive | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 5.376 | 5.6538 | 5.743 | 5.8919 | 6.0663 | 6.2634 | 6.4305 | 6.6234 | 6.7107 | 6.7965 | 6.8601 | 6.9143
Zs-Bellerive | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995 | 0.99995
Zs-Bellerive | Hours exceeding95% of maximum demand | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Zs-Bellerive | Load transfer capacity (MVA)1 | 3.1 | [11 empty] | Rokeby
Zs-Bellerive | Load transfer capacity (MVA)2 | 3.1 | [11 empty] | Howrah Zone
Zs-Bellerive | Load transfer capacity (MVA)3 | 6.2 | [11 empty] | Cambridge Zone
Zs-Bellerive | Load transfer capacity (MVA)4 | 4.1 | [11 empty] | Geilston Bay
Zs-Bellerive | Embedded generation capacity (MVA)Units less than 100 kVA | 6.108
Zs-Bellerive | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.014
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Zs-Cambridge | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Zs-Cambridge | Sub-transmission lines capacityTotal (winter) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
Zs-Cambridge | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Sub-transmission lines capacityTotal (summer) | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189 | 17.7189
Zs-Cambridge | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Cambridge | Maximum demand forecast(peak season)Maximum demand (MVA) | 7.2936 | 7.3407 | 7.3392 | 7.4326 | 7.5658 | 7.7242 | 7.8623 | 7.9668 | 8.0165 | 8.0589 | 8.0868 | 8.1634
Zs-Cambridge | Maximum demand forecast(peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Zs-Cambridge | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 3.7738 | 3.9689 | 4.0314 | 4.136 | 4.2584 | 4.3968 | 4.514 | 4.6495 | 4.7108 | 4.7709 | 4.8157 | 4.8537
Zs-Cambridge | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
Zs-Cambridge | Hours exceeding95% of maximum demand | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Zs-Cambridge | Load transfer capacity (MVA)1 | 7.4 | [11 empty] | Rokeby
Zs-Cambridge | Load transfer capacity (MVA)2 | 7.4 | [11 empty] | Bellerive
Zs-Cambridge | Load transfer capacity (MVA)3
Zs-Cambridge | Load transfer capacity (MVA)4
Zs-Cambridge | Embedded generation capacity (MVA)Units less than 100 kVA | 7.805
Zs-Cambridge | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-Claremont | Substation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Zs-Claremont | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Claremont | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Zs-Claremont | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-Claremont | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Claremont | Sub-transmission lines capacityTotal (summer) | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356
Zs-Claremont | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Claremont | Maximum demand forecast(peak season)Maximum demand (MVA) | 23.3517 | 23.5023 | 23.4976 | 23.7967 | 24.2233 | 24.7304 | 25.1723 | 25.5068 | 25.6661 | 25.8019 | 25.8913 | 26.1364
Zs-Claremont | Maximum demand forecast(peak season)Power factor (coincident) | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959
Zs-Claremont | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 12.4688 | 13.1133 | 13.32 | 13.6654 | 14.0699 | 14.5271 | 14.9145 | 15.362 | 15.5645 | 15.7634 | 15.9111 | 16.0367
Zs-Claremont | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921 | 0.99921
Zs-Claremont | Hours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Zs-Claremont | Load transfer capacity (MVA)1
Zs-Claremont | Load transfer capacity (MVA)2
Zs-Claremont | Load transfer capacity (MVA)3
Zs-Claremont | Load transfer capacity (MVA)4
Zs-Claremont | Embedded generation capacity (MVA)Units less than 100 kVA | 11.167
Zs-Claremont | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Derwent Park | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Derwent Park | Sub-transmission lines capacityTotal (winter) | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666 | 40.8666
Zs-Derwent Park | Sub-transmission lines capacityFirm delivery (winter) | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325 | 19.4325
Zs-Derwent Park | Sub-transmission lines capacityTotal (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-Derwent Park | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Derwent Park | Maximum demand forecast(peak season)Maximum demand (MVA) | 18.8467 | 18.9682 | 18.9643 | 19.2058 | 19.55 | 19.9593 | 20.316 | 20.586 | 20.7145 | 20.8241 | 20.8963 | 21.0941
Zs-Derwent Park | Maximum demand forecast(peak season)Power factor (coincident) | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841 | 0.98841
Zs-Derwent Park | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 10.4375 | 10.977 | 11.1501 | 11.4392 | 11.7779 | 12.1606 | 12.4849 | 12.8595 | 13.029 | 13.1954 | 13.3191 | 13.4242
Zs-Derwent Park | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503 | 0.97503
Zs-Derwent Park | Hours exceeding95% of maximum demand | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Zs-Derwent Park | Load transfer capacity (MVA)1
Zs-Derwent Park | Load transfer capacity (MVA)2
Zs-Derwent Park | Load transfer capacity (MVA)3
Zs-Derwent Park | Load transfer capacity (MVA)4
Zs-Derwent Park | Embedded generation capacity (MVA)Units less than 100 kVA | 3.878
Zs-Derwent Park | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-East Hobart | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-East Hobart | Sub-transmission lines capacityTotal (winter) | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196
Zs-East Hobart | Sub-transmission lines capacityFirm delivery (winter) | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054
Zs-East Hobart | Sub-transmission lines capacityTotal (summer) | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196 | 42.7196
Zs-East Hobart | Sub-transmission lines capacityFirm delivery (summer) | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054 | 42.7054
Zs-East Hobart | Maximum demand forecast(peak season)Maximum demand (MVA) | 28.6182 | 28.8027 | 28.7969 | 29.1635 | 29.6862 | 30.3078 | 30.8493 | 31.2593 | 31.4544 | 31.6209 | 31.7305 | 32.0308
Zs-East Hobart | Maximum demand forecast(peak season)Power factor (coincident) | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513 | 0.98513
Zs-East Hobart | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 20.0579 | 21.0946 | 21.4271 | 21.9827 | 22.6336 | 23.369 | 23.9922 | 24.7121 | 25.0378 | 25.3577 | 25.5954 | 25.7973
Zs-East Hobart | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136 | 0.97136
Zs-East Hobart | Hours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Zs-East Hobart | Load transfer capacity (MVA)1
Zs-East Hobart | Load transfer capacity (MVA)2
Zs-East Hobart | Load transfer capacity (MVA)3
Zs-East Hobart | Load transfer capacity (MVA)4
Zs-East Hobart | Embedded generation capacity (MVA)Units less than 100 kVA | 0.491
Zs-East Hobart | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.027
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-Geilston Bay | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-Geilston Bay | Sub-transmission lines capacityTotal (winter) | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683 | 42.8683
Zs-Geilston Bay | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Geilston Bay | Sub-transmission lines capacityTotal (summer) | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356 | 27.0356
Zs-Geilston Bay | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Geilston Bay | Maximum demand forecast(peak season)Maximum demand (MVA) | 18.6282 | 18.7483 | 18.7445 | 18.9832 | 19.3234 | 19.728 | 20.0805 | 20.3474 | 20.4744 | 20.5827 | 20.6541 | 20.8495
Zs-Geilston Bay | Maximum demand forecast(peak season)Power factor (coincident) | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982
Zs-Geilston Bay | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 8.6066 | 9.0514 | 9.1941 | 9.4325 | 9.7118 | 10.0273 | 10.2947 | 10.6036 | 10.7434 | 10.8807 | 10.9826 | 11.0693
Zs-Geilston Bay | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947 | 0.99947
Zs-Geilston Bay | Hours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
Zs-Geilston Bay | Load transfer capacity (MVA)1 | 5.1 | [11 empty] | Bellerive
Zs-Geilston Bay | Load transfer capacity (MVA)2 | 5.1 | [11 empty] | Derwent Park
Zs-Geilston Bay | Load transfer capacity (MVA)3 | 3.8 | [11 empty] | East Hobart
Zs-Geilston Bay | Load transfer capacity (MVA)4
Zs-Geilston Bay | Embedded generation capacity (MVA)Units less than 100 kVA | 10.85
Zs-Geilston Bay | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Howrah | Substation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | Winter
Zs-Howrah | Substation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Zs-Howrah | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
Zs-Howrah | Sub-transmission lines capacityTotal (winter) | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124
Zs-Howrah | Sub-transmission lines capacityFirm delivery (winter) | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062
Zs-Howrah | Sub-transmission lines capacityTotal (summer) | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124 | 48.0124
Zs-Howrah | Sub-transmission lines capacityFirm delivery (summer) | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062 | 24.0062
Zs-Howrah | Maximum demand forecast(peak season)Maximum demand (MVA) | 17.0475 | 17.1574 | 17.1539 | 17.3723 | 17.6837 | 18.0539 | 18.3766 | 18.6208 | 18.737 | 18.8362 | 18.9015 | 19.0803
Zs-Howrah | Maximum demand forecast(peak season)Power factor (coincident) | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837 | 0.99837
Zs-Howrah | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 8.7221 | 9.173 | 9.3176 | 9.5592 | 9.8422 | 10.162 | 10.433 | 10.746 | 10.8877 | 11.0268 | 11.1301 | 11.2179
Zs-Howrah | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379 | 0.99379
Zs-Howrah | Hours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Zs-Howrah | Load transfer capacity (MVA)1 | 7.1 | [11 empty] | Rokeby
Zs-Howrah | Load transfer capacity (MVA)2 | 2.4 | [11 empty] | Bellerive
Zs-Howrah | Load transfer capacity (MVA)3
Zs-Howrah | Load transfer capacity (MVA)4
Zs-Howrah | Embedded generation capacity (MVA)Units less than 100 kVA | 13.516
Zs-Howrah | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Zs-New Town | Substation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | Winter
Zs-New Town | Substation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Zs-New Town | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Zs-New Town | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-New Town | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-New Town | Sub-transmission lines capacityTotal (summer) | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662 | 34.8662
Zs-New Town | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-New Town | Maximum demand forecast(peak season)Maximum demand (MVA) | 21.2344 | 21.3713 | 21.367 | 21.639 | 22.0269 | 22.488 | 22.8899 | 23.1941 | 23.3389 | 23.4624 | 23.5437 | 23.7665
Zs-New Town | Maximum demand forecast(peak season)Power factor (coincident) | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713 | 0.99713
Zs-New Town | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 10.5981 | 11.1459 | 11.3216 | 11.6151 | 11.959 | 12.3476 | 12.6769 | 13.0573 | 13.2294 | 13.3984 | 13.5239 | 13.6307
Zs-New Town | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487 | 0.99487
Zs-New Town | Hours exceeding95% of maximum demand | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Zs-New Town | Load transfer capacity (MVA)1
Zs-New Town | Load transfer capacity (MVA)2
Zs-New Town | Load transfer capacity (MVA)3
Zs-New Town | Load transfer capacity (MVA)4
Zs-New Town | Embedded generation capacity (MVA)Units less than 100 kVA | 8.702
Zs-New Town | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.032
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Sub-transmission lines capacityTotal (winter) | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911
Zs-Rosny Park | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Sub-transmission lines capacityTotal (summer) | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911 | 20.6911
Zs-Rosny Park | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Rosny Park | Maximum demand forecast(peak season)Maximum demand (MVA) | 15.5425 | 15.6428 | 15.6396 | 15.8387 | 16.1226 | 16.4602 | 16.7543 | 16.977 | 17.0829 | 17.1733 | 17.2329 | 17.396
Zs-Rosny Park | Maximum demand forecast(peak season)Power factor (coincident) | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939 | 0.99939
Zs-Rosny Park | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 7.5217 | 7.9105 | 8.0352 | 8.2435 | 8.4876 | 8.7634 | 8.9971 | 9.267 | 9.3892 | 9.5091 | 9.5982 | 9.674
Zs-Rosny Park | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871 | 0.99871
Zs-Rosny Park | Hours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Zs-Rosny Park | Load transfer capacity (MVA)1
Zs-Rosny Park | Load transfer capacity (MVA)2
Zs-Rosny Park | Load transfer capacity (MVA)3
Zs-Rosny Park | Load transfer capacity (MVA)4
Zs-Rosny Park | Embedded generation capacity (MVA)Units less than 100 kVA | 7.466
Zs-Rosny Park | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-Sandy Bay | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-Sandy Bay | Sub-transmission lines capacityTotal (winter) | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686 | 44.0686
Zs-Sandy Bay | Sub-transmission lines capacityFirm delivery (winter) | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341 | 21.4341
Zs-Sandy Bay | Sub-transmission lines capacityTotal (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-Sandy Bay | Sub-transmission lines capacityFirm delivery (summer) | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321 | 13.4321
Zs-Sandy Bay | Maximum demand forecast(peak season)Maximum demand (MVA) | 32.8562 | 33.0681 | 33.0614 | 33.4823 | 34.0825 | 34.796 | 35.4178 | 35.8885 | 36.1125 | 36.3036 | 36.4295 | 36.7742
Zs-Sandy Bay | Maximum demand forecast(peak season)Power factor (coincident) | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99985
Zs-Sandy Bay | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 14.3926 | 15.1365 | 15.3751 | 15.7738 | 16.2408 | 16.7685 | 17.2157 | 17.7322 | 17.966 | 18.1955 | 18.366 | 18.5109
Zs-Sandy Bay | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885 | 0.99885
Zs-Sandy Bay | Hours exceeding95% of maximum demand | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5 | 26.5
Zs-Sandy Bay | Load transfer capacity (MVA)1
Zs-Sandy Bay | Load transfer capacity (MVA)2
Zs-Sandy Bay | Load transfer capacity (MVA)3
Zs-Sandy Bay | Load transfer capacity (MVA)4
Zs-Sandy Bay | Embedded generation capacity (MVA)Units less than 100 kVA | 18.762
Zs-Sandy Bay | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.011
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | Winter
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Sub-transmission lines capacityTotal (winter) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
Zs-Summerleas | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Sub-transmission lines capacityTotal (summer) | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353 | 25.8353
Zs-Summerleas | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Summerleas | Maximum demand forecast(peak season)Maximum demand (MVA) | 10.8982 | 10.9685 | 10.9663 | 11.1059 | 11.305 | 11.5417 | 11.7479 | 11.904 | 11.9783 | 12.0417 | 12.0835 | 12.1978
Zs-Summerleas | Maximum demand forecast(peak season)Power factor (coincident) | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
Zs-Summerleas | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 4.8693 | 5.121 | 5.2017 | 5.3366 | 5.4946 | 5.6732 | 5.8244 | 5.9992 | 6.0783 | 6.1559 | 6.2136 | 6.2627
Zs-Summerleas | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807 | 0.99807
Zs-Summerleas | Hours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Zs-Summerleas | Load transfer capacity (MVA)1 | 4.9 | [11 empty] | Kingston
Zs-Summerleas | Load transfer capacity (MVA)2
Zs-Summerleas | Load transfer capacity (MVA)3
Zs-Summerleas | Load transfer capacity (MVA)4
Zs-Summerleas | Embedded generation capacity (MVA)Units less than 100 kVA | 7.197
Zs-Summerleas | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | Winter
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Zs-Trial Harbour | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Zs-Trial Harbour | Sub-transmission lines capacityTotal (winter) | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186
Zs-Trial Harbour | Sub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Sub-transmission lines capacityTotal (summer) | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186 | 18.186
Zs-Trial Harbour | Sub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Maximum demand forecast(peak season)Maximum demand (MVA) | 2.4377 | 2.4534 | 2.4529 | 2.4842 | 2.5287 | 2.5816 | 2.6278 | 2.6627 | 2.6793 | 2.6935 | 2.7028 | 2.7284
Zs-Trial Harbour | Maximum demand forecast(peak season)Power factor (coincident) | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418 | 0.98418
Zs-Trial Harbour | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 1.2914 | 1.3581 | 1.3795 | 1.4153 | 1.4572 | 1.5046 | 1.5447 | 1.591 | 1.612 | 1.6326 | 1.6479 | 1.6609
Zs-Trial Harbour | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971 | 0.9971
Zs-Trial Harbour | Hours exceeding95% of maximum demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Zs-Trial Harbour | Load transfer capacity (MVA)1
Zs-Trial Harbour | Load transfer capacity (MVA)2
Zs-Trial Harbour | Load transfer capacity (MVA)3
Zs-Trial Harbour | Load transfer capacity (MVA)4
Zs-Trial Harbour | Embedded generation capacity (MVA)Units less than 100 kVA | 0.809
Zs-Trial Harbour | Embedded generation capacity (MVA)Units greater than 100 kVA | 0
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | Winter
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Zs-West Hobart | Substation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
Zs-West Hobart | Sub-transmission lines capacityTotal (winter) | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033 | 67.9033
Zs-West Hobart | Sub-transmission lines capacityFirm delivery (winter) | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689 | 45.2689
Zs-West Hobart | Sub-transmission lines capacityTotal (summer) | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962 | 40.2962
Zs-West Hobart | Sub-transmission lines capacityFirm delivery (summer) | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641 | 26.8641
Zs-West Hobart | Maximum demand forecast(peak season)Maximum demand (MVA) | 35.3144 | 35.5421 | 35.5349 | 35.9873 | 36.6324 | 37.3993 | 38.0676 | 38.5735 | 38.8143 | 39.0197 | 39.155 | 39.5255
Zs-West Hobart | Maximum demand forecast(peak season)Power factor (coincident) | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823 | 0.99823
Zs-West Hobart | Maximum demand forecast(non-peak season)Maximum demand (MVA) | 15.8555 | 16.675 | 16.9379 | 17.3771 | 17.8916 | 18.4729 | 18.9656 | 19.5346 | 19.7921 | 20.045 | 20.2328 | 20.3925
Zs-West Hobart | Maximum demand forecast(non-peak season)Power factor (coincident) | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994 | 0.99994
Zs-West Hobart | Hours exceeding95% of maximum demand | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Zs-West Hobart | Load transfer capacity (MVA)1
Zs-West Hobart | Load transfer capacity (MVA)2
Zs-West Hobart | Load transfer capacity (MVA)3
Zs-West Hobart | Load transfer capacity (MVA)4
Zs-West Hobart | Embedded generation capacity (MVA)Units less than 100 kVA | 13.843
Zs-West Hobart | Embedded generation capacity (MVA)Units greater than 100 kVA | 0.024
Winter
Winter
Winter

## Maximum Demand Forecast
Summer | Actuals |  | Forecast | [11 empty] | Winter | Actuals |  | Forecast | [11 empty] | Hours exceeding 95% maximum demand |  | Substation firm delivery |  |  | Hours exceeding firm capacity |  |  | Load transfer capacity |  |  |  | Substation Total Capacity
Substation | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Power Factor | Diversity Factor | Substation | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Power Factor | Diversity Factor | Substation | Hours | Substation | Firm | Short-term firm | Substation | continuous rating | short-term rating | Substation |  | Load transfer point | MVA | Substation | Total (MVA)
Arthurs Lake (DL) | 0.017402 | 0.018301 | 0.01859 | 0.019072 | 0.019637 | 0.020275 | 0.020815 | 0.02144 | 0.021723 | 0.022 | 0.022206 | 0.022381 | 0.36455 | 0.79208 | Arthurs Lake (DL) | 0.020573 | 0.020706 | 0.020701 | 0.020965 | 0.021341 | 0.021788 | 0.022177 | 0.022472 | 0.022612 | 0.022732 | 0.02281 | 0.023026 | 0.42422 | 0.91429 | Arthurs Lake (DL) | 1226 | Arthurs Lake (DL) | 0 | 0 | Arthurs Lake (DL) | 8753.5 | 8753.5 | Arthurs Lake (DL) | Load transfer capacity (MVA)1 | Waddmana | 0.1 | Arthurs Lake (DL) | 25
Avoca | 8.9186 | 9.3796 | 9.5275 | 9.7745 | 10.0639 | 10.3909 | 10.668 | 10.9881 | 11.1329 | 11.2752 | 11.3808 | 11.4706 | 0.97924 | 0.56211 | Avoca | 8.0203 | 8.072 | 8.0704 | 8.1731 | 8.3196 | 8.4938 | 8.6456 | 8.7605 | 8.8151 | 8.8618 | 8.8925 | 8.9767 | 0.99673 | 0.83413 | Avoca | 3.5 | Avoca | 0 | 0 | Avoca | 8308.5 | 8308.5 | Arthurs Lake (DL) | Load transfer capacity (MVA)2 |  |  | Avoca | 17
Bridgewater | 18.418 | 19.3699 | 19.6753 | 20.1854 | 20.7831 | 21.4584 | 22.0307 | 22.6917 | 22.9908 | 23.2845 | 23.5027 | 23.6882 | 1 | 0.9735 | Bridgewater | 36.056 | 36.2885 | 36.2811 | 36.7431 | 37.4016 | 38.1847 | 38.867 | 39.3835 | 39.6294 | 39.8391 | 39.9772 | 40.3556 | 0.99914 | 0.96741 | Bridgewater | 4.5 | Bridgewater | 35 | 42 | Bridgewater | 4824 | 4824 | Arthurs Lake (DL) | Load transfer capacity (MVA)3 |  |  | Bridgewater | 70
Burnie | 34.0843 | 35.846 | 36.4111 | 37.3552 | 38.4612 | 39.7109 | 40.77 | 41.9932 | 42.5467 | 43.0904 | 43.4941 | 43.8373 | 0.99624 | 0.93786 | Burnie | 61.7219 | 62.1198 | 62.1073 | 62.8981 | 64.0254 | 65.3659 | 66.5339 | 67.4181 | 67.839 | 68.198 | 68.4344 | 69.082 | 0.99909 | 0.9684 | Burnie | 3.5 | Burnie | 60 | 72 | Burnie | 7096 | 6031.5 | Arthurs Lake (DL) | Load transfer capacity (MVA)4 |  |  | Burnie | 120
Chapel Street | 17.7188 | 18.6347 | 18.9284 | 19.4192 | 19.9942 | 20.6439 | 21.1944 | 21.8303 | 22.1181 | 22.4007 | 22.6106 | 22.789 | 0.99982 | 0.96596 | Chapel Street | 36.972 | 37.2104 | 37.2029 | 37.6765 | 38.3518 | 39.1548 | 39.8545 | 40.3841 | 40.6362 | 40.8513 | 40.9928 | 41.3808 | 0.99999 | 1 | Chapel Street | 8.5 | Chapel Street | 60 | 72 | Chapel Street | 4824 | 4824 | Arthurs Lake (DL) | Load transfer capacity (MVA)5 |  |  | Chapel Street | 120
Creek Road | 41.0703 | 43.1931 | 43.874 | 45.0116 | 46.3443 | 47.8502 | 49.1263 | 50.6003 | 51.2673 | 51.9223 | 52.4088 | 52.8224 | 0.99958 | 0.96484 | Creek Road | 88.6872 | 89.259 | 89.241 | 90.3772 | 91.9971 | 93.9232 | 95.6016 | 96.872 | 97.4768 | 97.9927 | 98.3323 | 99.2629 | 0.9911 | 1 | Creek Road | 10 | Creek Road | 120 | 72 | Creek Road | 4824 | 5087 | Avoca | Load transfer capacity (MVA)1 | St Marys | 4.6 | Creek Road | 180
Derby | 5.6047 | 5.8944 | 5.9874 | 6.1426 | 6.3245 | 6.53 | 6.7041 | 6.9053 | 6.9963 | 7.0857 | 7.1521 | 7.2085 | 0.99081 | 0.78267 | Derby | 3.4247 | 3.4468 | 3.4461 | 3.4899 | 3.5525 | 3.6269 | 3.6917 | 3.7407 | 3.7641 | 3.784 | 3.7971 | 3.8331 | 0.9769 | 0.69464 | Derby | 0.5 | Derby | 0 | 0 | Derby | 8723.5 | 8723.5 | Avoca | Load transfer capacity (MVA)2 | Palmerston | 4.6 | Derby | 25
Derwent Bridge | 0.23429 | 0.2464 | 0.25029 | 0.25678 | 0.26438 | 0.27297 | 0.28025 | 0.28866 | 0.29246 | 0.2962 | 0.29898 | 0.30133 | 0.9815 | 0.49386 | Derwent Bridge | 0.31649 | 0.31853 | 0.31847 | 0.32252 | 0.3283 | 0.33518 | 0.34116 | 0.3457 | 0.34786 | 0.3497 | 0.35091 | 0.35423 | 0.98716 | 0.75693 | Derwent Bridge | 8.5 | Derwent Bridge | 0 | 0 | Derwent Bridge | 8657.5 | 8657.5 | Avoca | Load transfer capacity (MVA)3 |  |  | Derwent Bridge | 6
Devonport | 28.8693 | 30.3615 | 30.8401 | 31.6398 | 32.5765 | 33.6351 | 34.5321 | 35.5682 | 36.037 | 36.4974 | 36.8394 | 37.1301 | 0.99106 | 0.85864 | Devonport | 57.4129 | 57.7831 | 57.7714 | 58.507 | 59.5556 | 60.8025 | 61.889 | 62.7115 | 63.103 | 63.4369 | 63.6568 | 64.2593 | 0.99725 | 0.98848 | Devonport | 2 | Devonport | 60 | 72 | Devonport | 4825 | 4824 | Avoca | Load transfer capacity (MVA)4 |  |  | Devonport | 110
Electrona | 8.8817 | 9.3407 | 9.488 | 9.734 | 10.0222 | 10.3479 | 10.6238 | 10.9426 | 11.0868 | 11.2285 | 11.3337 | 11.4231 | 0.99719 | 0.99316 | Electrona | 15.4347 | 15.5342 | 15.5311 | 15.7288 | 16.0108 | 16.346 | 16.6381 | 16.8592 | 16.9644 | 17.0542 | 17.1133 | 17.2753 | 0.99905 | 0.96119 | Electrona | 12.5 | Electrona | 25 | 30 | Electrona | 4736.5 | 4732 | Avoca | Load transfer capacity (MVA)5 |  |  | Electrona | 50
Emu Bay (RT) | 6.5005 | 6.8364 | 6.9442 | 7.1243 | 7.3352 | 7.5736 | 7.7755 | 8.0088 | 8.1144 | 8.2181 | 8.2951 | 8.3605 | 0.9791 | 0.42035 | Emu Bay (RT) | 9.0186 | 9.0768 | 9.0749 | 9.1905 | 9.3552 | 9.5511 | 9.7217 | 9.8509 | 9.9124 | 9.9649 | 9.9994 | 10.0941 | 0.98074 | 0.79298 | Emu Bay (RT) | 4 | Emu Bay (RT) | 30 | 30 | Emu Bay (RT) | 4824 | 4824 | Bridgewater | Load transfer capacity (MVA)1 |  |  | Emu Bay (RT) | 76
George Town | 10.8329 | 11.3928 | 11.5724 | 11.8725 | 12.224 | 12.6212 | 12.9578 | 13.3466 | 13.5225 | 13.6953 | 13.8236 | 13.9327 | 0.99635 | 0.884 | George Town | 18.8071 | 18.9284 | 18.9246 | 19.1655 | 19.5091 | 19.9175 | 20.2734 | 20.5428 | 20.6711 | 20.7805 | 20.8525 | 21.0498 | 0.99971 | 0.98843 | George Town | 4 | George Town | 48 | 48 | George Town | 4713 | 4713 | Bridgewater | Load transfer capacity (MVA)2 |  |  | George Town | 96
Hadspen | 34.3141 | 36.0877 | 36.6565 | 37.607 | 38.7205 | 39.9786 | 41.0448 | 42.2763 | 42.8336 | 43.3809 | 43.7873 | 44.1329 | 0.99922 | 1 | Hadspen | 56.613 | 56.978 | 56.9665 | 57.6918 | 58.7259 | 59.9554 | 61.0268 | 61.8377 | 62.2238 | 62.5531 | 62.7699 | 63.3639 | 0.99973 | 0.99582 | Hadspen | 1.5 | Hadspen | 50 | 60 | Hadspen | 4916.5 | 4827 | Bridgewater | Load transfer capacity (MVA)3 |  |  | Hadspen | 100
Huon River | 0.61083 | 0.6424 | 0.65253 | 0.66945 | 0.68927 | 0.71167 | 0.73064 | 0.75257 | 0.76249 | 0.77223 | 0.77946 | 0.78561 | 0.641 | 0.83697 | Huon River | 0.71774 | 0.72237 | 0.72222 | 0.73142 | 0.74453 | 0.76012 | 0.7737 | 0.78398 | 0.78887 | 0.79305 | 0.7958 | 0.80333 | 0.66532 | 0.75717 | Huon River | 52.5 | Huon River | 0 | 0 | Huon River | 8748 | 8748 | Bridgewater | Load transfer capacity (MVA)4 |  |  | Huon River | 25
Kermandie | 6.6328 | 6.9756 | 7.0856 | 7.2693 | 7.4845 | 7.7277 | 7.9338 | 8.1719 | 8.2796 | 8.3854 | 8.464 | 8.5307 | 0.97932 | 0.96533 | Kermandie | 8.5108 | 8.5657 | 8.564 | 8.673 | 8.8285 | 9.0133 | 9.1744 | 9.2963 | 9.3543 | 9.4038 | 9.4364 | 9.5257 | 0.99183 | 0.96604 | Kermandie | 11.5 | Kermandie | 25 | 37.5 | Kermandie | 4811 | 4811 | Bridgewater | Load transfer capacity (MVA)5 |  |  | Kermandie | 50
Kingston 11kV | 12.2529 | 12.8862 | 13.0893 | 13.4287 | 13.8263 | 14.2756 | 14.6563 | 15.096 | 15.295 | 15.4904 | 15.6356 | 15.759 | 0.99745 | 0.93731 | Kingston 11kV | 26.3672 | 26.5372 | 26.5319 | 26.8697 | 27.3513 | 27.9239 | 28.4229 | 28.8006 | 28.9804 | 29.1338 | 29.2348 | 29.5115 | 0.99998 | 1 | Kingston 11kV | 4 | Kingston 11kV | 35 | 42 | Kingston 11kV | 4805.5 | 4804 | Burnie | Load transfer capacity (MVA)1 | Port Latta | 8.8 | Kingston 11kV | 70
Kingston 33kV | 4.8757 | 5.1277 | 5.2085 | 5.3436 | 5.5018 | 5.6806 | 5.8321 | 6.007 | 6.0862 | 6.164 | 6.2217 | 6.2708 | 0.99963 | 0.9369 | Kingston 33kV | 10.9108 | 10.9811 | 10.9789 | 11.1187 | 11.318 | 11.5549 | 11.7614 | 11.9177 | 11.9921 | 12.0556 | 12.0974 | 12.2119 | 0.99637 | 0.94758 | Kingston 33kV | 7 | Kingston 33kV | 60 | 72 | Kingston 33kV | 4823.5 | 4823 | Burnie | Load transfer capacity (MVA)2 | Ulverstone | 8.8 | Kingston 33kV | 120
Knights Road | 13.1525 | 13.8323 | 14.0504 | 14.4147 | 14.8415 | 15.3237 | 15.7324 | 16.2044 | 16.418 | 16.6278 | 16.7836 | 16.916 | 0.98584 | 0.95494 | Knights Road | 19.5009 | 19.6267 | 19.6227 | 19.8726 | 20.2288 | 20.6523 | 21.0213 | 21.3007 | 21.4336 | 21.5471 | 21.6218 | 21.8264 | 0.9948 | 1 | Knights Road | 17 | Knights Road | 20 | 24 | Knights Road | 4859 | 4824 | Burnie | Load transfer capacity (MVA)3 |  |  | Knights Road | 40
Lindisfarne | 18.2318 | 19.1742 | 19.4764 | 19.9814 | 20.573 | 21.2415 | 21.808 | 22.4623 | 22.7584 | 23.0492 | 23.2652 | 23.4487 | 0.99983 | 1 | Lindisfarne | 37.1821 | 37.4219 | 37.4143 | 37.8907 | 38.5698 | 39.3774 | 40.081 | 40.6137 | 40.8672 | 41.0835 | 41.2259 | 41.616 | 0.9986 | 1 | Lindisfarne | 9.5 | Lindisfarne | 60 | 78 | Lindisfarne | 4824 | 4824 | Burnie | Load transfer capacity (MVA)4 |  |  | Lindisfarne | 120
Meadowbank | 6.6837 | 7.0291 | 15.7316 | 16.1395 | 16.6173 | 17.1573 | 17.6148 | 18.1434 | 18.3825 | 18.6174 | 18.7918 | 18.9401 | 0.95789 | 0.80781 | Meadowbank | 4.423 | 4.4515 | 13.6996 | 13.874 | 14.1227 | 14.4183 | 14.676 | 14.871 | 14.9638 | 15.043 | 15.0952 | 15.238 | 0.99764 | 0.76365 | Meadowbank | 17.5 | Meadowbank | 0 | 0 | Meadowbank | 8681 | 8681 | Burnie | Load transfer capacity (MVA)5 |  |  | Meadowbank | 25
Mornington | 19.7185 | 20.7377 | 21.0646 | 21.6108 | 22.2506 | 22.9736 | 23.5863 | 24.294 | 24.6142 | 24.9287 | 25.1623 | 25.3608 | 0.99805 | 1 | Mornington | 40.4191 | 40.6797 | 40.6715 | 41.1893 | 41.9276 | 42.8054 | 43.5703 | 44.1493 | 44.4249 | 44.6601 | 44.8148 | 45.239 | 0.99848 | 1 | Mornington | 3.5 | Mornington | 60 | 72 | Mornington | 4824 | 4824 | Chapel Street | Load transfer capacity (MVA)1 |  |  | Mornington | 120
Mowbray | 17.7798 | 18.6987 | 18.9935 | 19.486 | 20.0629 | 20.7148 | 21.2673 | 21.9054 | 22.1941 | 22.4777 | 22.6883 | 22.8673 | 0.98961 | 0.93537 | Mowbray | 37.7013 | 37.9444 | 37.9367 | 38.4197 | 39.1084 | 39.9272 | 40.6406 | 41.1807 | 41.4378 | 41.6571 | 41.8015 | 42.1971 | 0.9972 | 0.97894 | Mowbray | 3.5 | Mowbray | 50 | 60 | Mowbray | 4824 | 4824 | Chapel Street | Load transfer capacity (MVA)2 |  |  | Mowbray | 100
New Norfolk | 12.0862 | 12.7109 | 12.9113 | 13.2461 | 13.6382 | 14.0814 | 14.4569 | 14.8907 | 15.087 | 15.2797 | 15.4229 | 15.5446 | 0.99661 | 0.98903 | New Norfolk | 17.7724 | 17.887 | 17.8834 | 18.1111 | 18.4357 | 18.8217 | 19.158 | 19.4126 | 19.5338 | 19.6372 | 19.7052 | 19.8917 | 0.99994 | 0.90236 | New Norfolk | 19 | New Norfolk | 30 | 37 | New Norfolk | 4824 | 4824 | Chapel Street | Load transfer capacity (MVA)3 |  |  | New Norfolk | 60
Newton | 3.3228 | 3.4946 | 3.5497 | 3.6417 | 3.7495 | 3.8714 | 3.9746 | 4.0939 | 4.1478 | 4.2008 | 4.2402 | 4.2737 | 0.99726 | 0.85116 | Newton | 4.1058 | 4.1323 | 4.1315 | 4.1841 | 4.2591 | 4.3482 | 4.4259 | 4.4847 | 4.5127 | 4.5366 | 4.5524 | 4.5954 | 0.99991 | 0.88727 | Newton | 1.5 | Newton | 0 | 0 | Newton | 8745.5 | 8745.5 | Chapel Street | Load transfer capacity (MVA)4 |  |  | Newton | 22.5
North Hobart | 16.7929 | 17.6608 | 17.9392 | 18.4044 | 18.9493 | 19.565 | 20.0868 | 20.6895 | 20.9622 | 21.23 | 21.4289 | 21.598 | 0.99313 | 0.88363 | North Hobart | 36.7547 | 36.9917 | 36.9843 | 37.4552 | 38.1265 | 38.9247 | 39.6203 | 40.1468 | 40.3974 | 40.6112 | 40.752 | 41.1377 | 0.99859 | 1 | North Hobart | 7 | North Hobart | 45 | 50 | North Hobart | 4824 | 4824 | Chapel Street | Load transfer capacity (MVA)5 |  |  | North Hobart | 90
Norwood | 16.2809 | 17.1224 | 17.3923 | 17.8433 | 18.3716 | 18.9686 | 19.4744 | 20.0588 | 20.3231 | 20.5828 | 20.7757 | 20.9396 | 1 | 1 | Norwood | 30.7146 | 30.9127 | 30.9065 | 31.3 | 31.861 | 32.528 | 33.1093 | 33.5493 | 33.7587 | 33.9374 | 34.055 | 34.3773 | 0.99998 | 0.96163 | Norwood | 1 | Norwood | 50 | 60 | Norwood | 4824 | 4824 | Creek Road | Load transfer capacity (MVA)1 |  |  | Norwood | 100
Palmerston | 12.9431 | 13.6121 | 13.8267 | 14.1852 | 14.6052 | 15.0798 | 15.4819 | 15.9465 | 16.1567 | 16.3631 | 16.5164 | 16.6467 | 0.95131 | 0.8283 | Palmerston | 9.3818 | 9.4423 | 9.4404 | 9.5606 | 9.7319 | 9.9357 | 10.1132 | 10.2476 | 10.3116 | 10.3662 | 10.4021 | 10.5005 | 0.99514 | 0.78234 | Palmerston | 13.5 | Palmerston | 25 | 30 | Palmerston | 4824 | 4824 | Creek Road | Load transfer capacity (MVA)2 |  |  | Palmerston | 50
Port Latta (RT) | 8.6584 | 9.1059 | 9.2494 | 9.4893 | 9.7702 | 10.0877 | 10.3567 | 10.6675 | 10.8081 | 10.9462 | 11.0487 | 11.1359 | 0.94677 | 0.76875 | Port Latta (RT) | 7.45 | 7.4981 | 7.4965 | 7.592 | 7.7281 | 7.8899 | 8.0309 | 8.1376 | 8.1884 | 8.2317 | 8.2602 | 8.3384 | 0.99929 | 0.96743 | Port Latta (RT) | 26 | Port Latta (RT) | 25 | 37.5 | Port Latta (RT) | 4824 | 4824 | Creek Road | Load transfer capacity (MVA)3 |  |  | Port Latta (RT) | 50
Queenstown | 3.4436 | 3.6216 | 3.6786 | 3.774 | 3.8858 | 4.012 | 4.119 | 4.2426 | 4.2985 | 4.3535 | 4.3943 | 4.4289 | 0.99965 | 0.92005 | Queenstown | 5.9564 | 5.9948 | 5.9936 | 6.0699 | 6.1787 | 6.3081 | 6.4208 | 6.5061 | 6.5467 | 6.5814 | 6.6042 | 6.6667 | 0.99994 | 0.87538 | Queenstown | 22.5 | Queenstown | 25 | 30 | Queenstown | 4824 | 4824 | Creek Road | Load transfer capacity (MVA)4 |  |  | Queenstown | 50
Railton | 35.9498 | 37.8079 | 38.4039 | 39.3997 | 40.5662 | 41.8844 | 43.0014 | 44.2916 | 44.8754 | 45.4488 | 45.8746 | 46.2366 | 0.9791 | 0.78059 | Railton | 53.5273 | 53.8724 | 53.8616 | 54.5473 | 55.525 | 56.6875 | 57.7005 | 58.4673 | 58.8323 | 59.1436 | 59.3486 | 59.9103 | 0.98125 | 1 | Railton | 17.5 | Railton | 50 | 60 | Railton | 4830.5 | 4824 | Creek Road | Load transfer capacity (MVA)5 |  |  | Railton | 100
Risdon 33kV | 38.7052 | 40.7058 | 41.3474 | 42.4196 | 43.6755 | 45.0947 | 46.2973 | 47.6864 | 48.3149 | 48.9323 | 49.3908 | 49.7805 | 0.97794 | 0.7858 | Risdon 33kV | 67.9432 | 68.3813 | 68.3675 | 69.238 | 70.479 | 71.9545 | 73.2403 | 74.2136 | 74.6769 | 75.0721 | 75.3323 | 76.0453 | 0.98433 | 0.95396 | Risdon 33kV | 5.5 | Risdon 33kV | 100 | 60 | Risdon 33kV | 4824 | 4925 | Derby | Load transfer capacity (MVA)1 | Scottsdale | 5.3 | Risdon 33kV | 150
Rokeby | 11.1132 | 11.6876 | 11.8718 | 12.1796 | 12.5402 | 12.9477 | 13.293 | 13.6919 | 13.8723 | 14.0496 | 14.1812 | 14.2931 | 0.99809 | 0.99563 | Rokeby | 23.1812 | 23.3307 | 23.326 | 23.6229 | 24.0464 | 24.5498 | 24.9885 | 25.3206 | 25.4786 | 25.6135 | 25.7022 | 25.9455 | 1 | 0.96359 | Rokeby | 4 | Rokeby | 35 | 42 | Rokeby | 4698 | 4693 | Derby | Load transfer capacity (MVA)2 |  |  | Rokeby | 70
Rosebery 22kV | 1.2321 | 1.2958 | 1.3163 | 1.3504 | 1.3904 | 1.4355 | 1.4738 | 1.5181 | 1.5381 | 1.5577 | 1.5723 | 1.5847 | 1 | 0.58328 | Rosebery 22kV | 2.3944 | 2.4099 | 2.4094 | 2.4401 | 2.4838 | 2.5358 | 2.5811 | 2.6154 | 2.6317 | 2.6457 | 2.6548 | 2.68 | 1 | 0.96808 | Rosebery 22kV | 2.5 | Rosebery 22kV | 10 | 10 | Rosebery 22kV | 8752.5 | 8752.5 | Derby | Load transfer capacity (MVA)3 |  |  | Rosebery 22kV | 16
Rosebery 44kV | 13.9079 | 14.6267 | 14.8573 | 15.2425 | 15.6938 | 16.2038 | 16.6359 | 17.1351 | 17.3609 | 17.5827 | 17.7475 | 17.8875 | 0.88317 | 0.81631 | Rosebery 44kV | 17.0539 | 17.1639 | 17.1604 | 17.3789 | 17.6904 | 18.0608 | 18.3835 | 18.6278 | 18.7441 | 18.8433 | 18.9086 | 19.0876 | 0.86886 | 0.83391 | Rosebery 44kV | 523 | Rosebery 44kV | 66 | 72 | Rosebery 44kV | 4824 | 4824 | Derby | Load transfer capacity (MVA)4 |  |  | Rosebery 44kV | 102
Savage River DL | 0.75017 | 0.78895 | 0.80138 | 0.82216 | 0.84651 | 0.87401 | 0.89732 | 0.92424 | 0.93643 | 0.94839 | 0.95728 | 0.96483 | 1 | 0.54092 | Savage River DL | 1.1492 | 1.1566 | 1.1564 | 1.1711 | 1.1921 | 1.2171 | 1.2388 | 1.2553 | 1.2631 | 1.2698 | 1.2742 | 1.2863 | 1 | 0.8085 | Savage River DL | 805 | Savage River DL | 22.5 | 27 | Savage River DL | 4794.5 | 4794.5 | Derby | Load transfer capacity (MVA)5 |  |  | Savage River DL | 45
Scottsdale | 9.7165 | 10.2187 | 10.3798 | 10.6489 | 10.9642 | 11.3205 | 11.6224 | 11.9711 | 12.1289 | 12.2838 | 12.3989 | 12.4968 | 0.98927 | 0.89632 | Scottsdale | 12.4193 | 12.4994 | 12.4969 | 12.656 | 12.8828 | 13.1525 | 13.3876 | 13.5655 | 13.6501 | 13.7224 | 13.7699 | 13.9003 | 0.99887 | 0.99022 | Scottsdale | 18 | Scottsdale | 31.5 | 36 | Scottsdale | 4824 | 4824 | Derwent Bridge | Load transfer capacity (MVA)1 |  |  | Scottsdale | 63
Sheffield | 6.1049 | 6.4204 | 6.5216 | 6.6907 | 6.8888 | 7.1127 | 7.3024 | 7.5215 | 7.6206 | 7.718 | 7.7903 | 7.8517 | 0.99997 | 0.61158 | Sheffield | 3.0579 | 3.0776 | 3.077 | 3.1162 | 3.172 | 3.2384 | 3.2963 | 3.3401 | 3.361 | 3.3788 | 3.3905 | 3.4226 | 0.99287 | 0.80394 | Sheffield | 2 | Sheffield | 0 | 0 | Sheffield | 8749.5 | 8749.5 | Derwent Bridge | Load transfer capacity (MVA)2 |  |  | Sheffield | 25
Smithton | 19.4177 | 20.4213 | 20.7433 | 21.2811 | 21.9112 | 22.6232 | 23.2265 | 23.9234 | 24.2387 | 24.5484 | 24.7785 | 24.974 | 0.94511 | 0.80678 | Smithton | 21.6235 | 21.7629 | 21.7585 | 22.0355 | 22.4305 | 22.9001 | 23.3093 | 23.6191 | 23.7665 | 23.8923 | 23.9751 | 24.202 | 0.98875 | 0.89408 | Smithton | 15.5 | Smithton | 35 | 42 | Smithton | 4824 | 4824 | Derwent Bridge | Load transfer capacity (MVA)3 |  |  | Smithton | 70
Sorell | 19.1532 | 20.1432 | 20.4607 | 20.9912 | 21.6127 | 22.315 | 22.9101 | 23.5975 | 23.9085 | 24.214 | 24.4409 | 24.6338 | 0.99848 | 1 | Sorell | 37.1113 | 37.3506 | 37.3431 | 37.8185 | 38.4964 | 39.3024 | 40.0047 | 40.5363 | 40.7893 | 41.0052 | 41.1473 | 41.5368 | 0.9986 | 0.90758 | Sorell | 16 | Sorell | 60 | 78 | Sorell | 4820.5 | 4819.5 | Derwent Bridge | Load transfer capacity (MVA)4 |  |  | Sorell | 120
St Leonards | 15.8781 | 16.6988 | 16.9621 | 17.4019 | 17.9171 | 18.4993 | 18.9927 | 19.5625 | 19.8204 | 20.0736 | 20.2617 | 20.4216 | 0.99898 | 1 | St Leonards | 29.9459 | 30.139 | 30.1329 | 30.5166 | 31.0636 | 31.7139 | 32.2806 | 32.7096 | 32.9138 | 33.088 | 33.2027 | 33.5169 | 0.99999 | 0.96901 | St Leonards | 2.5 | St Leonards | 60 | 78 | St Leonards | 4824 | 4824 | Derwent Bridge | Load transfer capacity (MVA)5 |  |  | St Leonards | 120
St Marys | 9.0396 | 9.5068 | 9.6567 | 9.9071 | 10.2004 | 10.5318 | 10.8127 | 11.1371 | 11.2839 | 11.4281 | 11.5352 | 11.6262 | 1 | 0.72187 | St Marys | 16.3642 | 16.4697 | 16.4664 | 16.676 | 16.9749 | 17.3303 | 17.64 | 17.8744 | 17.986 | 18.0812 | 18.1438 | 18.3156 | 0.99986 | 0.98284 | St Marys | 2.5 | St Marys | 10 | 12 | St Marys | 5333 | 4951.5 | Devonport | Load transfer capacity (MVA)1 | Railton | 5.1 | St Marys | 20
Trevallyn | 38.3144 | 40.2948 | 40.93 | 41.9913 | 43.2345 | 44.6394 | 45.8298 | 47.2049 | 47.8271 | 48.4382 | 48.8921 | 49.2779 | 0.99986 | 1 | Trevallyn | 73.613 | 74.0877 | 74.0727 | 75.0158 | 76.3604 | 77.9591 | 79.3522 | 80.4067 | 80.9087 | 81.3369 | 81.6187 | 82.3912 | 0.99984 | 0.95866 | Trevallyn | 2 | Trevallyn | 100 | 130 | Trevallyn | 4824 | 4824 | Devonport | Load transfer capacity (MVA)2 | Ulverstone | 6.3 | Trevallyn | 150
Triabunna (RT) | 4.5504 | 4.7856 | 4.8611 | 4.9871 | 5.1348 | 5.3016 | 5.443 | 5.6063 | 5.6802 | 5.7528 | 5.8067 | 5.8525 | 0.99473 | 0.70509 | Triabunna (RT) | 7.5785 | 7.6273 | 7.6258 | 7.7229 | 7.8613 | 8.0259 | 8.1693 | 8.2779 | 8.3296 | 8.3736 | 8.4027 | 8.4822 | 0.99996 | 0.84397 | Triabunna (RT) | 2 | Triabunna (RT) | 25 | 30 | Triabunna (RT) | 4800 | 4800 | Devonport | Load transfer capacity (MVA)3 |  |  | Triabunna (RT) | 50
Tungatinah | 0.60813 | 0.63957 | 0.64965 | 0.66649 | 0.68623 | 0.70853 | 0.72742 | 0.74925 | 0.75912 | 0.76882 | 0.77603 | 0.78215 | 0.99908 | 0.58677 | Tungatinah | 0.97194 | 0.97821 | 0.97801 | 0.99046 | 1.0082 | 1.0293 | 1.0477 | 1.0616 | 1.0683 | 1.0739 | 1.0776 | 1.0878 | 0.99949 | 0.89714 | Tungatinah | 2.5 | Tungatinah | 0 | 0 | Tungatinah | 8760.5 | 8760.5 | Devonport | Load transfer capacity (MVA)4 |  |  | Tungatinah | 13
Ulverstone | 15.1241 | 15.9058 | 16.1566 | 16.5755 | 17.0662 | 17.6208 | 18.0907 | 18.6335 | 18.8791 | 19.1203 | 19.2995 | 19.4518 | 0.99709 | 0.92286 | Ulverstone | 31.0919 | 31.2924 | 31.2861 | 31.6844 | 32.2524 | 32.9276 | 33.516 | 33.9614 | 34.1734 | 34.3543 | 34.4733 | 34.7996 | 0.99973 | 0.93687 | Ulverstone | 1.5 | Ulverstone | 45 | 54 | Ulverstone | 4823.5 | 4823.5 | Devonport | Load transfer capacity (MVA)5 |  |  | Ulverstone | 90
Waddamana | 0.40619 | 0.42719 | 0.43392 | 0.44517 | 0.45835 | 0.47325 | 0.48587 | 0.50045 | 0.50704 | 0.51352 | 0.51833 | 0.52242 | 0.96814 | 0.55644 | Waddamana | 0.67308 | 0.67742 | 0.67729 | 0.68591 | 0.6982 | 0.71282 | 0.72556 | 0.7352 | 0.73979 | 0.74371 | 0.74628 | 0.75335 | 0.99498 | 0.58751 | Waddamana | 4 | Waddamana | 0 | 0 | Waddamana | 8732 | 8732 | Electrona | Load transfer capacity (MVA)1 | Kingston | 8 | Waddamana | 4
Wesley Vale | 9.6106 | 10.1073 | 10.2666 | 10.5328 | 10.8447 | 11.1971 | 11.4957 | 11.8406 | 11.9967 | 12.1499 | 12.2638 | 12.3606 | 0.99022 | 0.88063 | Wesley Vale | 11.0843 | 11.1558 | 11.1535 | 11.2956 | 11.498 | 11.7387 | 11.9485 | 12.1073 | 12.1829 | 12.2474 | 12.2898 | 12.4061 | 0.99971 | 0.99692 | Wesley Vale | 2.5 | Wesley Vale | 25 | 28 | Wesley Vale | 2834 | 2834 | Electrona | Load transfer capacity (MVA)2 | Knights Road | 3 | Wesley Vale | 50
[38 empty] | Electrona | Load transfer capacity (MVA)3
Zs-Bellerive | 5.3757 | 5.6535 | 5.7426 | 5.8915 | 6.066 | 6.2631 | 6.4301 | 6.623 | 6.7103 | 6.7961 | 6.8598 | 6.9139 | 0.99995 | 0 | Zs-Bellerive | 9.7512 | 9.8141 | 9.8121 | 9.937 | 10.1151 | 10.3269 | 10.5114 | 10.6511 | 10.7176 | 10.7743 | 10.8117 | 10.914 | 0.99994 | 0 | Zs-Bellerive | 5 | Zs-Bellerive | 22.5 | 22.9 |  |  |  | Electrona | Load transfer capacity (MVA)4 |  |  | Zs-Bellerive | 45 | Zone | Summer | Winter | Summer firm | Winter firm
Zs-Cambridge | 3.7737 | 3.9687 | 4.0313 | 4.1358 | 4.2583 | 4.3966 | 4.5139 | 4.6493 | 4.7106 | 4.7708 | 4.8155 | 4.8535 | 0.99996 | 0 | Zs-Cambridge | 7.2932 | 7.3403 | 7.3388 | 7.4322 | 7.5654 | 7.7238 | 7.8618 | 7.9663 | 8.016 | 8.0585 | 8.0864 | 8.1629 | 0.99994 | 0 | Zs-Cambridge | 3.5 | Zs-Cambridge | 20 | 26 |  |  |  | Electrona | Load transfer capacity (MVA)5 |  |  | Zs-Cambridge | 40 | Zs-Bellerive | 27.2071 | 42.8683 | 13.6035 | 21.4341
Zs-Claremont | 12.4589 | 13.1029 | 13.3094 | 13.6545 | 14.0588 | 14.5156 | 14.9028 | 15.3499 | 15.5522 | 15.7509 | 15.8985 | 16.024 | 0.99921 | 0 | Zs-Claremont | 23.3423 | 23.4928 | 23.488 | 23.7871 | 24.2134 | 24.7204 | 25.1621 | 25.4965 | 25.6557 | 25.7914 | 25.8808 | 26.1258 | 0.99959 | 0 | Zs-Claremont | 7 | Zs-Claremont | 22.5 | 30 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)1 |  |  | Zs-Claremont | 50 | Zs-Cambridge | 17.7189 | 17.7189 | 0 | 0
Zs-Derwent Park | 10.1769 | 10.7029 | 10.8716 | 11.1535 | 11.4838 | 11.8569 | 12.1731 | 12.5384 | 12.7036 | 12.8659 | 12.9865 | 13.089 | 0.97503 | 0 | Zs-Derwent Park | 18.6282 | 18.7483 | 18.7445 | 18.9832 | 19.3234 | 19.728 | 20.0805 | 20.3473 | 20.4744 | 20.5827 | 20.6541 | 20.8495 | 0.98841 | 0 | Zs-Derwent Park | 3.5 | Zs-Derwent Park | 22.5 | 22.9 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)2 |  |  | Zs-Derwent Park | 45 | Zs-Claremont | 27.0356 | 44.0686 | 13.4321 | 21.4341
Zs-East Hobart | 19.4834 | 20.4905 | 20.8135 | 21.3532 | 21.9854 | 22.6997 | 23.3051 | 24.0044 | 24.3208 | 24.6315 | 24.8623 | 25.0585 | 0.97136 | 0 | Zs-East Hobart | 28.1925 | 28.3743 | 28.3686 | 28.7298 | 29.2447 | 29.857 | 30.3905 | 30.7944 | 30.9866 | 31.1506 | 31.2586 | 31.5544 | 0.98513 | 0 | Zs-East Hobart | 6 | Zs-East Hobart | 60 | 78 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)3 |  |  | Zs-East Hobart | 90 | Zs-Derwent Park | 26.8641 | 40.8666 | 13.4321 | 19.4325
Zs-Geilston Bay | 8.602 | 9.0466 | 9.1892 | 9.4275 | 9.7066 | 10.022 | 10.2893 | 10.598 | 10.7377 | 10.8749 | 10.9768 | 11.0634 | 0.99947 | 0 | Zs-Geilston Bay | 18.6248 | 18.7449 | 18.7411 | 18.9797 | 19.3199 | 19.7244 | 20.0768 | 20.3436 | 20.4706 | 20.579 | 20.6503 | 20.8457 | 0.99982 | 0 | Zs-Geilston Bay | 13.5 | Zs-Geilston Bay | 22.5 | 22.9 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)4 |  |  | Zs-Geilston Bay | 45 | Zs-East Hobart | 42.7196 | 42.7196 | 42.7054 | 42.7054
Zs-Howrah | 8.668 | 9.116 | 9.2597 | 9.4998 | 9.781 | 10.0989 | 10.3682 | 10.6793 | 10.82 | 10.9583 | 11.061 | 11.1482 | 0.99379 | 0 | Zs-Howrah | 17.0197 | 17.1295 | 17.126 | 17.3441 | 17.6549 | 18.0245 | 18.3466 | 18.5905 | 18.7065 | 18.8055 | 18.8707 | 19.0493 | 0.99837 | 0 | Zs-Howrah | 7 | Zs-Howrah | 25 | 32.5 |  |  |  | Emu Bay (RT) | Load transfer capacity (MVA)5 |  |  | Zs-Howrah | 50 | Zs-Geilston Bay | 27.0356 | 42.8683 | 13.4321 | 21.4341
Zs-New Town | 10.5437 | 11.0886 | 11.2634 | 11.5555 | 11.8976 | 12.2842 | 12.6118 | 12.9902 | 13.1615 | 13.3296 | 13.4545 | 13.5607 | 0.99487 | 0 | Zs-New Town | 21.1734 | 21.3099 | 21.3056 | 21.5769 | 21.9636 | 22.4234 | 22.8241 | 23.1274 | 23.2718 | 23.395 | 23.4761 | 23.6983 | 0.99713 | 0 | Zs-New Town | 15 | Zs-New Town | 22.5 | 22.9 |  |  |  | George Town | Load transfer capacity (MVA)1 | Scottsdale | 2.1 | Zs-New Town | 45 | Zs-Howrah | 48.0124 | 48.0124 | 24.0062 | 24.0062
Zs-Rosny Park | 7.512 | 7.9002 | 8.0248 | 8.2329 | 8.4766 | 8.752 | 8.9855 | 9.2551 | 9.377 | 9.4969 | 9.5858 | 9.6615 | 0.99871 | 0 | Zs-Rosny Park | 15.533 | 15.6332 | 15.63 | 15.8291 | 16.1128 | 16.4501 | 16.7441 | 16.9666 | 17.0725 | 17.1629 | 17.2223 | 17.3853 | 0.99939 | 0 | Zs-Rosny Park | 2.5 | Zs-Rosny Park | 0 | 0 |  |  |  | George Town | Load transfer capacity (MVA)2 | Trevallyn | 2.1 | Zs-Rosny Park | 25 | Zs-New Town | 34.8662 | 44.0686 | 13.4321 | 21.4341
Zs-Sandy Bay | 14.376 | 15.1191 | 15.3574 | 15.7556 | 16.2221 | 16.7492 | 17.1959 | 17.7118 | 17.9453 | 18.1746 | 18.3449 | 18.4896 | 0.99885 | 0 | Zs-Sandy Bay | 32.8514 | 33.0633 | 33.0566 | 33.4775 | 34.0775 | 34.791 | 35.4127 | 35.8833 | 36.1073 | 36.2984 | 36.4242 | 36.7689 | 0.99985 | 0 | Zs-Sandy Bay | 26.5 | Zs-Sandy Bay | 60 | 78 |  |  |  | George Town | Load transfer capacity (MVA)3 | Mowbray | 2.1 | Zs-Sandy Bay | 90 | Zs-Rosny Park | 20.6911 | 20.6911 | 0 | 0
Zs-Summerleas | 4.8599 | 5.1111 | 5.1917 | 5.3263 | 5.484 | 5.6622 | 5.8132 | 5.9876 | 6.0665 | 6.1441 | 6.2016 | 6.2506 | 0.99807 | 0 | Zs-Summerleas | 10.898 | 10.9683 | 10.9661 | 11.1057 | 11.3047 | 11.5414 | 11.7477 | 11.9038 | 11.9781 | 12.0415 | 12.0832 | 12.1976 | 0.99998 | 0 | Zs-Summerleas | 8.5 | Zs-Summerleas | 0 | 0 |  |  |  | George Town | Load transfer capacity (MVA)4 |  |  | Zs-Summerleas | 25 | Zs-Sandy Bay | 26.8641 | 44.0686 | 13.4321 | 21.4341
Zs-Trial Harbour | 1.2876 | 1.3542 | 1.3755 | 1.4112 | 1.453 | 1.5002 | 1.5402 | 1.5864 | 1.6073 | 1.6279 | 1.6431 | 1.6561 | 0.9971 | 0 | Zs-Trial Harbour | 2.3991 | 2.4146 | 2.4141 | 2.4449 | 2.4887 | 2.5408 | 2.5862 | 2.6206 | 2.6369 | 2.6509 | 2.6601 | 2.6852 | 0.98418 | 0 | Zs-Trial Harbour | 0 | Zs-Trial Harbour | 20 | 26 |  |  |  | George Town | Load transfer capacity (MVA)5 |  |  | Zs-Trial Harbour | 40 | Zs-Summerleas | 25.8353 | 25.8353 | 0 | 0
Zs-West Hobart | 15.8546 | 16.6741 | 16.937 | 17.3761 | 17.8906 | 18.4719 | 18.9645 | 19.5335 | 19.791 | 20.0439 | 20.2317 | 20.3913 | 0.99994 | 0 | Zs-West Hobart | 35.2518 | 35.4791 | 35.4719 | 35.9235 | 36.5674 | 37.333 | 38.0001 | 38.5051 | 38.7455 | 38.9505 | 39.0855 | 39.4554 | 0.99823 | 0 | Zs-West Hobart | 6.5 | Zs-West Hobart | 60 | 78 |  |  |  | Gordon | Load transfer capacity (MVA)1 |  |  | Zs-West Hobart | 90 | Zs-Trial Harbour | 18.186 | 18.186 | 0 | 0
[38 empty] | Gordon | Load transfer capacity (MVA)2 |  |  |  |  | Zs-West Hobart | 40.2962 | 67.9033 | 26.8641 | 45.2689
Summer | Actuals |  | Forecast | [11 empty] | Winter | Actuals |  | Forecast | [19 empty] | Gordon | Load transfer capacity (MVA)3
Feeder | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 |  |  | Feeder | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | [10 empty] | Gordon | Load transfer capacity (MVA)4
10001 | 88.6634 | 93.2462 | 94.7161 | 97.172 | 100.049 | 103.3 | 106.0549 | 109.237 | 110.6768 | 112.0909 | 113.1412 | 114.034 |  |  | 10001 | 203.058 | 204.3674 | 204.3261 | 206.9276 | 210.6365 | 215.0465 | 218.8893 | 221.7981 | 223.1827 | 224.3639 | 225.1415 | 227.2723 | [10 empty] | Gordon | Load transfer capacity (MVA)5
10002 | 91.8241 | 96.5702 | 98.0925 | 100.6359 | 103.6155 | 106.9824 | 109.8354 | 113.131 | 114.6221 | 116.0866 | 117.1744 | 118.099 |  |  | 10002 | 201.5688 | 202.8686 | 202.8276 | 205.41 | 209.0918 | 213.4693 | 217.2839 | 220.1715 | 221.5459 | 222.7184 | 223.4903 | 225.6055 | [10 empty] | Hadspen | Load transfer capacity (MVA)1 | Trevallyn | 26.7
10003 | 90.5741 | 95.2556 | 96.7571 | 99.266 | 102.205 | 105.526 | 108.3403 | 111.5909 | 113.0618 | 114.5064 | 115.5793 | 116.4913 |  |  | 10003 | 208.2177 | 209.5603 | 209.518 | 212.1856 | 215.9888 | 220.5107 | 224.4512 | 227.434 | 228.8537 | 230.0649 | 230.8622 | 233.0472 | [10 empty] | Hadspen | Load transfer capacity (MVA)2 | Norwood | 13.4
10007 | 109.0672 | 114.7046 | 116.5127 | 119.5338 | 123.0729 | 127.072 | 130.4608 | 134.3752 | 136.1464 | 137.8859 | 139.178 | 140.2762 |  |  | 10007 | 208.0883 | 209.4301 | 209.3877 | 212.0537 | 215.8545 | 220.3737 | 224.3117 | 227.2926 | 228.7115 | 229.9219 | 230.7188 | 232.9023 | [10 empty] | Hadspen | Load transfer capacity (MVA)3 | Palmerston | 5.3
10008 | 82.1664 | 86.4133 | 87.7755 | 90.0515 | 92.7176 | 95.7304 | 98.2834 | 101.2323 | 102.5666 | 103.8771 | 104.8505 | 105.6778 |  |  | 10008 | 195.9438 | 197.2073 | 197.1674 | 199.6778 | 203.2568 | 207.5122 | 211.2204 | 214.0273 | 215.3634 | 216.5032 | 217.2535 | 219.3097 | [10 empty] | Hadspen | Load transfer capacity (MVA)4
10022 | 80.9877 | 85.1737 | 86.5163 | 88.7597 | 91.3876 | 94.3571 | 96.8735 | 99.7801 | 101.0953 | 102.387 | 103.3464 | 104.1618 |  |  | 10022 | 186.8807 | 188.0857 | 188.0477 | 190.442 | 193.8554 | 197.914 | 201.4506 | 204.1278 | 205.402 | 206.4891 | 207.2047 | 209.1658 | [10 empty] | Hadspen | Load transfer capacity (MVA)5
10024 | 82.0903 | 86.3333 | 87.6943 | 89.9681 | 92.6318 | 95.6418 | 98.1924 | 101.1386 | 102.4717 | 103.781 | 104.7534 | 105.58 |  |  | 10024 | 195.1691 | 196.4276 | 196.3879 | 198.8883 | 202.4532 | 206.6918 | 210.3853 | 213.1811 | 214.5119 | 215.6472 | 216.3946 | 218.4426 | [10 empty] | Huon River | Load transfer capacity (MVA)1
10026 | 103.3306 | 108.6714 | 110.3845 | 113.2467 | 116.5996 | 120.3884 | 123.599 | 127.3075 | 128.9855 | 130.6335 | 131.8576 | 132.898 |  |  | 10026 | 196.5014 | 197.7685 | 197.7285 | 200.2461 | 203.8352 | 208.1027 | 211.8215 | 214.6364 | 215.9763 | 217.1193 | 217.8718 | 219.9338 | [10 empty] | Huon River | Load transfer capacity (MVA)2
11004 | 111.4324 | 117.192 | 119.0394 | 122.126 | 125.7418 | 129.8276 | 133.29 | 137.2892 | 139.0988 | 140.8761 | 142.1961 | 143.3181 |  |  | 11004 | 168.7489 | 169.8371 | 169.8027 | 171.9647 | 175.0469 | 178.7118 | 181.9053 | 184.3226 | 185.4733 | 186.4549 | 187.1011 | 188.8719 | [10 empty] | Huon River | Load transfer capacity (MVA)3
11005 | 115.3496 | 121.3117 | 123.224 | 126.4192 | 130.162 | 134.3915 | 137.9756 | 142.1154 | 143.9886 | 145.8284 | 147.1948 | 148.3563 |  |  | 11005 | 162.6469 | 163.6957 | 163.6626 | 165.7464 | 168.7172 | 172.2495 | 175.3275 | 177.6575 | 178.7665 | 179.7127 | 180.3355 | 182.0422 | [10 empty] | Huon River | Load transfer capacity (MVA)4
11006 | 116.8274 | 122.8658 | 124.8026 | 128.0387 | 131.8296 | 136.1132 | 139.7432 | 143.9361 | 145.8332 | 147.6966 | 149.0805 | 150.2568 |  |  | 11006 | 163.9427 | 164.9998 | 164.9665 | 167.0669 | 170.0613 | 173.6218 | 176.7243 | 179.0728 | 180.1907 | 181.1444 | 181.7721 | 183.4925 | [10 empty] | Huon River | Load transfer capacity (MVA)5
11021 | 89.3615 | 93.9804 | 95.4618 | 97.9371 | 100.8367 | 104.1133 | 106.8899 | 110.097 | 111.5482 | 112.9735 | 114.032 | 114.9318 |  |  | 11021 | 157.8115 | 158.8291 | 158.797 | 160.8188 | 163.7013 | 167.1286 | 170.1151 | 172.3758 | 173.4519 | 174.3699 | 174.9742 | 176.6302 | [10 empty] | Kermandie | Load transfer capacity (MVA)1 | Knights Road | 4.4
11023 | 92.9283 | 97.7315 | 99.2721 | 101.8462 | 104.8615 | 108.2689 | 111.1563 | 114.4915 | 116.0005 | 117.4827 | 118.5835 | 119.5192 |  |  | 11023 | 191.995 | 193.233 | 193.1939 | 195.6537 | 199.1606 | 203.3302 | 206.9637 | 209.7141 | 211.0232 | 212.1401 | 212.8752 | 214.89 | [10 empty] | Kermandie | Load transfer capacity (MVA)2
11025 | 90.546 | 95.226 | 96.7272 | 99.2353 | 102.1733 | 105.4933 | 108.3067 | 111.5563 | 113.0267 | 114.4709 | 115.5435 | 116.4552 |  |  | 11025 | 164.2687 | 165.3279 | 165.2945 | 167.3991 | 170.3995 | 173.967 | 177.0757 | 179.4289 | 180.549 | 181.5046 | 182.1336 | 183.8574 | [10 empty] | Kermandie | Load transfer capacity (MVA)3
11027 | 88.6419 | 93.2235 | 94.6931 | 97.1484 | 100.0247 | 103.2749 | 106.0291 | 109.2104 | 110.6499 | 112.0637 | 113.1137 | 114.0063 |  |  | 11027 | 173.1471 | 174.2636 | 174.2283 | 176.4467 | 179.6092 | 183.3696 | 186.6463 | 189.1267 | 190.3073 | 191.3145 | 191.9776 | 193.7945 | [10 empty] | Kermandie | Load transfer capacity (MVA)4
12017 | 64.4336 | 67.764 | 68.8322 | 70.617 | 72.7078 | 75.0703 | 77.0724 | 79.3849 | 80.4312 | 81.4589 | 82.2222 | 82.871 |  |  | 12017 | 145.5777 | 146.5165 | 146.4868 | 148.3519 | 151.011 | 154.1726 | 156.9276 | 159.013 | 160.0057 | 160.8525 | 161.4099 | 162.9376 | [10 empty] | Kermandie | Load transfer capacity (MVA)5
12018 | 52.1292 | 54.8236 | 55.6878 | 57.1317 | 58.8232 | 60.7346 | 62.3543 | 64.2252 | 65.0718 | 65.9032 | 66.5207 | 67.0456 |  |  | 12018 | 137.2119 | 138.0967 | 138.0688 | 139.8267 | 142.3329 | 145.3128 | 147.9095 | 149.8751 | 150.8107 | 151.6089 | 152.1343 | 153.5741 | [10 empty] | Kingston kV | Load transfer capacity (MVA)1 | Electrona | 7.8
12019 | 80.4429 | 84.6008 | 85.9344 | 88.1626 | 90.7729 | 93.7224 | 96.2219 | 99.1089 | 100.4153 | 101.6983 | 102.6512 | 103.4612 |  |  | 12019 | 188.0644 | 189.2771 | 189.2388 | 191.6483 | 195.0833 | 199.1676 | 202.7267 | 205.4208 | 206.7031 | 207.7971 | 208.5172 | 210.4907 | [10 empty] | Kingston kV | Load transfer capacity (MVA)2 | Kermandie | 3.1
12030 | 53.968 | 56.7575 | 57.6522 | 59.1471 | 60.8982 | 62.8771 | 64.5539 | 66.4908 | 67.3672 | 68.2279 | 68.8673 | 69.4107 |  |  | 12030 | 168.3557 | 169.4413 | 169.407 | 171.5639 | 174.639 | 178.2953 | 181.4813 | 183.8931 | 185.041 | 186.0204 | 186.665 | 188.4317 | [10 empty] | Kingston kV | Load transfer capacity (MVA)3 | Kingston | 1.6
12031 | 83.7367 | 88.0648 | 89.453 | 91.7725 | 94.4896 | 97.5599 | 100.1617 | 103.167 | 104.5268 | 105.8624 | 106.8543 | 107.6975 |  |  | 12031 | 201.2524 | 202.5501 | 202.5091 | 205.0875 | 208.7635 | 213.1342 | 216.9428 | 219.8258 | 221.1981 | 222.3688 | 223.1394 | 225.2513 | [10 empty] | Kingston kV | Load transfer capacity (MVA)4
12032 | 48.8274 | 51.3511 | 52.1606 | 53.5131 | 55.0975 | 56.8878 | 58.4049 | 60.1573 | 60.9502 | 61.729 | 62.3074 | 62.7991 |  |  | 12032 | 107.9795 | 108.6758 | 108.6538 | 110.0372 | 112.0095 | 114.3546 | 116.398 | 117.9449 | 118.6811 | 119.3093 | 119.7227 | 120.8558 | [10 empty] | Kingston kV | Load transfer capacity (MVA)5
12033 | 21.0376 | 22.1249 | 22.4737 | 23.0565 | 23.7391 | 24.5105 | 25.1641 | 25.9192 | 26.2608 | 26.5963 | 26.8455 | 27.0574 |  |  | 12033 | 57.5051 | 57.8759 | 57.8642 | 58.601 | 59.6513 | 60.9002 | 61.9885 | 62.8122 | 63.2044 | 63.5389 | 63.7591 | 64.3625 | [10 empty] | Kingston kV | Load transfer capacity (MVA)1
12034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 12034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Kingston kV | Load transfer capacity (MVA)2
12035 | 58.7712 | 61.8089 | 62.7832 | 64.4112 | 66.3182 | 68.4731 | 70.2992 | 72.4085 | 73.3629 | 74.3003 | 74.9965 | 75.5882 |  |  | 12035 | 157.2855 | 158.2997 | 158.2677 | 160.2828 | 163.1557 | 166.5715 | 169.5481 | 171.8012 | 172.8737 | 173.7887 | 174.3909 | 176.0414 | [10 empty] | Kingston kV | Load transfer capacity (MVA)3
12036 | 108.5881 | 114.2007 | 116.0009 | 119.0088 | 122.5323 | 126.5138 | 129.8878 | 133.785 | 135.5483 | 137.2803 | 138.5666 | 139.66 |  |  | 12036 | 195.062 | 196.3199 | 196.2802 | 198.7792 | 202.3421 | 206.5784 | 210.2699 | 213.0642 | 214.3942 | 215.5289 | 216.2759 | 218.3228 | [10 empty] | Kingston kV | Load transfer capacity (MVA)4
12037 | 92.3744 | 97.149 | 98.6804 | 101.2391 | 104.2365 | 107.6236 | 110.4938 | 113.809 | 115.3091 | 116.7825 | 117.8767 | 118.8068 |  |  | 12037 | 166.2192 | 167.291 | 167.2572 | 169.3868 | 172.4228 | 176.0327 | 179.1783 | 181.5595 | 182.6929 | 183.6598 | 184.2963 | 186.0405 | [10 empty] | Kingston kV | Load transfer capacity (MVA)5
12038 | 70.7616 | 74.419 | 75.5921 | 77.5522 | 79.8483 | 82.4429 | 84.6415 | 87.1811 | 88.3302 | 89.4588 | 90.2971 | 91.0096 |  |  | 12038 | 147.6519 | 148.604 | 148.5739 | 150.4656 | 153.1625 | 156.3691 | 159.1634 | 161.2785 | 162.2853 | 163.1442 | 163.7096 | 165.259 | [10 empty] | Knights Road | Load transfer capacity (MVA)1 | Electrona | 1.7
12039 | 88.3902 | 92.9588 | 94.4241 | 96.8725 | 99.7406 | 102.9816 | 105.728 | 108.9003 | 110.3356 | 111.7454 | 112.7925 | 113.6825 |  |  | 12039 | 172.7451 | 173.859 | 173.8239 | 176.037 | 179.1923 | 182.9439 | 186.213 | 188.6876 | 189.8655 | 190.8704 | 191.5319 | 193.3446 | [10 empty] | Knights Road | Load transfer capacity (MVA)2 | Kermandie | 3.4
13043 | 28.0795 | 29.5309 | 29.9964 | 30.7742 | 31.6853 | 32.7149 | 33.5874 | 34.5951 | 35.0511 | 35.499 | 35.8316 | 36.1143 |  |  | 13043 | 72.9473 | 73.4177 | 73.4029 | 74.3374 | 75.6699 | 77.2541 | 78.6346 | 79.6796 | 80.177 | 80.6013 | 80.8807 | 81.6461 | [10 empty] | Knights Road | Load transfer capacity (MVA)3 | Kingston | 1.7
13044 | 91.5674 | 96.3002 | 97.8183 | 100.3547 | 103.3259 | 106.6833 | 109.5284 | 112.8148 | 114.3017 | 115.7622 | 116.8469 | 117.7689 |  |  | 13044 | 94.3343 | 94.9425 | 94.9233 | 96.1319 | 97.855 | 99.9037 | 101.6889 | 103.0403 | 103.6835 | 104.2323 | 104.5935 | 105.5834 | [10 empty] | Knights Road | Load transfer capacity (MVA)4
13045 | 96.8905 | 101.8985 | 103.5048 | 106.1886 | 109.3326 | 112.8852 | 115.8957 | 119.3731 | 120.9465 | 122.4918 | 123.6396 | 124.6152 |  |  | 13045 | 229.0613 | 230.5384 | 230.4918 | 233.4264 | 237.6103 | 242.585 | 246.9199 | 250.2012 | 251.7631 | 253.0956 | 253.9727 | 256.3764 | [10 empty] | Knights Road | Load transfer capacity (MVA)5
13046 | 43.1839 | 45.416 | 46.1319 | 47.3281 | 48.7293 | 50.3127 | 51.6545 | 53.2043 | 53.9056 | 54.5944 | 55.1059 | 55.5407 |  |  | 13046 | 63.5932 | 64.0033 | 63.9903 | 64.8051 | 65.9666 | 67.3477 | 68.5512 | 69.4622 | 69.8958 | 70.2657 | 70.5093 | 71.1766 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)1
13047 | 46.4396 | 48.8399 | 49.6098 | 50.8962 | 52.403 | 54.1058 | 55.5488 | 57.2155 | 57.9696 | 58.7103 | 59.2604 | 59.728 |  |  | 13047 | 50.3429 | 50.6675 | 50.6573 | 51.3023 | 52.2218 | 53.3151 | 54.2679 | 54.989 | 55.3323 | 55.6252 | 55.8179 | 56.3462 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)2
13048 | 60.7693 | 63.9102 | 64.9177 | 66.601 | 68.5729 | 70.8011 | 72.6892 | 74.8702 | 75.857 | 76.8263 | 77.5462 | 78.158 |  |  | 13048 | 117.6061 | 118.3644 | 118.3405 | 119.8472 | 121.9953 | 124.5495 | 126.7751 | 128.4599 | 129.2618 | 129.9459 | 130.3962 | 131.6303 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)3
13049 | 59.486 | 62.5607 | 63.5469 | 65.1946 | 67.1248 | 69.306 | 71.1543 | 73.2892 | 74.2552 | 75.204 | 75.9086 | 76.5076 |  |  | 13049 | 147.3615 | 148.3117 | 148.2817 | 150.1697 | 152.8613 | 156.0616 | 158.8504 | 160.9614 | 161.9662 | 162.8234 | 163.3877 | 164.934 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)4
13050 | 34.2201 | 35.9889 | 36.5562 | 37.5041 | 38.6145 | 39.8692 | 40.9325 | 42.1606 | 42.7163 | 43.2621 | 43.6675 | 44.012 |  |  | 13050 | 70.3568 | 70.8105 | 70.7962 | 71.6976 | 72.9827 | 74.5107 | 75.8421 | 76.85 | 77.3298 | 77.739 | 78.0084 | 78.7467 | [10 empty] | Lindisfarne | Load transfer capacity (MVA)5
13052 | 134.1762 | 141.1114 | 143.3358 | 147.0525 | 151.4062 | 156.326 | 160.495 | 165.3106 | 167.4895 | 169.6295 | 171.219 | 172.57 |  |  | 13052 | 197.2235 | 198.4953 | 198.4551 | 200.9819 | 204.5843 | 208.8675 | 212.5998 | 215.4251 | 216.7699 | 217.9172 | 218.6724 | 220.742 | [10 empty] | Meadowbank | Load transfer capacity (MVA)1 | New Norfolk | 3.4
13053 | 61.3301 | 64.5001 | 65.5168 | 67.2156 | 69.2057 | 71.4545 | 73.3601 | 75.5612 | 76.5571 | 77.5353 | 78.2618 | 78.8794 |  |  | 13053 | 134.613 | 135.481 | 135.4536 | 137.1782 | 139.637 | 142.5605 | 145.108 | 147.0363 | 147.9542 | 148.7373 | 149.2527 | 150.6653 | [10 empty] | Meadowbank | Load transfer capacity (MVA)2 | Wayatinah Zone | 0.5
13054 | 47.3759 | 49.8246 | 50.61 | 51.9223 | 53.4596 | 55.1967 | 56.6687 | 58.369 | 59.1384 | 59.894 | 60.4552 | 60.9322 |  |  | 13054 | 76.3237 | 76.8158 | 76.8003 | 77.7782 | 79.1722 | 80.8298 | 82.2742 | 83.3675 | 83.888 | 84.332 | 84.6242 | 85.4251 | [10 empty] | Meadowbank | Load transfer capacity (MVA)3
13055 | 81.0741 | 85.2645 | 86.6086 | 88.8544 | 91.4851 | 94.4578 | 96.9768 | 99.8866 | 101.2031 | 102.4962 | 103.4566 | 104.273 |  |  | 13055 | 179.5229 | 180.6805 | 180.6439 | 182.9439 | 186.223 | 190.1218 | 193.5192 | 196.0909 | 197.315 | 198.3593 | 199.0467 | 200.9306 | [10 empty] | Meadowbank | Load transfer capacity (MVA)4
13056 | 33.0082 | 34.7143 | 35.2615 | 36.1758 | 37.2469 | 38.4572 | 39.4828 | 40.6674 | 41.2034 | 41.7299 | 42.1209 | 42.4533 |  |  | 13056 | 84.3856 | 84.9298 | 84.9126 | 85.9937 | 87.5351 | 89.3677 | 90.9647 | 92.1735 | 92.7489 | 93.2398 | 93.5629 | 94.4484 | [10 empty] | Meadowbank | Load transfer capacity (MVA)5
13057 | 92.4799 | 97.2599 | 98.7931 | 101.3548 | 104.3556 | 107.7465 | 110.62 | 113.939 | 115.4408 | 116.9158 | 118.0114 | 118.9425 |  |  | 13057 | 187.2575 | 188.465 | 188.4268 | 190.8259 | 194.2463 | 198.313 | 201.8568 | 204.5393 | 205.8162 | 206.9055 | 207.6225 | 209.5875 | [10 empty] | Mornington | Load transfer capacity (MVA)1
13058 | 45.2942 | 47.6353 | 48.3862 | 49.6408 | 51.1105 | 52.7713 | 54.1787 | 55.8042 | 56.5398 | 57.2622 | 57.7988 | 58.2548 |  |  | 13058 | 30.5806 | 30.7778 | 30.7716 | 31.1634 | 31.7219 | 32.3861 | 32.9648 | 33.4029 | 33.6114 | 33.7893 | 33.9064 | 34.2273 | [10 empty] | Mornington | Load transfer capacity (MVA)2
14060 | 66.33 | 69.7584 | 70.8581 | 72.6954 | 74.8477 | 77.2798 | 79.3407 | 81.7213 | 82.7984 | 83.8564 | 84.6421 | 85.31 |  |  | 14060 | 95.9165 | 96.535 | 96.5155 | 97.7443 | 99.4963 | 101.5794 | 103.3945 | 104.7686 | 105.4226 | 105.9805 | 106.3478 | 107.3543 | [10 empty] | Mornington | Load transfer capacity (MVA)3
14061 | 48.393 | 50.8943 | 51.6966 | 53.037 | 54.6073 | 56.3817 | 57.8853 | 59.6221 | 60.408 | 61.1798 | 61.7531 | 62.2404 |  |  | 14061 | 65.9379 | 66.3631 | 66.3496 | 67.1944 | 68.3988 | 69.8308 | 71.0787 | 72.0232 | 72.4728 | 72.8564 | 73.1089 | 73.8008 | [10 empty] | Mornington | Load transfer capacity (MVA)4
14062 | 23.9969 | 25.2372 | 25.635 | 26.2997 | 27.0784 | 27.9583 | 28.7039 | 29.5651 | 29.9548 | 30.3376 | 30.6218 | 30.8634 |  |  | 14062 | 30.3201 | 30.5156 | 30.5094 | 30.8979 | 31.4517 | 32.1102 | 32.684 | 33.1183 | 33.325 | 33.5014 | 33.6175 | 33.9357 | [10 empty] | Mornington | Load transfer capacity (MVA)5
14063 | 68.5116 | 72.0527 | 73.1885 | 75.0863 | 77.3094 | 79.8215 | 81.9502 | 84.409 | 85.5216 | 86.6143 | 87.4259 | 88.1158 |  |  | 14063 | 130.9837 | 131.8283 | 131.8017 | 133.4798 | 135.8722 | 138.7169 | 141.1957 | 143.0721 | 143.9652 | 144.7272 | 145.2287 | 146.6032 | [10 empty] | Mowbray | Load transfer capacity (MVA)1 | Trevallyn | 31.4
14064 | 73.1056 | 76.8842 | 78.0962 | 80.1212 | 82.4934 | 85.1739 | 87.4454 | 90.0691 | 91.2563 | 92.4223 | 93.2883 | 94.0244 |  |  | 14064 | 95.2264 | 95.8404 | 95.821 | 97.041 | 98.7804 | 100.8485 | 102.6506 | 104.0147 | 104.664 | 105.218 | 105.5826 | 106.5819 | [10 empty] | Mowbray | Load transfer capacity (MVA)2 | Norwood | 6.3
14065 | 148.216 | 155.8768 | 158.334 | 162.4395 | 167.2489 | 172.6835 | 177.2887 | 182.6081 | 185.015 | 187.379 | 189.1348 | 190.6271 |  |  | 14065 | 195.8161 | 197.0787 | 197.0389 | 199.5476 | 203.1243 | 207.3769 | 211.0827 | 213.8878 | 215.223 | 216.3621 | 217.1119 | 219.1667 | [10 empty] | Mowbray | Load transfer capacity (MVA)3
14066 | 72.6323 | 76.3864 | 77.5905 | 79.6024 | 81.9592 | 84.6224 | 86.8791 | 89.4859 | 90.6654 | 91.8238 | 92.6842 | 93.4156 |  |  | 14066 | 122.7172 | 123.5086 | 123.4836 | 125.0558 | 127.2973 | 129.9624 | 132.2848 | 134.0427 | 134.8795 | 135.5933 | 136.0633 | 137.351 | [10 empty] | Mowbray | Load transfer capacity (MVA)4
14067 | 34.8903 | 36.6937 | 37.2721 | 38.2385 | 39.3707 | 40.65 | 41.7341 | 42.9862 | 43.5528 | 44.1093 | 44.5226 | 44.8739 |  |  | 14067 | 72.6355 | 73.1039 | 73.0891 | 74.0197 | 75.3464 | 76.9239 | 78.2985 | 79.339 | 79.8343 | 80.2568 | 80.5349 | 81.2971 | [10 empty] | Mowbray | Load transfer capacity (MVA)5
14068 | 96.5056 | 101.4936 | 103.0935 | 105.7667 | 108.8981 | 112.4367 | 115.4352 | 118.8988 | 120.4659 | 122.0051 | 123.1484 | 124.1201 |  |  | 14068 | 163.6139 | 164.6689 | 164.6356 | 166.7318 | 169.7202 | 173.2735 | 176.3699 | 178.7137 | 179.8293 | 180.7811 | 181.4076 | 183.1245 | [10 empty] | New Norfolk | Load transfer capacity (MVA)1 | Meadowbank | 6.6
14069 | 128.7771 | 135.4331 | 137.5681 | 141.1351 | 145.3137 | 150.0356 | 154.0368 | 158.6586 | 160.7498 | 162.8037 | 164.3292 | 165.6259 |  |  | 14069 | 144.7347 | 145.668 | 145.6385 | 147.4928 | 150.1365 | 153.2798 | 156.0188 | 158.0922 | 159.0791 | 159.921 | 160.4752 | 161.994 | [10 empty] | New Norfolk | Load transfer capacity (MVA)2
14070 | 120.8874 | 127.1357 | 129.1398 | 132.4884 | 136.411 | 140.8435 | 144.5996 | 148.9382 | 150.9013 | 152.8294 | 154.2614 | 155.4786 |  |  | 14070 | 178.0353 | 179.1833 | 179.1471 | 181.4281 | 184.6799 | 188.5464 | 191.9157 | 194.4661 | 195.68 | 196.7157 | 197.3974 | 199.2657 | [10 empty] | New Norfolk | Load transfer capacity (MVA)3
14071 | 136.9709 | 144.0505 | 146.3212 | 150.1153 | 154.5598 | 159.582 | 163.8378 | 168.7537 | 170.978 | 173.1626 | 174.7852 | 176.1643 |  |  | 14071 | 174.0813 | 175.2038 | 175.1684 | 177.3987 | 180.5783 | 184.3589 | 187.6534 | 190.1471 | 191.3341 | 192.3468 | 193.0134 | 194.8401 | [10 empty] | New Norfolk | Load transfer capacity (MVA)4
14072 | 10.0189 | 10.5367 | 10.7028 | 10.9804 | 11.3055 | 11.6728 | 11.9841 | 12.3437 | 12.5064 | 12.6662 | 12.7849 | 12.8857 |  |  | 14072 | 16.7426 | 16.8506 | 16.8472 | 17.0617 | 17.3675 | 17.7311 | 18.048 | 18.2878 | 18.402 | 18.4994 | 18.5635 | 18.7392 | [10 empty] | New Norfolk | Load transfer capacity (MVA)5
16091 | 84.0009 | 88.3427 | 89.7353 | 92.0621 | 94.7878 | 97.8678 | 100.4778 | 103.4926 | 104.8567 | 106.1965 | 107.1915 | 108.0373 |  |  | 16091 | 188.7947 | 190.012 | 189.9736 | 192.3924 | 195.8408 | 199.941 | 203.5138 | 206.2184 | 207.5057 | 208.6039 | 209.3269 | 211.308 | [10 empty] | Newton | Load transfer capacity (MVA)1
16092 | 64.8662 | 68.2189 | 69.2943 | 71.0911 | 73.1959 | 75.5743 | 77.5897 | 79.9178 | 80.9711 | 82.0057 | 82.7741 | 83.4273 |  |  | 16092 | 120.7435 | 121.522 | 121.4975 | 123.0444 | 125.2498 | 127.8721 | 130.1571 | 131.8868 | 132.7101 | 133.4125 | 133.8748 | 135.1419 | [10 empty] | Newton | Load transfer capacity (MVA)2
16093 | 81.8669 | 86.0984 | 87.4556 | 89.7233 | 92.3797 | 95.3815 | 97.9252 | 100.8634 | 102.1928 | 103.4986 | 104.4684 | 105.2927 |  |  | 16093 | 125.2901 | 126.098 | 126.0725 | 127.6777 | 129.9662 | 132.6872 | 135.0583 | 136.8531 | 137.7074 | 138.4362 | 138.916 | 140.2307 | [10 empty] | Newton | Load transfer capacity (MVA)3
16094 | 51.4918 | 54.1533 | 55.0069 | 56.4332 | 58.104 | 59.9921 | 61.592 | 63.44 | 64.2762 | 65.0975 | 65.7074 | 66.2259 |  |  | 16094 | 113.4375 | 114.169 | 114.1459 | 115.5992 | 117.6712 | 120.1348 | 122.2815 | 123.9066 | 124.68 | 125.3399 | 125.7743 | 126.9647 | [10 empty] | Newton | Load transfer capacity (MVA)4
16095 | 118.8057 | 124.9464 | 126.916 | 130.2069 | 134.0619 | 138.4181 | 142.1095 | 146.3734 | 148.3027 | 150.1976 | 151.605 | 152.8012 |  |  | 16095 | 164.9405 | 166.0041 | 165.9705 | 168.0837 | 171.0964 | 174.6785 | 177.7999 | 180.1628 | 181.2874 | 182.2469 | 182.8785 | 184.6093 | [10 empty] | Newton | Load transfer capacity (MVA)5
16096 | 85.1987 | 89.6023 | 91.0148 | 93.3747 | 96.1393 | 99.2632 | 101.9104 | 104.9682 | 106.3517 | 107.7106 | 108.7199 | 109.5778 |  |  | 16096 | 205.969 | 207.2972 | 207.2553 | 209.8941 | 213.6562 | 218.1293 | 222.0272 | 224.9778 | 226.3822 | 227.5803 | 228.369 | 230.5304 | [10 empty] | North Hobart | Load transfer capacity (MVA)1
16097 | 39.9187 | 41.982 | 42.6438 | 43.7496 | 45.0448 | 46.5085 | 47.7488 | 49.1815 | 49.8298 | 50.4664 | 50.9393 | 51.3413 |  |  | 16097 | 52.1529 | 52.4892 | 52.4786 | 53.1468 | 54.0994 | 55.232 | 56.219 | 56.9661 | 57.3217 | 57.6251 | 57.8248 | 58.3721 | [10 empty] | North Hobart | Load transfer capacity (MVA)2
16098 | 78.7634 | 82.8344 | 84.1402 | 86.3219 | 88.8776 | 91.7656 | 94.2129 | 97.0397 | 98.3187 | 99.5749 | 100.508 | 101.301 |  |  | 16098 | 200.8805 | 202.1759 | 202.135 | 204.7086 | 208.3778 | 212.7404 | 216.542 | 219.4197 | 220.7894 | 221.9579 | 222.7271 | 224.8351 | [10 empty] | North Hobart | Load transfer capacity (MVA)3
17100 | 72.5229 | 76.2714 | 77.4737 | 79.4826 | 81.8358 | 84.495 | 86.7484 | 89.3512 | 90.5289 | 91.6856 | 92.5447 | 93.275 |  |  | 17100 | 120.8939 | 121.6734 | 121.6488 | 123.1977 | 125.4058 | 128.0313 | 130.3192 | 132.0511 | 132.8754 | 133.5786 | 134.0416 | 135.3102 | [10 empty] | North Hobart | Load transfer capacity (MVA)4
17101 | 57.1429 | 60.0964 | 61.0438 | 62.6266 | 64.4808 | 66.576 | 68.3515 | 70.4024 | 71.3303 | 72.2417 | 72.9186 | 73.494 |  |  | 17101 | 121.1395 | 121.9206 | 121.896 | 123.448 | 125.6606 | 128.2915 | 130.584 | 132.3194 | 133.1454 | 133.8501 | 134.3139 | 135.5851 | [10 empty] | North Hobart | Load transfer capacity (MVA)5
17102 | 8.5218 | 8.9622 | 9.1035 | 9.3396 | 9.6161 | 9.9285 | 10.1933 | 10.4992 | 10.6375 | 10.7735 | 10.8744 | 10.9602 |  |  | 17102 | 11.8575 | 11.934 | 11.9316 | 12.0835 | 12.3001 | 12.5576 | 12.782 | 12.9519 | 13.0327 | 13.1017 | 13.1471 | 13.2715 | [10 empty] | Norwood | Load transfer capacity (MVA)1 | Trevallyn | 16.2
17103 | 80.4696 | 84.6288 | 85.9629 | 88.1919 | 90.803 | 93.7535 | 96.2538 | 99.1418 | 100.4486 | 101.732 | 102.6853 | 103.4955 |  |  | 17103 | 153.0634 | 154.0503 | 154.0192 | 155.9802 | 158.776 | 162.1001 | 164.9968 | 167.1895 | 168.2331 | 169.1235 | 169.7096 | 171.3158 | [10 empty] | Norwood | Load transfer capacity (MVA)2 | Mowbray | 10.8
17104 | 67.5468 | 71.038 | 72.1579 | 74.0289 | 76.2207 | 78.6974 | 80.7961 | 83.2203 | 84.3173 | 85.3946 | 86.1948 | 86.8749 |  |  | 17104 | 105.8985 | 106.5814 | 106.5598 | 107.9166 | 109.8508 | 112.1507 | 114.1548 | 115.6718 | 116.3939 | 117.0099 | 117.4154 | 118.5267 | [10 empty] | Norwood | Load transfer capacity (MVA)3 | St Leonards | 27
17105 | 112.5272 | 118.3434 | 120.209 | 123.3259 | 126.9772 | 131.1032 | 134.5996 | 138.6381 | 140.4655 | 142.2602 | 143.5932 | 144.7263 |  |  | 17105 | 212.3821 | 213.7515 | 213.7083 | 216.4293 | 220.3085 | 224.921 | 228.9402 | 231.9826 | 233.4308 | 234.6662 | 235.4795 | 237.7081 | [10 empty] | Norwood | Load transfer capacity (MVA)4 | Hadspen | 16.2
17106 | 120.6315 | 126.8665 | 128.8664 | 132.2079 | 136.1221 | 140.5453 | 144.2934 | 148.6229 | 150.5818 | 152.5058 | 153.9348 | 155.1495 |  |  | 17106 | 175.8207 | 176.9544 | 176.9187 | 179.1712 | 182.3827 | 186.201 | 189.5284 | 192.0471 | 193.2459 | 194.2687 | 194.9419 | 196.7869 | [10 empty] | Norwood | Load transfer capacity (MVA)5
17107 | 72.5039 | 76.2514 | 77.4534 | 79.4618 | 81.8144 | 84.4729 | 86.7256 | 89.3278 | 90.5052 | 91.6616 | 92.5205 | 93.2505 |  |  | 17107 | 108.6762 | 109.377 | 109.3549 | 110.7472 | 112.7322 | 115.0924 | 117.149 | 118.7058 | 119.4469 | 120.0791 | 120.4952 | 121.6356 | [10 empty] | Palmerston | Load transfer capacity (MVA)1 | Norwood | 2
17108 | 26.9151 | 28.3063 | 28.7525 | 29.498 | 30.3713 | 31.3582 | 32.1945 | 33.1605 | 33.5976 | 34.0268 | 34.3457 | 34.6167 |  |  | 17108 | 28.935 | 29.1216 | 29.1157 | 29.4864 | 30.0149 | 30.6433 | 31.1909 | 31.6054 | 31.8027 | 31.971 | 32.0818 | 32.3854 | [10 empty] | Palmerston | Load transfer capacity (MVA)2 | Hadspen | 5
17109 | 40.722 | 42.8268 | 43.5019 | 44.6299 | 45.9512 | 47.4444 | 48.7096 | 50.1711 | 50.8324 | 51.4819 | 51.9643 | 52.3743 |  |  | 17109 | 61.7223 | 62.1203 | 62.1077 | 62.8985 | 64.0258 | 65.3663 | 66.5344 | 67.4186 | 67.8394 | 68.1985 | 68.4348 | 69.0825 | [10 empty] | Palmerston | Load transfer capacity (MVA)3
20534 | 27.6333 | 29.0616 | 29.5197 | 30.2851 | 31.1818 | 32.195 | 33.0536 | 34.0453 | 34.4941 | 34.9348 | 35.2622 | 35.5404 |  |  | 20534 | 56.3236 | 56.6868 | 56.6753 | 57.3969 | 58.4257 | 59.6489 | 60.7148 | 61.5216 | 61.9057 | 62.2333 | 62.449 | 63.04 | [10 empty] | Palmerston | Load transfer capacity (MVA)4
20535 | 60.0821 | 63.1876 | 64.1836 | 65.8479 | 67.7975 | 70.0005 | 71.8673 | 74.0236 | 74.9993 | 75.9576 | 76.6693 | 77.2743 |  |  | 20535 | 146.8833 | 147.8304 | 147.8005 | 149.6823 | 152.3652 | 155.5551 | 158.3349 | 160.439 | 161.4405 | 162.295 | 162.8574 | 164.3988 | [10 empty] | Palmerston | Load transfer capacity (MVA)5
20536 | 58.2182 | 61.2273 | 62.1924 | 63.8051 | 65.6941 | 67.8288 | 69.6377 | 71.7271 | 72.6725 | 73.6011 | 74.2908 | 74.877 |  |  | 20536 | 139.0365 | 139.933 | 139.9047 | 141.686 | 144.2256 | 147.2451 | 149.8763 | 151.868 | 152.8161 | 153.6249 | 154.1573 | 155.6163 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)1 | Burnie | 3.9
20537 | 51.8234 | 54.502 | 55.3612 | 56.7967 | 58.4783 | 60.3784 | 61.9887 | 63.8486 | 64.6901 | 65.5167 | 66.1306 | 66.6524 |  |  | 20537 | 119.4662 | 120.2365 | 120.2122 | 121.7428 | 123.9249 | 126.5194 | 128.7802 | 130.4916 | 131.3062 | 132.0011 | 132.4586 | 133.7122 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)2 | Smithton | 3.9
20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)3
20539 | 18.6813 | 19.6469 | 19.9566 | 20.4741 | 21.0803 | 21.7653 | 22.3457 | 23.0162 | 23.3195 | 23.6175 | 23.8388 | 24.0269 |  |  | 20539 | 35.1369 | 35.3635 | 35.3564 | 35.8065 | 36.4483 | 37.2114 | 37.8763 | 38.3797 | 38.6193 | 38.8237 | 38.9582 | 39.3269 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)4
20540 | 98.6111 | 103.708 | 105.3428 | 108.0743 | 111.274 | 114.8898 | 117.9537 | 121.4928 | 123.0942 | 124.667 | 125.8351 | 126.828 |  |  | 20540 | 116.7277 | 117.4804 | 117.4567 | 118.9522 | 121.0842 | 123.6193 | 125.8283 | 127.5005 | 128.2964 | 128.9754 | 129.4224 | 130.6473 | [10 empty] | Port Latta (RT) | Load transfer capacity (MVA)5
20541 | 108.1917 | 113.7838 | 115.5775 | 118.5744 | 122.085 | 126.052 | 129.4136 | 133.2966 | 135.0536 | 136.7792 | 138.0608 | 139.1502 |  |  | 20541 | 214.8713 | 216.2568 | 216.2131 | 218.966 | 222.8906 | 227.5571 | 231.6235 | 234.7016 | 236.1667 | 237.4166 | 238.2394 | 240.4942 | [10 empty] | Queenstown | Load transfer capacity (MVA)1
20544 | 69.562 | 73.1574 | 74.3106 | 76.2375 | 78.4946 | 81.0452 | 83.2066 | 85.7031 | 86.8328 | 87.9422 | 88.7663 | 89.4667 |  |  | 20544 | 142.8665 | 143.7878 | 143.7587 | 145.5891 | 148.1986 | 151.3013 | 154.005 | 156.0516 | 157.0257 | 157.8568 | 158.4039 | 159.903 | [10 empty] | Queenstown | Load transfer capacity (MVA)2
20545 | 25.9954 | 27.3391 | 27.77 | 28.4901 | 29.3336 | 30.2868 | 31.0945 | 32.0274 | 32.4496 | 32.8642 | 33.1721 | 33.4339 |  |  | 20545 | 52.7131 | 53.053 | 53.0423 | 53.7176 | 54.6805 | 55.8253 | 56.8228 | 57.578 | 57.9374 | 58.244 | 58.4459 | 58.999 | [10 empty] | Queenstown | Load transfer capacity (MVA)3
20547 | 119.4716 | 125.6467 | 127.6273 | 130.9366 | 134.8133 | 139.1939 | 142.906 | 147.1938 | 149.1339 | 151.0394 | 152.4547 | 153.6576 |  |  | 20547 | 276.527 | 278.3102 | 278.2539 | 281.7967 | 286.8475 | 292.853 | 298.0862 | 302.0475 | 303.9331 | 305.5416 | 306.6005 | 309.5023 | [10 empty] | Queenstown | Load transfer capacity (MVA)4
20548 | 83.2248 | 87.5265 | 88.9062 | 91.2115 | 93.912 | 96.9636 | 99.5494 | 102.5363 | 103.8878 | 105.2152 | 106.2011 | 107.0391 |  |  | 20548 | 216.5132 | 217.9094 | 217.8653 | 220.6392 | 224.5939 | 229.296 | 233.3935 | 236.4951 | 237.9714 | 239.2309 | 240.0599 | 242.3319 | [10 empty] | Queenstown | Load transfer capacity (MVA)5
20549 | 69.8381 | 73.4478 | 74.6056 | 76.5401 | 78.8062 | 81.367 | 83.5369 | 86.0434 | 87.1775 | 88.2914 | 89.1187 | 89.8219 |  |  | 20549 | 149.2132 | 150.1754 | 150.145 | 152.0567 | 154.7821 | 158.0227 | 160.8465 | 162.984 | 164.0014 | 164.8694 | 165.4408 | 167.0066 | [10 empty] | Railton | Load transfer capacity (MVA)1 | Devonport | 8.7
20551 | 44.0356 | 46.3117 | 47.0417 | 48.2615 | 49.6904 | 51.305 | 52.6732 | 54.2537 | 54.9688 | 55.6711 | 56.1928 | 56.6362 |  |  | 20551 | 45.7398 | 46.0347 | 46.0254 | 46.6114 | 47.4469 | 48.4402 | 49.3058 | 49.9611 | 50.273 | 50.539 | 50.7142 | 51.1941 | [10 empty] | Railton | Load transfer capacity (MVA)2 | Ulverstone | 4.4
20552 | 66.8096 | 70.2628 | 71.3704 | 73.221 | 75.3888 | 77.8385 | 79.9144 | 82.3121 | 83.3971 | 84.4627 | 85.2541 | 85.9268 |  |  | 20552 | 153.8062 | 154.798 | 154.7667 | 156.7372 | 159.5465 | 162.8868 | 165.7975 | 168.0009 | 169.0496 | 169.9443 | 170.5333 | 172.1473 | [10 empty] | Railton | Load transfer capacity (MVA)3
20553 | 71.9051 | 75.6216 | 76.8137 | 78.8055 | 81.1386 | 83.7752 | 86.0093 | 88.59 | 89.7576 | 90.9045 | 91.7563 | 92.4803 |  |  | 20553 | 147.797 | 148.7501 | 148.72 | 150.6135 | 153.3131 | 156.5229 | 159.3199 | 161.4371 | 162.4449 | 163.3046 | 163.8706 | 165.4215 | [10 empty] | Railton | Load transfer capacity (MVA)4
20554 | 67.1399 | 70.6102 | 71.7233 | 73.583 | 75.7616 | 78.2234 | 80.3095 | 82.7191 | 83.8094 | 84.8803 | 85.6756 | 86.3516 |  |  | 20554 | 119.0205 | 119.7879 | 119.7637 | 121.2886 | 123.4625 | 126.0473 | 128.2998 | 130.0048 | 130.8163 | 131.5087 | 131.9644 | 133.2134 | [10 empty] | Railton | Load transfer capacity (MVA)5
21081 | 84.7757 | 89.1574 | 90.5629 | 92.9111 | 95.662 | 98.7704 | 101.4045 | 104.447 | 105.8237 | 107.1759 | 108.1801 | 109.0337 |  |  | 21081 | 153.0747 | 154.0618 | 154.0306 | 155.9918 | 158.7877 | 162.1121 | 165.009 | 167.2019 | 168.2456 | 169.1361 | 169.7222 | 171.3285 | [10 empty] | Risdon kV | Load transfer capacity (MVA)1
21082 | 18.8166 | 19.7892 | 20.1011 | 20.6224 | 21.2329 | 21.9229 | 22.5075 | 23.1828 | 23.4884 | 23.7885 | 24.0114 | 24.2009 |  |  | 21082 | 42.3993 | 42.6727 | 42.6641 | 43.2073 | 43.9818 | 44.9026 | 45.705 | 46.3123 | 46.6015 | 46.8481 | 47.0104 | 47.4554 | [10 empty] | Risdon kV | Load transfer capacity (MVA)2
21083 | 134.8321 | 141.8012 | 144.0365 | 147.7713 | 152.1463 | 157.0902 | 161.2796 | 166.1186 | 168.3082 | 170.4587 | 172.0559 | 173.4135 |  |  | 21083 | 165.1078 | 166.1724 | 166.1388 | 168.2542 | 171.2699 | 174.8556 | 177.9802 | 180.3455 | 181.4713 | 182.4317 | 183.064 | 184.7965 | [10 empty] | Risdon kV | Load transfer capacity (MVA)3
21084 | 118.8152 | 124.9564 | 126.9262 | 130.2173 | 134.0726 | 138.4292 | 142.1209 | 146.3851 | 148.3146 | 150.2096 | 151.6171 | 152.8135 |  |  | 21084 | 137.2986 | 138.184 | 138.156 | 139.9151 | 142.4229 | 145.4047 | 148.003 | 149.9698 | 150.906 | 151.7047 | 152.2304 | 153.6712 | [10 empty] | Risdon kV | Load transfer capacity (MVA)4
21085 | 111.5909 | 117.3587 | 119.2087 | 122.2998 | 125.9207 | 130.0124 | 133.4796 | 137.4846 | 139.2967 | 141.0765 | 142.3984 | 143.522 |  |  | 21085 | 237.9602 | 239.4946 | 239.4462 | 242.4949 | 246.8413 | 252.0092 | 256.5125 | 259.9214 | 261.5439 | 262.9282 | 263.8394 | 266.3364 | [10 empty] | Risdon kV | Load transfer capacity (MVA)5
21086 | 51.354 | 54.0083 | 54.8597 | 56.2822 | 57.9485 | 59.8315 | 61.4271 | 63.2702 | 64.1041 | 64.9232 | 65.5315 | 66.0486 |  |  | 21086 | 127.8221 | 128.6464 | 128.6204 | 130.258 | 132.5927 | 135.3687 | 137.7877 | 139.6188 | 140.4903 | 141.2339 | 141.7233 | 143.0647 | [10 empty] | Rokeby | Load transfer capacity (MVA)1 | Howrah Zone | 4.8
21087 | 41.4777 | 43.6215 | 44.3092 | 45.4581 | 46.8039 | 48.3248 | 49.6135 | 51.1022 | 51.7757 | 52.4373 | 52.9286 | 53.3463 |  |  | 21087 | 90.7821 | 91.3675 | 91.349 | 92.5121 | 94.1703 | 96.1419 | 97.8599 | 99.1604 | 99.7794 | 100.3075 | 100.6551 | 101.6077 | [10 empty] | Rokeby | Load transfer capacity (MVA)2 | Cambridge Zone | 4.8
21088 | 26.839 | 28.2263 | 28.6712 | 29.4147 | 30.2855 | 31.2696 | 32.1036 | 33.0668 | 33.5026 | 33.9307 | 34.2486 | 34.5189 |  |  | 21088 | 53.4258 | 53.7703 | 53.7594 | 54.4439 | 55.4197 | 56.58 | 57.5911 | 58.3564 | 58.7207 | 59.0315 | 59.2361 | 59.7967 | [10 empty] | Rokeby | Load transfer capacity (MVA)3
21089 | 73.3642 | 77.1562 | 78.3724 | 80.4046 | 82.7851 | 85.4751 | 87.7546 | 90.3877 | 91.579 | 92.7491 | 93.6182 | 94.3569 |  |  | 21089 | 149.0692 | 150.0305 | 150.0001 | 151.91 | 154.6328 | 157.8702 | 160.6913 | 162.8267 | 163.8432 | 164.7103 | 165.2811 | 166.8454 | [10 empty] | Rokeby | Load transfer capacity (MVA)4
22323 | 46.1197 | 48.5035 | 49.2681 | 50.5456 | 52.0421 | 53.7332 | 55.1662 | 56.8214 | 57.5703 | 58.3059 | 58.8522 | 59.3166 |  |  | 22323 | 97.293 | 97.9204 | 97.9006 | 99.1471 | 100.9242 | 103.0372 | 104.8784 | 106.2721 | 106.9356 | 107.5015 | 107.8741 | 108.895 | [10 empty] | Rokeby | Load transfer capacity (MVA)5
22324 | 70.6057 | 74.2551 | 75.4256 | 77.3813 | 79.6724 | 82.2612 | 84.455 | 86.989 | 88.1356 | 89.2617 | 90.0981 | 90.8091 |  |  | 22324 | 161.4737 | 162.5149 | 162.482 | 164.5508 | 167.5002 | 171.007 | 174.0628 | 176.3759 | 177.477 | 178.4163 | 179.0346 | 180.729 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)1
22325 | 66.5173 | 69.9554 | 71.0581 | 72.9006 | 75.059 | 77.498 | 79.5647 | 81.952 | 83.0322 | 84.0931 | 84.8811 | 85.5508 |  |  | 22325 | 144.4633 | 145.3948 | 145.3654 | 147.2163 | 149.8549 | 152.9923 | 155.7262 | 157.7957 | 158.7808 | 159.6211 | 160.1743 | 161.6902 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)2
22326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 22326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)3
22328 | 100.4917 | 105.6858 | 107.3518 | 110.1354 | 113.3962 | 117.0809 | 120.2033 | 123.8099 | 125.4418 | 127.0446 | 128.235 | 129.2469 |  |  | 22328 | 182.6434 | 183.8211 | 183.7839 | 186.1239 | 189.46 | 193.4265 | 196.883 | 199.4994 | 200.7448 | 201.8072 | 202.5066 | 204.4232 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)4
22329 | 62.8505 | 66.0991 | 67.141 | 68.882 | 70.9214 | 73.2259 | 75.1787 | 77.4344 | 78.455 | 79.4575 | 80.202 | 80.8348 |  |  | 22329 | 179.1736 | 180.329 | 180.2925 | 182.588 | 185.8607 | 189.7519 | 193.1427 | 195.7094 | 196.9311 | 197.9734 | 198.6595 | 200.5397 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)5
22330 | 6.345 | 6.6729 | 6.7781 | 6.9539 | 7.1598 | 7.3924 | 7.5896 | 7.8173 | 7.9203 | 8.0215 | 8.0967 | 8.1606 |  |  | 22330 | 13.168 | 13.253 | 13.2503 | 13.419 | 13.6595 | 13.9455 | 14.1947 | 14.3833 | 14.4731 | 14.5497 | 14.6001 | 14.7383 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)1
22331 | 92.6881 | 97.4789 | 99.0155 | 101.5829 | 104.5905 | 107.9891 | 110.869 | 114.1955 | 115.7007 | 117.179 | 118.277 | 119.2103 |  |  | 22331 | 205.127 | 206.4497 | 206.408 | 209.036 | 212.7827 | 217.2376 | 221.1195 | 224.058 | 225.4567 | 226.65 | 227.4354 | 229.588 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)2
23340 | 74.4455 | 78.2933 | 79.5275 | 81.5896 | 84.0052 | 86.7349 | 89.048 | 91.7198 | 92.9287 | 94.1161 | 94.998 | 95.7476 |  |  | 23340 | 73.3294 | 73.8023 | 73.7874 | 74.7268 | 76.0662 | 77.6588 | 79.0465 | 80.097 | 80.597 | 81.0235 | 81.3043 | 82.0738 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)3
23341 | 53.7389 | 56.5165 | 57.4074 | 58.896 | 60.6397 | 62.6102 | 64.2799 | 66.2085 | 67.0812 | 67.9383 | 68.5749 | 69.116 |  |  | 23341 | 111.8376 | 112.5588 | 112.536 | 113.9689 | 116.0116 | 118.4405 | 120.5569 | 122.159 | 122.9216 | 123.5722 | 124.0004 | 125.174 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)4
23342 | 79.7849 | 83.9087 | 85.2314 | 87.4415 | 90.0303 | 92.9558 | 95.4348 | 98.2982 | 99.5939 | 100.8664 | 101.8115 | 102.6149 |  |  | 23342 | 190.9463 | 192.1776 | 192.1387 | 194.5851 | 198.0728 | 202.2197 | 205.8333 | 208.5686 | 209.8706 | 210.9814 | 211.7126 | 213.7163 | [10 empty] | Rosebery kV | Load transfer capacity (MVA)5
23343 | 110.2007 | 115.8967 | 117.7236 | 120.7762 | 124.352 | 128.3927 | 131.8167 | 135.7718 | 137.5614 | 139.319 | 140.6245 | 141.7341 |  |  | 23343 | 176.8009 | 177.941 | 177.905 | 180.1701 | 183.3995 | 187.2392 | 190.585 | 193.1178 | 194.3233 | 195.3518 | 196.0288 | 197.8841 | [10 empty] | Savage River DL | Load transfer capacity (MVA)1
23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 23346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Savage River DL | Load transfer capacity (MVA)2
23347 | 58.4119 | 61.431 | 62.3994 | 64.0174 | 65.9128 | 68.0545 | 69.8694 | 71.9658 | 72.9144 | 73.846 | 74.538 | 75.1261 |  |  | 23347 | 121.247 | 122.0288 | 122.0041 | 123.5575 | 125.7721 | 128.4053 | 130.6999 | 132.4368 | 133.2635 | 133.9688 | 134.4331 | 135.7054 | [10 empty] | Savage River DL | Load transfer capacity (MVA)3
23348 | 64.4551 | 67.7866 | 68.8551 | 70.6405 | 72.732 | 75.0953 | 77.098 | 79.4113 | 80.458 | 81.486 | 82.2495 | 82.8985 |  |  | 23348 | 141.8518 | 142.7665 | 142.7376 | 144.555 | 147.146 | 150.2266 | 152.9111 | 154.9432 | 155.9104 | 156.7356 | 157.2788 | 158.7673 | [10 empty] | Savage River DL | Load transfer capacity (MVA)4
24401 | 74.1864 | 78.0209 | 79.2508 | 81.3057 | 83.7129 | 86.4331 | 88.7382 | 91.4007 | 92.6054 | 93.7886 | 94.6675 | 95.4144 |  |  | 24401 | 146.2113 | 147.1541 | 147.1244 | 148.9976 | 151.6682 | 154.8435 | 157.6105 | 159.7051 | 160.702 | 161.5525 | 162.1124 | 163.6467 | [10 empty] | Savage River DL | Load transfer capacity (MVA)5
24402 | 65.4047 | 68.7852 | 69.8696 | 71.6812 | 73.8035 | 76.2017 | 78.2339 | 80.5812 | 81.6433 | 82.6865 | 83.4613 | 84.1198 |  |  | 24402 | 125.8022 | 126.6134 | 126.5878 | 128.1996 | 130.4974 | 133.2295 | 135.6102 | 137.4124 | 138.2702 | 139.002 | 139.4837 | 140.8038 | [10 empty] | Scottsdale | Load transfer capacity (MVA)1 | Derby | 4.8
24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Scottsdale | Load transfer capacity (MVA)2 | George Town | 3.2
24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Scottsdale | Load transfer capacity (MVA)3
24405 | 126.5404 | 133.0809 | 135.1787 | 138.6838 | 142.7899 | 147.4297 | 151.3614 | 155.9029 | 157.9578 | 159.9761 | 161.4751 | 162.7492 |  |  | 24405 | 267.7691 | 269.4958 | 269.4413 | 272.8719 | 277.7628 | 283.578 | 288.6455 | 292.4813 | 294.3072 | 295.8648 | 296.8901 | 299.7 | [10 empty] | Scottsdale | Load transfer capacity (MVA)4
24406 | 74.175 | 78.0089 | 79.2386 | 81.2932 | 83.7001 | 86.4198 | 88.7245 | 91.3866 | 92.5912 | 93.7742 | 94.6529 | 95.3998 |  |  | 24406 | 144.3336 | 145.2643 | 145.2349 | 147.0841 | 149.7204 | 152.8549 | 155.5864 | 157.654 | 158.6382 | 159.4778 | 160.0305 | 161.545 | [10 empty] | Scottsdale | Load transfer capacity (MVA)5
25305 | 42.5566 | 44.7562 | 45.4618 | 46.6406 | 48.0214 | 49.5819 | 50.9041 | 52.4315 | 53.1226 | 53.8013 | 54.3054 | 54.7339 |  |  | 25305 | 77.5443 | 78.0444 | 78.0286 | 79.0221 | 80.4384 | 82.1225 | 83.59 | 84.7008 | 85.2296 | 85.6807 | 85.9776 | 86.7913 | [10 empty] | Sheffield | Load transfer capacity (MVA)1
25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Sheffield | Load transfer capacity (MVA)2
25307 | 72.5746 | 76.3258 | 77.529 | 79.5393 | 81.8942 | 84.5553 | 86.8102 | 89.4149 | 90.5935 | 91.751 | 92.6107 | 93.3415 |  |  | 25307 | 158.3575 | 159.3786 | 159.3464 | 161.3752 | 164.2677 | 167.7068 | 170.7037 | 172.9722 | 174.052 | 174.9731 | 175.5795 | 177.2413 | [10 empty] | Sheffield | Load transfer capacity (MVA)3
25308 | 70.6752 | 74.3282 | 75.4999 | 77.4576 | 79.7508 | 82.3423 | 84.5382 | 87.0747 | 88.2224 | 89.3497 | 90.1869 | 90.8985 |  |  | 25308 | 154.5619 | 155.5586 | 155.5271 | 157.5073 | 160.3305 | 163.6872 | 166.6122 | 168.8263 | 169.8802 | 170.7793 | 171.3712 | 172.9931 | [10 empty] | Sheffield | Load transfer capacity (MVA)4
25309 | 92.8263 | 97.6242 | 99.1631 | 101.7344 | 104.7465 | 108.1501 | 111.0343 | 114.3658 | 115.8732 | 117.3538 | 118.4534 | 119.388 |  |  | 25309 | 151.1792 | 152.154 | 152.1232 | 154.0601 | 156.8214 | 160.1047 | 162.9657 | 165.1314 | 166.1622 | 167.0416 | 167.6205 | 169.2069 | [10 empty] | Sheffield | Load transfer capacity (MVA)5
25310 | 45.058 | 47.3869 | 48.1339 | 49.382 | 50.844 | 52.4961 | 53.8961 | 55.5133 | 56.245 | 56.9636 | 57.4974 | 57.9511 |  |  | 25310 | 82.6796 | 83.2127 | 83.1959 | 84.2552 | 85.7654 | 87.561 | 89.1256 | 90.3101 | 90.8738 | 91.3548 | 91.6714 | 92.539 | [10 empty] | Smithton | Load transfer capacity (MVA)1 | Port Latta | 5.1
26161 | 77.3565 | 81.3549 | 82.6373 | 84.7801 | 87.2901 | 90.1265 | 92.5301 | 95.3064 | 96.5626 | 97.7964 | 98.7128 | 99.4917 |  |  | 26161 | 141.8981 | 142.8131 | 142.7843 | 144.6022 | 147.194 | 150.2757 | 152.9611 | 154.9938 | 155.9614 | 156.7868 | 157.3302 | 158.8192 | [10 empty] | Smithton | Load transfer capacity (MVA)2
26162 | 68.9441 | 72.5076 | 73.6506 | 75.5603 | 77.7974 | 80.3254 | 82.4675 | 84.9419 | 86.0615 | 87.1611 | 87.9778 | 88.672 |  |  | 26162 | 162.8617 | 163.9119 | 163.8788 | 165.9653 | 168.94 | 172.477 | 175.5591 | 177.8921 | 179.0026 | 179.95 | 180.5736 | 182.2826 | [10 empty] | Smithton | Load transfer capacity (MVA)3
26163 | 37.1859 | 39.1079 | 39.7244 | 40.7544 | 41.961 | 43.3245 | 44.4799 | 45.8145 | 46.4184 | 47.0115 | 47.452 | 47.8264 |  |  | 26163 | 93.3469 | 93.9488 | 93.9298 | 95.1257 | 96.8307 | 98.858 | 100.6246 | 101.9618 | 102.5983 | 103.1413 | 103.4987 | 104.4783 | [10 empty] | Smithton | Load transfer capacity (MVA)4
26164 | 87.076 | 91.5767 | 93.0203 | 95.4323 | 98.2577 | 101.4505 | 104.156 | 107.2812 | 108.6952 | 110.084 | 111.1155 | 111.9923 |  |  | 26164 | 190.087 | 191.3127 | 191.274 | 193.7094 | 197.1814 | 201.3096 | 204.9069 | 207.63 | 208.9261 | 210.0318 | 210.7597 | 212.7544 | [10 empty] | Smithton | Load transfer capacity (MVA)5
26165 | 57.9319 | 60.9262 | 61.8866 | 63.4913 | 65.3711 | 67.4952 | 69.2952 | 71.3744 | 72.3152 | 73.2391 | 73.9254 | 74.5087 |  |  | 26165 | 129.0392 | 129.8712 | 129.845 | 131.4982 | 133.8551 | 136.6576 | 139.0996 | 140.9481 | 141.828 | 142.5786 | 143.0727 | 144.4268 | [10 empty] | Sorell | Load transfer capacity (MVA)1 | Avoca | 1.5
26166 | 37.2762 | 39.2029 | 39.8209 | 40.8534 | 42.0629 | 43.4297 | 44.588 | 45.9258 | 46.5311 | 47.1257 | 47.5672 | 47.9426 |  |  | 26166 | 81.5109 | 82.0365 | 82.0199 | 83.0642 | 84.553 | 86.3232 | 87.8658 | 89.0335 | 89.5893 | 90.0634 | 90.3755 | 91.2309 | [10 empty] | Sorell | Load transfer capacity (MVA)2 | Triabunna | 1.5
26167 | 104.5473 | 109.951 | 111.6843 | 114.5802 | 117.9725 | 121.806 | 125.0543 | 128.8065 | 130.5043 | 132.1717 | 133.4102 | 134.4629 |  |  | 26167 | 223.846 | 225.2894 | 225.2438 | 228.1117 | 232.2003 | 237.0617 | 241.2979 | 244.5046 | 246.0309 | 247.333 | 248.1902 | 250.5391 | [10 empty] | Sorell | Load transfer capacity (MVA)3 | Meadowbank | 1.5
26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 26169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Sorell | Load transfer capacity (MVA)4
27171 | 69.0914 | 72.6625 | 73.808 | 75.7218 | 77.9637 | 80.497 | 82.6438 | 85.1234 | 86.2454 | 87.3474 | 88.1659 | 88.8615 |  |  | 27171 | 148.6448 | 149.6033 | 149.573 | 151.4774 | 154.1925 | 157.4207 | 160.2337 | 162.3631 | 163.3767 | 164.2413 | 164.8105 | 166.3703 | [10 empty] | Sorell | Load transfer capacity (MVA)5
27172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | St Leonards | Load transfer capacity (MVA)1 | Trevallyn | 3
27173 | 20.9931 | 22.0782 | 22.4262 | 23.0077 | 23.6889 | 24.4586 | 25.1109 | 25.8644 | 26.2053 | 26.5401 | 26.7888 | 27.0002 |  |  | 27173 | 39.9372 | 40.1947 | 40.1866 | 40.6982 | 41.4277 | 42.295 | 43.0508 | 43.6229 | 43.8952 | 44.1276 | 44.2805 | 44.6996 | [10 empty] | St Leonards | Load transfer capacity (MVA)2 | Mowbray | 3
27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | St Leonards | Load transfer capacity (MVA)3 | Norwood | 10
27175 | 64.2531 | 67.5741 | 68.6393 | 70.4191 | 72.504 | 74.86 | 76.8564 | 79.1624 | 80.2058 | 81.2306 | 81.9918 | 82.6387 |  |  | 27175 | 146.7896 | 147.7361 | 147.7062 | 149.5869 | 152.268 | 155.4559 | 158.2339 | 160.3367 | 161.3376 | 162.1915 | 162.7536 | 164.2939 | [10 empty] | St Leonards | Load transfer capacity (MVA)4
27176 | 47.4757 | 49.9296 | 50.7166 | 52.0317 | 53.5722 | 55.313 | 56.7881 | 58.492 | 59.2629 | 60.0202 | 60.5826 | 61.0606 |  |  | 27176 | 70.5883 | 71.0435 | 71.0291 | 71.9334 | 73.2228 | 74.7558 | 76.0916 | 77.1028 | 77.5841 | 77.9948 | 78.2651 | 79.0058 | [10 empty] | St Leonards | Load transfer capacity (MVA)5
27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 27177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | St Marys | Load transfer capacity (MVA)1 | Avoca | 2.8
27178 | 50.0802 | 52.6687 | 53.499 | 54.8862 | 56.5112 | 58.3475 | 59.9035 | 61.7009 | 62.5141 | 63.3129 | 63.9061 | 64.4104 |  |  | 27178 | 114.3102 | 115.0473 | 115.024 | 116.4886 | 118.5765 | 121.059 | 123.2223 | 124.8598 | 125.6392 | 126.3042 | 126.7419 | 127.9414 | [10 empty] | St Marys | Load transfer capacity (MVA)2 | Triabunna | 4.5
28221 | 78.3861 | 82.4376 | 83.7372 | 85.9084 | 88.4519 | 91.3261 | 93.7616 | 96.5749 | 97.8478 | 99.098 | 100.0266 | 100.8158 |  |  | 28221 | 165.0863 | 166.1508 | 166.1172 | 168.2323 | 171.2476 | 174.8329 | 177.9571 | 180.322 | 181.4477 | 182.408 | 183.0401 | 184.7725 | [10 empty] | St Marys | Load transfer capacity (MVA)3 | Derby | 4
28222 | 75.2835 | 79.1746 | 80.4227 | 82.508 | 84.9509 | 87.7113 | 90.0504 | 92.7523 | 93.9748 | 95.1756 | 96.0674 | 96.8254 |  |  | 28222 | 162.2077 | 163.2536 | 163.2206 | 165.2988 | 168.2616 | 171.7843 | 174.854 | 177.1777 | 178.2837 | 179.2273 | 179.8484 | 181.5506 | [10 empty] | St Marys | Load transfer capacity (MVA)4
28223 | 109.2528 | 114.8997 | 116.711 | 119.7372 | 123.2823 | 127.2882 | 130.6828 | 134.6039 | 136.3781 | 138.1206 | 139.4148 | 140.5149 |  |  | 28223 | 241.9073 | 243.4671 | 243.4179 | 246.5172 | 250.9357 | 256.1893 | 260.7673 | 264.2327 | 265.8822 | 267.2894 | 268.2157 | 270.7542 | [10 empty] | St Marys | Load transfer capacity (MVA)5
28224 | 60.4502 | 63.5747 | 64.5769 | 66.2513 | 68.2129 | 70.4294 | 72.3076 | 74.4771 | 75.4588 | 76.423 | 77.1391 | 77.7477 |  |  | 28224 | 144.2532 | 145.1833 | 145.154 | 147.0021 | 149.637 | 152.7698 | 155.4997 | 157.5662 | 158.5498 | 159.3889 | 159.9413 | 161.455 | [10 empty] | Trevallyn | Load transfer capacity (MVA)1 | George Town | 3.6
28225 | 3.0807 | 3.2399 | 3.291 | 3.3763 | 3.4763 | 3.5893 | 3.685 | 3.7955 | 3.8456 | 3.8947 | 3.9312 | 3.9622 |  |  | 28225 | 4.0729 | 4.0991 | 4.0983 | 4.1505 | 4.2249 | 4.3133 | 4.3904 | 4.4487 | 4.4765 | 4.5002 | 4.5158 | 4.5585 | [10 empty] | Trevallyn | Load transfer capacity (MVA)2 | Mowbray | 36.1
28228 | 60.1464 | 63.2552 | 64.2523 | 65.9183 | 67.87 | 70.0753 | 71.9441 | 74.1028 | 75.0795 | 76.0388 | 76.7513 | 77.3569 |  |  | 28228 | 128.6854 | 129.5151 | 129.489 | 131.1376 | 133.4881 | 136.2829 | 138.7182 | 140.5616 | 141.4391 | 142.1877 | 142.6804 | 144.0308 | [10 empty] | Trevallyn | Load transfer capacity (MVA)3 | Norwood | 21.7
28229 | 4.927 | 5.1817 | 5.2634 | 5.3998 | 5.5597 | 5.7404 | 5.8934 | 6.0703 | 6.1503 | 6.2289 | 6.2872 | 6.3368 |  |  | 28229 | 11.7618 | 11.8376 | 11.8352 | 11.9859 | 12.2008 | 12.4562 | 12.6788 | 12.8473 | 12.9275 | 12.9959 | 13.0409 | 13.1644 | [10 empty] | Trevallyn | Load transfer capacity (MVA)4 | St Leonards | 21.7
28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Trevallyn | Load transfer capacity (MVA)5 | Hadspen | 14.4
28231 | 118.9917 | 125.142 | 127.1147 | 130.4107 | 134.2718 | 138.6348 | 142.332 | 146.6026 | 148.5349 | 150.4328 | 151.8424 | 153.0405 |  |  | 28231 | 217.6117 | 219.0149 | 218.9706 | 221.7586 | 225.7334 | 230.4594 | 234.5776 | 237.6949 | 239.1788 | 240.4446 | 241.2779 | 243.5614 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)1 | St Marys | 3
28232 | 75.7386 | 79.6533 | 80.9089 | 83.0069 | 85.4645 | 88.2415 | 90.5948 | 93.313 | 94.543 | 95.751 | 96.6482 | 97.4108 |  |  | 28232 | 173.6888 | 174.8088 | 174.7734 | 176.9987 | 180.1712 | 183.9432 | 187.2302 | 189.7184 | 190.9027 | 191.9131 | 192.5782 | 194.4008 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)2 | Sorell | 1.8
29481 | 33.0609 | 34.7698 | 35.3179 | 36.2336 | 37.3064 | 38.5186 | 39.5459 | 40.7324 | 41.2693 | 41.7966 | 42.1882 | 42.5211 |  |  | 29481 | 66.5488 | 66.9779 | 66.9644 | 67.817 | 69.0325 | 70.4778 | 71.7372 | 72.6905 | 73.1443 | 73.5314 | 73.7863 | 74.4846 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)3
29482 | 16.8529 | 17.724 | 18.0034 | 18.4702 | 19.0171 | 19.635 | 20.1587 | 20.7635 | 21.0372 | 21.306 | 21.5056 | 21.6753 |  |  | 29482 | 43.6026 | 43.8838 | 43.8749 | 44.4335 | 45.2299 | 46.1769 | 47.002 | 47.6267 | 47.924 | 48.1776 | 48.3446 | 48.8021 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)4
29483 | 72.8599 | 76.6258 | 77.8337 | 79.8519 | 82.2161 | 84.8876 | 87.1515 | 89.7664 | 90.9496 | 92.1116 | 92.9747 | 93.7084 |  |  | 29483 | 144.5389 | 145.4709 | 145.4415 | 147.2933 | 149.9333 | 153.0723 | 155.8077 | 157.8783 | 158.8638 | 159.7046 | 160.2581 | 161.7748 | [10 empty] | Triabunna (RT) | Load transfer capacity (MVA)5
29485 | 81.713 | 85.9364 | 87.2911 | 89.5545 | 92.206 | 95.2021 | 97.741 | 100.6737 | 102.0006 | 103.3039 | 104.2719 | 105.0946 |  |  | 29485 | 95.3524 | 95.9672 | 95.9478 | 97.1695 | 98.9111 | 100.9819 | 102.7864 | 104.1524 | 104.8026 | 105.3572 | 105.7224 | 106.7229 | [10 empty] | Tungatinah | Load transfer capacity (MVA)1
29486 | 36.6084 | 38.5006 | 39.1075 | 40.1216 | 41.3094 | 42.6517 | 43.7892 | 45.1031 | 45.6976 | 46.2814 | 46.7151 | 47.0837 |  |  | 29486 | 46.6245 | 46.9251 | 46.9157 | 47.513 | 48.3646 | 49.3772 | 50.2595 | 50.9274 | 51.2454 | 51.5166 | 51.6951 | 52.1844 | [10 empty] | Tungatinah | Load transfer capacity (MVA)2
29488 | 164.1279 | 172.6112 | 175.3321 | 179.8784 | 185.2041 | 191.2221 | 196.3217 | 202.2122 | 204.8775 | 207.4953 | 209.4395 | 211.0921 |  |  | 29488 | 228.5126 | 229.9861 | 229.9396 | 232.8673 | 237.0411 | 242.0039 | 246.3284 | 249.6019 | 251.16 | 252.4893 | 253.3643 | 255.7623 | [10 empty] | Tungatinah | Load transfer capacity (MVA)3
29489 | 61.6714 | 64.859 | 65.8814 | 67.5896 | 69.5908 | 71.8521 | 73.7682 | 75.9816 | 76.9831 | 77.9667 | 78.6973 | 79.3183 |  |  | 29489 | 114.4607 | 115.1988 | 115.1755 | 116.642 | 118.7326 | 121.2184 | 123.3845 | 125.0242 | 125.8047 | 126.4705 | 126.9088 | 128.1099 | [10 empty] | Tungatinah | Load transfer capacity (MVA)4
29490 | 35.6531 | 37.4959 | 38.087 | 39.0746 | 40.2314 | 41.5387 | 42.6465 | 43.9261 | 44.5051 | 45.0737 | 45.4961 | 45.855 |  |  | 29490 | 66.6859 | 67.1159 | 67.1023 | 67.9567 | 69.1747 | 70.623 | 71.885 | 72.8403 | 73.295 | 73.6829 | 73.9383 | 74.638 | [10 empty] | Tungatinah | Load transfer capacity (MVA)5
29491 | 59.6291 | 62.7111 | 63.6997 | 65.3514 | 67.2862 | 69.4726 | 71.3254 | 73.4654 | 74.4338 | 75.3848 | 76.0912 | 76.6916 |  |  | 29491 | 86.7783 | 87.3378 | 87.3202 | 88.432 | 90.017 | 91.9016 | 93.5439 | 94.787 | 95.3787 | 95.8835 | 96.2158 | 97.1264 | [10 empty] | Ulverstone | Load transfer capacity (MVA)1 | Burnie | 6.8
29492 | 1.9953 | 2.0984 | 2.1315 | 2.1868 | 2.2515 | 2.3247 | 2.3867 | 2.4583 | 2.4907 | 2.5225 | 2.5462 | 2.5662 |  |  | 29492 | 2.2829 | 2.2977 | 2.2972 | 2.3265 | 2.3682 | 2.4177 | 2.4609 | 2.4936 | 2.5092 | 2.5225 | 2.5312 | 2.5552 | [10 empty] | Ulverstone | Load transfer capacity (MVA)2 | Devonport | 10.3
30603 | 167.9767 | 176.6589 | 179.4437 | 184.0966 | 189.5471 | 195.7063 | 200.9255 | 206.9541 | 209.6819 | 212.3611 | 214.3509 | 216.0423 |  |  | 30603 | 232.6274 | 234.1274 | 234.0801 | 237.0605 | 241.3095 | 246.3616 | 250.764 | 254.0964 | 255.6826 | 257.0358 | 257.9266 | 260.3677 | [10 empty] | Ulverstone | Load transfer capacity (MVA)3 | Railton | 3.4
30604 | 102.1115 | 107.3893 | 109.0822 | 111.9106 | 115.224 | 118.968 | 122.1407 | 125.8055 | 127.4637 | 129.0923 | 130.3019 | 131.3301 |  |  | 30604 | 43.3572 | 43.6367 | 43.6279 | 44.1834 | 44.9753 | 45.9169 | 46.7374 | 47.3586 | 47.6542 | 47.9064 | 48.0724 | 48.5274 | [10 empty] | Ulverstone | Load transfer capacity (MVA)4
30605 | 202.6175 | 213.0901 | 216.4492 | 222.0617 | 228.6362 | 236.0656 | 242.3611 | 249.6329 | 252.9233 | 256.1549 | 258.5552 | 260.5953 |  |  | 30605 | 217.7263 | 219.1303 | 219.086 | 221.8754 | 225.8523 | 230.5807 | 234.7011 | 237.8201 | 239.3047 | 240.5712 | 241.405 | 243.6897 | [10 empty] | Ulverstone | Load transfer capacity (MVA)5
30606 | 144.5045 | 151.9735 | 154.3692 | 158.3719 | 163.0608 | 168.3593 | 172.8492 | 178.0355 | 180.3821 | 182.6869 | 184.3987 | 185.8537 |  |  | 30606 | 305.2075 | 307.1756 | 307.1135 | 311.0237 | 316.5984 | 323.2268 | 329.0027 | 333.3749 | 335.456 | 337.2314 | 338.4001 | 341.6029 | [10 empty] | Waddamana | Load transfer capacity (MVA)1 | Arthurs Lake | 0.9
30607 | 70.6275 | 74.278 | 75.4489 | 77.4053 | 79.697 | 82.2867 | 84.4812 | 87.016 | 88.1629 | 89.2894 | 90.126 | 90.8372 |  |  | 30607 | 140.6305 | 141.5373 | 141.5087 | 143.3104 | 145.879 | 148.9332 | 151.5946 | 153.6091 | 154.5681 | 155.3861 | 155.9246 | 157.4003 | [10 empty] | Waddamana | Load transfer capacity (MVA)2
30608 | 146.0839 | 153.6345 | 156.0564 | 160.1028 | 164.843 | 170.1994 | 174.7384 | 179.9813 | 182.3536 | 184.6835 | 186.414 | 187.885 |  |  | 30608 | 163.0993 | 164.151 | 164.1178 | 166.2074 | 169.1865 | 172.7286 | 175.8152 | 178.1517 | 179.2638 | 180.2125 | 180.8371 | 182.5486 | [10 empty] | Waddamana | Load transfer capacity (MVA)3
31002 | 101.7455 | 107.0045 | 108.6912 | 111.5095 | 114.811 | 118.5417 | 121.703 | 125.3546 | 127.0069 | 128.6297 | 129.835 | 130.8594 |  |  | 31002 | 117.5917 | 118.35 | 118.3261 | 119.8326 | 121.9805 | 124.5343 | 126.7597 | 128.4442 | 129.246 | 129.93 | 130.3803 | 131.6143 | [10 empty] | Waddamana | Load transfer capacity (MVA)4
31007 | 69.8143 | 73.4228 | 74.5802 | 76.514 | 78.7794 | 81.3393 | 83.5085 | 86.0141 | 87.1478 | 88.2613 | 89.0883 | 89.7913 |  |  | 31007 | 134.7005 | 135.5691 | 135.5417 | 137.2675 | 139.7278 | 142.6532 | 145.2023 | 147.132 | 148.0504 | 148.834 | 149.3498 | 150.7633 | [10 empty] | Waddamana | Load transfer capacity (MVA)5
31008 | 108.0382 | 113.6223 | 115.4134 | 118.4061 | 121.9117 | 125.8731 | 129.23 | 133.1074 | 134.8619 | 136.585 | 137.8648 | 138.9527 |  |  | 31008 | 129.7426 | 130.5792 | 130.5528 | 132.215 | 134.5848 | 137.4025 | 139.8578 | 141.7164 | 142.6011 | 143.3558 | 143.8526 | 145.2141 | [10 empty] | Wayatinah | Load transfer capacity (MVA)1
31010 | 86.9712 | 91.4665 | 92.9083 | 95.3174 | 98.1394 | 101.3284 | 104.0307 | 107.152 | 108.5644 | 109.9515 | 110.9818 | 111.8575 |  |  | 31010 | 80.392 | 80.9104 | 80.894 | 81.924 | 83.3924 | 85.1383 | 86.6597 | 87.8113 | 88.3595 | 88.8271 | 89.135 | 89.9786 | [10 empty] | Wayatinah | Load transfer capacity (MVA)2
32374 | 84.115 | 88.4627 | 89.8572 | 92.1871 | 94.9165 | 98.0007 | 100.6143 | 103.6331 | 104.9991 | 106.3407 | 107.3371 | 108.184 |  |  | 32374 | 197.9145 | 199.1907 | 199.1504 | 201.686 | 205.301 | 209.5992 | 213.3447 | 216.1798 | 217.5293 | 218.6806 | 219.4385 | 221.5153 | [10 empty] | Wayatinah | Load transfer capacity (MVA)3
32377 | 100.5597 | 105.7573 | 107.4244 | 110.2099 | 113.4729 | 117.1601 | 120.2846 | 123.8936 | 125.5266 | 127.1305 | 128.3217 | 129.3343 |  |  | 32377 | 146.4642 | 147.4086 | 147.3788 | 149.2553 | 151.9305 | 155.1113 | 157.8831 | 159.9813 | 160.98 | 161.832 | 162.3928 | 163.9297 | [10 empty] | Wayatinah | Load transfer capacity (MVA)4
32379 | 108.0263 | 113.6099 | 115.4008 | 118.3931 | 121.8984 | 125.8593 | 129.2158 | 133.0928 | 134.8471 | 136.5701 | 137.8497 | 138.9375 |  |  | 32379 | 247.4669 | 249.0626 | 249.0123 | 252.1828 | 256.7028 | 262.0772 | 266.7604 | 270.3055 | 271.9928 | 273.4324 | 274.38 | 276.9768 | [10 empty] | Wayatinah | Load transfer capacity (MVA)5
33271 | 82.6431 | 86.9147 | 88.2848 | 90.574 | 93.2556 | 96.2859 | 98.8537 | 101.8197 | 103.1617 | 104.4799 | 105.4589 | 106.291 |  |  | 33271 | 146.1296 | 147.0719 | 147.0421 | 148.9143 | 151.5834 | 154.757 | 157.5225 | 159.6158 | 160.6122 | 161.4623 | 162.0218 | 163.5552 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)1
33272 | 94.9982 | 99.9083 | 101.4833 | 104.1147 | 107.1972 | 110.6805 | 113.6322 | 117.0416 | 118.5843 | 120.0995 | 121.2248 | 122.1814 |  |  | 33272 | 208.7206 | 210.0665 | 210.024 | 212.6981 | 216.5105 | 221.0434 | 224.9933 | 227.9833 | 229.4065 | 230.6207 | 231.4199 | 233.6101 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)2
33273 | 0.86119 | 0.9057 | 0.91998 | 0.94383 | 0.97177 | 1.0034 | 1.0301 | 1.061 | 1.075 | 1.0887 | 1.0989 | 1.1076 |  |  | 33273 | 1.289 | 1.2973 | 1.297 | 1.3135 | 1.3371 | 1.3651 | 1.3895 | 1.4079 | 1.4167 | 1.4242 | 1.4292 | 1.4427 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)3
33274 | 120.5232 | 126.7527 | 128.7508 | 132.0892 | 136 | 140.4192 | 144.164 | 148.4895 | 150.4467 | 152.369 | 153.7967 | 155.0102 |  |  | 33274 | 170.8896 | 171.9915 | 171.9567 | 174.1461 | 177.2675 | 180.9788 | 184.2128 | 186.6609 | 187.8261 | 188.8202 | 189.4745 | 191.2678 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)4
33275 | 43.9044 | 46.1737 | 46.9016 | 48.1177 | 49.5423 | 51.1522 | 52.5163 | 54.092 | 54.805 | 55.5052 | 56.0253 | 56.4674 |  |  | 33275 | 76.195 | 76.6864 | 76.6709 | 77.6471 | 79.0388 | 80.6935 | 82.1355 | 83.227 | 83.7466 | 84.1898 | 84.4816 | 85.2811 | [10 empty] | Wesley Vale | Load transfer capacity (MVA)5
33276 | 107.2464 | 112.7896 | 114.5676 | 117.5383 | 121.0183 | 124.9506 | 128.2829 | 132.1319 | 133.8735 | 135.584 | 136.8545 | 137.9344 |  |  | 33276 | 212.406 | 213.7757 | 213.7324 | 216.4537 | 220.3334 | 224.9463 | 228.966 | 232.0088 | 233.4571 | 234.6927 | 235.5061 | 237.735 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)1 | Rokeby | 3.1
33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 33277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)2 | Howrah Zone | 3.1
34251 | 56.3899 | 59.3045 | 60.2394 | 61.8013 | 63.6311 | 65.6987 | 67.4508 | 69.4746 | 70.3903 | 71.2897 | 71.9577 | 72.5255 |  |  | 34251 | 128.6859 | 129.5157 | 129.4895 | 131.1382 | 133.4887 | 136.2834 | 138.7188 | 140.5622 | 141.4397 | 142.1883 | 142.681 | 144.0314 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)3 | Cambridge Zone | 6.2
34252 | 111.6585 | 117.4298 | 119.2809 | 122.3738 | 125.997 | 130.0911 | 133.5604 | 137.5678 | 139.3811 | 141.162 | 142.4847 | 143.609 |  |  | 34252 | 251.836 | 253.4599 | 253.4086 | 256.6351 | 261.2349 | 266.7042 | 271.4701 | 275.0777 | 276.7949 | 278.2598 | 279.2242 | 281.8668 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)4 | Geilston Bay | 4.1
34253 | 50.2974 | 52.8971 | 53.731 | 55.1242 | 56.7562 | 58.6005 | 60.1633 | 61.9684 | 62.7852 | 63.5874 | 64.1833 | 64.6897 |  |  | 34253 | 122.9428 | 123.7356 | 123.7106 | 125.2857 | 127.5313 | 130.2013 | 132.5279 | 134.2891 | 135.1274 | 135.8426 | 136.3134 | 137.6035 | [10 empty] | Zs-Bellerive | Load transfer capacity (MVA)5
34254 | 7.9371 | 8.3474 | 8.479 | 8.6988 | 8.9564 | 9.2474 | 9.494 | 9.7789 | 9.9078 | 10.0344 | 10.1284 | 10.2083 |  |  | 34254 | 11.1804 | 11.2525 | 11.2502 | 11.3935 | 11.5977 | 11.8405 | 12.0521 | 12.2122 | 12.2885 | 12.3535 | 12.3963 | 12.5137 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)1 | Rokeby | 7.4
34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)2 | Bellerive | 7.4
34256 | 62.7765 | 66.0212 | 67.0619 | 68.8008 | 70.8378 | 73.1396 | 75.0901 | 77.3432 | 78.3626 | 79.3639 | 80.1075 | 80.7396 |  |  | 34256 | 144.7955 | 145.7291 | 145.6997 | 147.5548 | 150.1995 | 153.3441 | 156.0843 | 158.1585 | 159.1458 | 159.9881 | 160.5426 | 162.062 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)3
34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34257 | 0 | 240.4115 | 232.1186 | 257.7582 | 253.5571 | 253.3961 | 253.7698 | 254.9041 | 258.2804 | 268.9445 | 277.653 | 283.4447 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)4
34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 34258 | 0 | 78.4376 | 75.7319 | 76.339 | 75.0948 | 75.0471 | 75.1578 | 75.4937 | 76.4937 | 79.652 | 82.2312 | 83.9465 | [10 empty] | Zs-Cambridge | Load transfer capacity (MVA)5
34259 | 100.5116 | 105.7067 | 107.373 | 110.1571 | 113.4186 | 117.104 | 120.227 | 123.8343 | 125.4665 | 127.0696 | 128.2603 | 129.2723 |  |  | 34259 | 236.3474 | 237.8714 | 237.8234 | 240.8514 | 245.1683 | 250.3012 | 254.774 | 258.1598 | 259.7713 | 261.1462 | 262.0512 | 264.5313
34260 | 47.1188 | 49.5542 | 50.3354 | 51.6405 | 53.1695 | 54.8972 | 56.3612 | 58.0523 | 58.8174 | 59.5689 | 60.1271 | 60.6016 |  |  | 34260 | 76.3584 | 76.8507 | 76.8352 | 77.8135 | 79.2082 | 80.8665 | 82.3116 | 83.4054 | 83.9261 | 84.3702 | 84.6626 | 85.4639
34261 | 66.5899 | 70.0317 | 71.1357 | 72.9802 | 75.1409 | 77.5825 | 79.6515 | 82.0414 | 83.1228 | 84.1849 | 84.9737 | 85.6442 |  |  | 34261 | 111.771 | 112.4917 | 112.4689 | 113.9009 | 115.9424 | 118.3698 | 120.4851 | 122.0862 | 122.8483 | 123.4985 | 123.9265 | 125.0994
34262 | 67.3074 | 70.7863 | 71.9022 | 73.7666 | 75.9506 | 78.4185 | 80.5098 | 82.9254 | 84.0185 | 85.092 | 85.8893 | 86.567 |  |  | 34262 | 133.2638 | 134.1231 | 134.096 | 135.8034 | 138.2375 | 141.1316 | 143.6536 | 145.5626 | 146.4713 | 147.2465 | 147.7568 | 149.1552
34263 | 60.4724 | 63.598 | 64.6006 | 66.2756 | 68.2379 | 70.4552 | 72.3341 | 74.5045 | 75.4865 | 76.451 | 77.1674 | 77.7762 |  |  | 34263 | 127.7162 | 128.5398 | 128.5138 | 130.15 | 132.4828 | 135.2565 | 137.6735 | 139.5031 | 140.3739 | 141.1168 | 141.6059 | 142.9461
34264 | 101.7666 | 107.0267 | 108.7138 | 111.5327 | 114.8348 | 118.5663 | 121.7283 | 125.3806 | 127.0332 | 128.6564 | 129.8619 | 130.8866 |  |  | 34264 | 168.2642 | 169.3492 | 169.315 | 171.4708 | 174.5442 | 178.1984 | 181.3828 | 183.7932 | 184.9405 | 185.9193 | 186.5637 | 188.3294 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)1
36240 | 99.6662 | 104.8176 | 106.4699 | 109.2306 | 112.4646 | 116.1191 | 119.2158 | 122.7928 | 124.4113 | 126.0009 | 127.1815 | 128.1851 |  |  | 36240 | 113.904 | 114.6385 | 114.6153 | 116.0746 | 118.1551 | 120.6289 | 122.7844 | 124.4162 | 125.1928 | 125.8554 | 126.2916 | 127.4868 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)2
37001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 37001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)3
37002 | 50.0879 | 52.6768 | 53.5072 | 54.8946 | 56.5199 | 58.3564 | 59.9127 | 61.7104 | 62.5237 | 63.3226 | 63.916 | 64.4203 |  |  | 37002 | 17.1698 | 17.2805 | 17.277 | 17.497 | 17.8106 | 18.1835 | 18.5084 | 18.7544 | 18.8715 | 18.9713 | 19.0371 | 19.2173 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)4
38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 38422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Claremont | Load transfer capacity (MVA)5
38423 | 39.6526 | 41.7021 | 42.3595 | 43.4579 | 44.7445 | 46.1984 | 47.4305 | 48.8536 | 49.4975 | 50.13 | 50.5997 | 50.999 |  |  | 38423 | 43.017 | 43.2944 | 43.2856 | 43.8367 | 44.6225 | 45.5567 | 46.3708 | 46.987 | 47.2803 | 47.5305 | 47.6953 | 48.1467 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)1
39010 | 35.5269 | 37.3632 | 37.9522 | 38.9362 | 40.089 | 41.3917 | 42.4955 | 43.7706 | 44.3475 | 44.9141 | 45.335 | 45.6927 |  |  | 39010 | 69.9765 | 70.4277 | 70.4135 | 71.31 | 72.5881 | 74.1079 | 75.4321 | 76.4346 | 76.9117 | 77.3188 | 77.5867 | 78.321 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)2
39011 | 32.6559 | 34.3438 | 34.8852 | 35.7897 | 36.8494 | 38.0467 | 39.0614 | 40.2334 | 40.7637 | 41.2845 | 41.6714 | 42.0002 |  |  | 39011 | 60.3952 | 60.7847 | 60.7724 | 61.5461 | 62.6493 | 63.9609 | 65.1039 | 65.9691 | 66.3809 | 66.7322 | 66.9635 | 67.5972 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)3
39012 | 35.7458 | 37.5934 | 38.186 | 39.1761 | 40.336 | 41.6467 | 42.7574 | 44.0403 | 44.6207 | 45.1909 | 45.6143 | 45.9742 |  |  | 39012 | 65.6845 | 66.1081 | 66.0947 | 66.9362 | 68.136 | 69.5625 | 70.8055 | 71.7465 | 72.1944 | 72.5765 | 72.828 | 73.5172 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)4
39013 | 39.9056 | 41.9682 | 42.6297 | 43.7351 | 45.03 | 46.4932 | 47.7331 | 49.1653 | 49.8133 | 50.4498 | 50.9225 | 51.3243 |  |  | 39013 | 77.2042 | 77.702 | 77.6863 | 78.6754 | 80.0856 | 81.7622 | 83.2233 | 84.3293 | 84.8557 | 85.3048 | 85.6004 | 86.4106 | [10 empty] | Zs-Derwent Park | Load transfer capacity (MVA)5
39564 | 8.9828 | 9.4471 | 9.596 | 9.8448 | 10.1363 | 10.4657 | 10.7448 | 11.0672 | 11.213 | 11.3563 | 11.4627 | 11.5532 |  |  | 39564 | 10.266 | 10.3322 | 10.3301 | 10.4617 | 10.6492 | 10.8721 | 11.0664 | 11.2135 | 11.2835 | 11.3432 | 11.3825 | 11.4902 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)1
39565 | 71.4514 | 75.1445 | 76.3291 | 78.3082 | 80.6267 | 83.2466 | 85.4667 | 88.031 | 89.1913 | 90.3309 | 91.1774 | 91.8968 |  |  | 39565 | 135.0801 | 135.9511 | 135.9237 | 137.6543 | 140.1216 | 143.0552 | 145.6115 | 147.5466 | 148.4676 | 149.2534 | 149.7707 | 151.1881 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)2
39566 | 83.6111 | 87.9327 | 89.3189 | 91.6349 | 94.3479 | 97.4136 | 100.0115 | 103.0123 | 104.3701 | 105.7036 | 106.6941 | 107.536 |  |  | 39566 | 82.5162 | 83.0483 | 83.0315 | 84.0887 | 85.5958 | 87.3879 | 88.9495 | 90.1315 | 90.6942 | 91.1742 | 91.4902 | 92.3561 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)3
39568 | 55.6149 | 58.4895 | 59.4115 | 60.952 | 62.7566 | 64.7958 | 66.5239 | 68.5199 | 69.423 | 70.31 | 70.9688 | 71.5288 |  |  | 39568 | 85.6693 | 86.2217 | 86.2043 | 87.3019 | 88.8666 | 90.7272 | 92.3484 | 93.5757 | 94.1598 | 94.6582 | 94.9862 | 95.8852 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)4
39569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 39569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-East Hobart | Load transfer capacity (MVA)5
39570 | 30.821 | 32.4141 | 32.925 | 33.7788 | 34.7789 | 35.909 | 36.8666 | 37.9728 | 38.4733 | 38.9649 | 39.33 | 39.6403 |  |  | 39570 | 22.1578 | 22.3007 | 22.2962 | 22.5801 | 22.9848 | 23.466 | 23.8853 | 24.2027 | 24.3538 | 24.4827 | 24.5676 | 24.8001 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)1 | Bellerive | 5.1
39571 | 73.1481 | 76.9289 | 78.1416 | 80.1678 | 82.5413 | 85.2234 | 87.4962 | 90.1214 | 91.3093 | 92.476 | 93.3425 | 94.079 |  |  | 39571 | 55.4073 | 55.7646 | 55.7534 | 56.4632 | 57.4753 | 58.6786 | 59.7271 | 60.5209 | 60.8987 | 61.221 | 61.4331 | 62.0146 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)2 | Derwent Park | 5.1
40001 | 19.7122 | 20.7311 | 21.0579 | 21.6039 | 22.2435 | 22.9663 | 23.5788 | 24.2863 | 24.6064 | 24.9208 | 25.1543 | 25.3528 |  |  | 40001 | 36.9975 | 37.2361 | 37.2286 | 37.7026 | 38.3784 | 39.1819 | 39.882 | 40.412 | 40.6643 | 40.8795 | 41.0212 | 41.4094 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)3 | East Hobart | 3.8
40002 | 87.0228 | 91.5207 | 92.9634 | 95.3739 | 98.1977 | 101.3885 | 104.0924 | 107.2156 | 108.6288 | 110.0167 | 111.0476 | 111.9238 |  |  | 40002 | 117.3335 | 118.0901 | 118.0663 | 119.5695 | 121.7127 | 124.2608 | 126.4813 | 128.1622 | 128.9622 | 129.6448 | 130.0941 | 131.3253 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)4
40003 | 32.6408 | 34.3279 | 34.869 | 35.7732 | 36.8323 | 38.0291 | 39.0433 | 40.2148 | 40.7448 | 41.2654 | 41.6521 | 41.9808 |  |  | 40003 | 43.4286 | 43.7086 | 43.6998 | 44.2562 | 45.0494 | 45.9926 | 46.8144 | 47.4366 | 47.7327 | 47.9853 | 48.1516 | 48.6073 | [10 empty] | Zs-Geilston Bay | Load transfer capacity (MVA)5
41511 | 58.2694 | 61.2811 | 62.2472 | 63.8612 | 65.7519 | 67.8885 | 69.699 | 71.7902 | 72.7365 | 73.6658 | 74.3561 | 74.9428 |  |  | 41511 | 125.4877 | 126.2969 | 126.2714 | 127.8791 | 130.1712 | 132.8965 | 135.2713 | 137.0689 | 137.9246 | 138.6545 | 139.1351 | 140.4519 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)1
41512 | 92.9189 | 97.7216 | 99.262 | 101.8358 | 104.8509 | 108.2579 | 111.145 | 114.4798 | 115.9887 | 117.4708 | 118.5715 | 119.5071 |  |  | 41512 | 129.2303 | 130.0636 | 130.0373 | 131.693 | 134.0535 | 136.86 | 139.3057 | 141.1569 | 142.0381 | 142.7898 | 143.2847 | 144.6408 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)2
41513 | 83.4816 | 87.7965 | 89.1805 | 91.4929 | 94.2018 | 97.2628 | 99.8566 | 102.8527 | 104.2084 | 105.5399 | 106.5288 | 107.3694 |  |  | 41513 | 141.786 | 142.7002 | 142.6714 | 144.4879 | 147.0777 | 150.1569 | 152.8401 | 154.8713 | 155.8381 | 156.6628 | 157.2058 | 158.6936 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)3
41514 | 51.9166 | 54.6 | 55.4607 | 56.8988 | 58.5834 | 60.487 | 62.1001 | 63.9634 | 64.8064 | 65.6345 | 66.2495 | 66.7722 |  |  | 41514 | 69.3097 | 69.7567 | 69.7426 | 70.6305 | 71.8965 | 73.4018 | 74.7134 | 75.7063 | 76.1789 | 76.5821 | 76.8475 | 77.5748 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)4
41515 | 51.9476 | 54.6326 | 55.4938 | 56.9328 | 58.6184 | 60.5231 | 62.1372 | 64.0016 | 64.8451 | 65.6737 | 66.2891 | 66.8121 |  |  | 41515 | 102.8764 | 103.5398 | 103.5189 | 104.8369 | 106.716 | 108.9502 | 110.8971 | 112.3708 | 113.0723 | 113.6707 | 114.0647 | 115.1442 | [10 empty] | Zs-Gretna | Load transfer capacity (MVA)5
41516 | 78.6059 | 82.6688 | 83.972 | 86.1493 | 88.7 | 91.5822 | 94.0245 | 96.8457 | 98.1222 | 99.3759 | 100.3071 | 101.0986 |  |  | 41516 | 150.1943 | 151.1628 | 151.1323 | 153.0565 | 155.7999 | 159.0617 | 161.9041 | 164.0557 | 165.0798 | 165.9535 | 166.5286 | 168.1047 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)1 | Rokeby | 7.1
41517 | 64.9339 | 68.2901 | 69.3666 | 71.1653 | 73.2723 | 75.6532 | 77.6707 | 80.0012 | 81.0557 | 82.0913 | 82.8605 | 83.5143 |  |  | 41517 | 116.4061 | 117.1567 | 117.133 | 118.6244 | 120.7506 | 123.2786 | 125.4816 | 127.1491 | 127.9428 | 128.62 | 129.0657 | 130.2873 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)2 | Bellerive | 2.4
41518 | 67.965 | 71.4779 | 72.6046 | 74.4872 | 76.6926 | 79.1846 | 81.2964 | 83.7356 | 84.8393 | 85.9233 | 86.7284 | 87.4128 |  |  | 41518 | 133.0331 | 133.8909 | 133.8639 | 135.5683 | 137.9982 | 140.8873 | 143.4049 | 145.3106 | 146.2177 | 146.9916 | 147.501 | 148.897 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)3
43505 | 11.263 | 11.8451 | 12.0318 | 12.3438 | 12.7093 | 13.1222 | 13.4722 | 13.8764 | 14.0593 | 14.239 | 14.3724 | 14.4858 |  |  | 43505 | 18.1938 | 18.3111 | 18.3074 | 18.5405 | 18.8728 | 19.268 | 19.6123 | 19.8729 | 19.997 | 20.1028 | 20.1725 | 20.3634 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)4
43506 | 40.7636 | 42.8706 | 43.5464 | 44.6755 | 45.9982 | 47.4929 | 48.7594 | 50.2224 | 50.8844 | 51.5346 | 52.0174 | 52.4279 |  |  | 43506 | 59.9827 | 60.3694 | 60.3572 | 61.1257 | 62.2213 | 63.524 | 64.6591 | 65.5184 | 65.9274 | 66.2763 | 66.506 | 67.1354 | [10 empty] | Zs-Howrah | Load transfer capacity (MVA)5
43507 | 64.8799 | 68.2333 | 69.3089 | 71.1061 | 73.2113 | 75.5902 | 77.6061 | 79.9346 | 80.9882 | 82.023 | 82.7916 | 83.4449 |  |  | 43507 | 83.7253 | 84.2652 | 84.2482 | 85.3208 | 86.8501 | 88.6684 | 90.2529 | 91.4523 | 92.0232 | 92.5102 | 92.8308 | 93.7094 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)1
45001 | 60.6982 | 63.8355 | 64.8418 | 66.5231 | 68.4927 | 70.7183 | 72.6042 | 74.7827 | 75.7684 | 76.7365 | 77.4555 | 78.0667 |  |  | 45001 | 39.6618 | 39.9175 | 39.9094 | 40.4176 | 41.142 | 42.0034 | 42.7539 | 43.3221 | 43.5925 | 43.8233 | 43.9751 | 44.3913 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)2
45002 | 65.0442 | 68.4062 | 69.4845 | 71.2862 | 73.3968 | 75.7817 | 77.8027 | 80.1371 | 81.1934 | 82.2308 | 83.0013 | 83.6563 |  |  | 45002 | 67.9413 | 68.3794 | 68.3656 | 69.236 | 70.477 | 71.9525 | 73.2383 | 74.2115 | 74.6748 | 75.07 | 75.3302 | 76.0431 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)3
45003 | 94.3546 | 99.2315 | 314.9937 | 323.1613 | 332.7292 | 343.5409 | 352.7026 | 363.2852 | 368.0736 | 372.7765 | 376.2695 | 379.2385 |  |  | 45003 | 31.9232 | 32.129 | 262.7076 | 266.0524 | 270.8211 | 276.491 | 281.4318 | 285.1718 | 286.952 | 288.4707 | 289.4705 | 292.2101 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)4
48180 | 100.388 | 105.5767 | 107.241 | 110.0217 | 113.2791 | 116.96 | 120.0792 | 123.6821 | 125.3123 | 126.9134 | 128.1026 | 129.1134 |  |  | 48180 | 247.2749 | 248.8694 | 248.8191 | 251.9871 | 256.5037 | 261.8739 | 266.5535 | 270.0958 | 271.7818 | 273.2203 | 274.1671 | 276.7619 | [10 empty] | Zs-New Town | Load transfer capacity (MVA)5
48181 | 114.7471 | 120.678 | 122.5803 | 125.7588 | 129.4821 | 133.6895 | 137.2548 | 141.3731 | 143.2365 | 145.0666 | 146.4259 | 147.5813 |  |  | 48181 | 147.3407 | 148.2908 | 148.2608 | 150.1485 | 152.8397 | 156.0396 | 158.828 | 160.9387 | 161.9434 | 162.8004 | 163.3646 | 164.9108 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)1
48182 | 80.5989 | 84.7648 | 86.101 | 88.3336 | 90.9489 | 93.9042 | 96.4084 | 99.3011 | 100.61 | 101.8955 | 102.8503 | 103.6618 |  |  | 48182 | 138.7082 | 139.6027 | 139.5744 | 141.3515 | 143.8851 | 146.8975 | 149.5225 | 151.5095 | 152.4553 | 153.2622 | 153.7933 | 155.2489 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)2
48183 | 108.0736 | 113.6596 | 115.4513 | 118.4449 | 121.9517 | 125.9144 | 129.2724 | 133.1511 | 134.9061 | 136.6298 | 137.9101 | 138.9983 |  |  | 48183 | 172.8288 | 173.9433 | 173.9081 | 176.1223 | 179.2791 | 183.0325 | 186.3032 | 188.7791 | 189.9575 | 190.9629 | 191.6247 | 193.4383 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)3
48184 | 127.9813 | 134.5963 | 136.718 | 140.2631 | 144.4158 | 149.1085 | 153.085 | 157.6782 | 159.7565 | 161.7978 | 163.3138 | 164.6025 |  |  | 48184 | 211.8556 | 213.2217 | 213.1785 | 215.8928 | 219.7624 | 224.3634 | 228.3727 | 231.4076 | 232.8521 | 234.0845 | 234.8958 | 237.1189 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)4
48185 | 41.5983 | 43.7484 | 44.438 | 45.5903 | 46.9401 | 48.4654 | 49.7579 | 51.2508 | 51.9263 | 52.5898 | 53.0826 | 53.5014 |  |  | 48185 | 226.3515 | 227.811 | 227.765 | 230.6649 | 234.7993 | 239.7151 | 243.9987 | 247.2413 | 248.7847 | 250.1014 | 250.9682 | 253.3434 | [10 empty] | Zs-Richmond | Load transfer capacity (MVA)5
48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 48186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)1
48188 | 5.8319 | 6.1334 | 6.2301 | 6.3916 | 6.5808 | 6.7947 | 6.9759 | 7.1852 | 7.2799 | 7.3729 | 7.442 | 7.5007 |  |  | 48188 | 9.6998 | 9.7623 | 9.7604 | 9.8846 | 10.0618 | 10.2725 | 10.456 | 10.595 | 10.6611 | 10.7175 | 10.7547 | 10.8565 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)2
48189 | 51.0391 | 53.6771 | 54.5233 | 55.937 | 57.5932 | 59.4646 | 61.0504 | 62.8822 | 63.711 | 64.5251 | 65.1297 | 65.6436 |  |  | 48189 | 97.7771 | 98.4076 | 98.3877 | 99.6404 | 101.4264 | 103.5498 | 105.4002 | 106.8009 | 107.4676 | 108.0364 | 108.4108 | 109.4368 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)3
48190 | 137.422 | 144.5249 | 146.8031 | 150.6097 | 155.0688 | 160.1076 | 164.3774 | 169.3094 | 171.5411 | 173.7329 | 175.3608 | 176.7445 |  |  | 48190 | 237.9058 | 239.4398 | 239.3914 | 242.4394 | 246.7848 | 251.9516 | 256.4538 | 259.8619 | 261.4841 | 262.868 | 263.779 | 266.2755 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)4
48191 | 44.6208 | 46.9271 | 47.6669 | 48.9029 | 50.3507 | 51.9868 | 53.3733 | 54.9747 | 55.6993 | 56.411 | 56.9395 | 57.3888 |  |  | 48191 | 68.6974 | 69.1404 | 69.1264 | 70.0065 | 71.2613 | 72.7533 | 74.0533 | 75.0374 | 75.5059 | 75.9055 | 76.1685 | 76.8894 | [10 empty] | Zs-Rosny Park | Load transfer capacity (MVA)5
48192 | 121.1949 | 127.459 | 129.4683 | 132.8253 | 136.7579 | 141.2017 | 144.9673 | 149.317 | 151.2851 | 153.2181 | 154.6538 | 155.8741 |  |  | 48192 | 212.3564 | 213.7257 | 213.6825 | 216.4031 | 220.2819 | 224.8937 | 228.9125 | 231.9546 | 233.4026 | 234.6378 | 235.451 | 237.6794 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)1
48193 | 101.0763 | 106.3006 | 107.9763 | 110.7761 | 114.0558 | 117.7619 | 120.9025 | 124.5301 | 126.1715 | 127.7836 | 128.9809 | 129.9987 |  |  | 48193 | 181.4505 | 182.6205 | 182.5836 | 184.9083 | 188.2226 | 192.1632 | 195.5971 | 198.1964 | 199.4337 | 200.4892 | 201.184 | 203.0881 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)2
49101 | 28.5997 | 30.078 | 30.5521 | 31.3443 | 32.2723 | 33.321 | 34.2096 | 35.236 | 35.7005 | 36.1566 | 36.4954 | 36.7834 |  |  | 49101 | 31.3796 | 31.5819 | 31.5755 | 31.9775 | 32.5507 | 33.2322 | 33.826 | 34.2756 | 34.4895 | 34.6721 | 34.7922 | 35.1215 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)3
49202 | 10.2622 | 10.7927 | 10.9628 | 11.247 | 11.58 | 11.9563 | 12.2752 | 12.6435 | 12.8101 | 12.9738 | 13.0954 | 13.1987 |  |  | 49202 | 17.8846 | 17.9999 | 17.9963 | 18.2254 | 18.5521 | 18.9405 | 19.279 | 19.5352 | 19.6571 | 19.7612 | 19.8297 | 20.0173 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)4
49302 | 0.013308 | 0.013996 | 0.014216 | 0.014585 | 0.015017 | 0.015505 | 0.015918 | 0.016396 | 0.016612 | 0.016824 | 0.016982 | 0.017116 |  |  | 49302 | 0.015209 | 0.015307 | 0.015304 | 0.015499 | 0.015777 | 0.016107 | 0.016395 | 0.016613 | 0.016716 | 0.016805 | 0.016863 | 0.017023 | [10 empty] | Zs-Sandy Bay | Load transfer capacity (MVA)5
49303 | 7.1458 | 7.5152 | 7.6337 | 7.8316 | 8.0635 | 8.3255 | 8.5475 | 8.804 | 8.92 | 9.034 | 9.1186 | 9.1906 |  |  | 49303 | 11.159 | 11.231 | 11.2287 | 11.3717 | 11.5755 | 11.8178 | 12.029 | 12.1889 | 12.265 | 12.3299 | 12.3726 | 12.4897 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)1 | Kingston | 4.9
49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 49304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)2
49307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 49307 | 2.4782 | 2.4942 | 2.4937 | 2.5255 | 2.5707 | 2.6246 | 2.6715 | 2.707 | 2.7239 | 2.7383 | 2.7478 | 2.7738 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)3
49411 | 8.8687 | 9.3271 | 9.4741 | 9.7198 | 10.0076 | 10.3328 | 10.6083 | 10.9266 | 11.0706 | 11.2121 | 11.3172 | 11.4065 |  |  | 49411 | 11.5131 | 11.5873 | 11.585 | 11.7325 | 11.9428 | 12.1928 | 12.4107 | 12.5756 | 12.6541 | 12.7211 | 12.7652 | 12.886 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)4
49412 | 25.5515 | 26.8722 | 27.2958 | 28.0036 | 28.8327 | 29.7696 | 30.5635 | 31.4805 | 31.8954 | 32.303 | 32.6057 | 32.8629 |  |  | 49412 | 23.6462 | 23.7987 | 23.7939 | 24.0968 | 24.5287 | 25.0423 | 25.4898 | 25.8285 | 25.9897 | 26.1273 | 26.2178 | 26.466 | [10 empty] | Zs-Summerleas | Load transfer capacity (MVA)5
49621 | 0.076359 | 0.080306 | 0.081571 | 0.083687 | 0.086164 | 0.088964 | 0.091337 | 0.094077 | 0.095317 | 0.096535 | 0.09744 | 0.098208 |  |  | 49621 | 0.089145 | 0.08972 | 0.089701 | 0.090844 | 0.092472 | 0.094408 | 0.096095 | 0.097372 | 0.09798 | 0.098498 | 0.09884 | 0.099775 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)1
49801 | 4.8765 | 5.1286 | 5.2094 | 5.3445 | 5.5027 | 5.6815 | 5.833 | 6.0081 | 6.0872 | 6.165 | 6.2228 | 6.2719 |  |  | 49801 | 9.5588 | 9.6204 | 9.6185 | 9.741 | 9.9155 | 10.1231 | 10.304 | 10.441 | 10.5061 | 10.5618 | 10.5984 | 10.6987 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)2
51001 | 11.2892 | 11.8727 | 12.0599 | 12.3726 | 12.7389 | 13.1528 | 13.5036 | 13.9088 | 14.0921 | 14.2721 | 14.4059 | 14.5195 |  |  | 51001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)3
51002 | 11.2892 | 11.8727 | 12.0599 | 12.3726 | 12.7389 | 13.1528 | 13.5036 | 13.9088 | 14.0921 | 14.2721 | 14.4059 | 14.5195 |  |  | 51002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)4
51003 | 245.962 | 258.675 | 262.7527 | 269.5658 | 277.5468 | 286.5654 | 294.2077 | 303.0352 | 307.0294 | 310.9524 | 313.866 | 316.3426 |  |  | 51003 | 122.9684 | 123.7613 | 123.7363 | 125.3117 | 127.5578 | 130.2284 | 132.5555 | 134.3171 | 135.1555 | 135.8709 | 136.3417 | 137.6321 | [10 empty] | Zs-Trial Harbour | Load transfer capacity (MVA)5
51004 | 153.5842 | 161.5225 | 164.0687 | 168.3229 | 173.3064 | 178.9378 | 183.7099 | 189.2219 | 191.716 | 194.1656 | 195.985 | 197.5314 |  |  | 51004 | 94.817 | 95.4284 | 95.4091 | 96.6239 | 98.3557 | 100.4149 | 102.2093 | 103.5676 | 104.2141 | 104.7657 | 105.1288 | 106.1237 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)1
53001 | 91.7323 | 96.4737 | 97.9945 | 100.5354 | 103.512 | 106.8755 | 109.7257 | 113.0179 | 114.5076 | 115.9707 | 117.0574 | 117.981 |  |  | 53001 | 151.828 | 152.807 | 152.7761 | 154.7213 | 157.4945 | 160.7918 | 163.6651 | 165.8401 | 166.8753 | 167.7585 | 168.3399 | 169.9331 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)2
53002 | 9.5847 | 10.0801 | 10.239 | 10.5045 | 10.8155 | 11.167 | 11.4648 | 11.8088 | 11.9644 | 12.1173 | 12.2308 | 12.3273 |  |  | 53002 | 12.8527 | 12.9356 | 12.9329 | 13.0976 | 13.3324 | 13.6115 | 13.8547 | 14.0389 | 14.1265 | 14.2013 | 14.2505 | 14.3853 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)3
53003 | 107.0314 | 112.5635 | 114.3379 | 117.3026 | 120.7756 | 124.7001 | 128.0257 | 131.867 | 133.6051 | 135.3122 | 136.5801 | 137.6578 |  |  | 53003 | 142.7396 | 143.66 | 143.631 | 145.4597 | 148.0669 | 151.1668 | 153.8681 | 155.9129 | 156.8862 | 157.7165 | 158.2631 | 159.761 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)4
53004 | 36.198 | 38.069 | 38.6691 | 39.6718 | 40.8463 | 42.1736 | 43.2983 | 44.5974 | 45.1853 | 45.7626 | 46.1914 | 46.5559 |  |  | 53004 | 56.1727 | 56.5349 | 56.5235 | 57.2432 | 58.2692 | 59.4891 | 60.5522 | 61.3569 | 61.7399 | 62.0666 | 62.2817 | 62.8712 | [10 empty] | Zs-West Hobart | Load transfer capacity (MVA)5
53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 53005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 53006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 53007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53008 | 46.7633 | 49.1803 | 49.9556 | 51.2509 | 52.7683 | 54.4829 | 55.9359 | 57.6142 | 58.3736 | 59.1195 | 59.6734 | 60.1443 |  |  | 53008 | 69.5657 | 70.0143 | 70.0002 | 70.8914 | 72.1621 | 73.6728 | 74.9894 | 75.9859 | 76.4602 | 76.8649 | 77.1313 | 77.8613
53009 | 29.2071 | 30.7168 | 31.201 | 32.01 | 32.9577 | 34.0286 | 34.9361 | 35.9844 | 36.4587 | 36.9245 | 37.2705 | 37.5646 |  |  | 53009 | 52.6218 | 52.9611 | 52.9504 | 53.6246 | 54.5857 | 55.7286 | 56.7244 | 57.4782 | 57.837 | 58.1431 | 58.3446 | 58.8968
53010 | 43.4249 | 45.6694 | 46.3893 | 47.5922 | 49.0012 | 50.5935 | 51.9427 | 53.5012 | 54.2064 | 54.899 | 55.4134 | 55.8507 |  |  | 53010 | 51.9473 | 52.2823 | 52.2717 | 52.9373 | 53.8861 | 55.0143 | 55.9973 | 56.7415 | 57.0957 | 57.3979 | 57.5968 | 58.1419
54003 | 146.4575 | 154.0274 | 156.4554 | 160.5123 | 165.2645 | 170.6346 | 175.1852 | 180.4415 | 182.8199 | 185.1558 | 186.8907 | 188.3654 |  |  | 54003 | 146.3093 | 147.2527 | 147.2229 | 149.0974 | 151.7698 | 154.9473 | 157.7161 | 159.8121 | 160.8097 | 161.6608 | 162.221 | 163.7563
54004 | 4.6571 | 4.8978 | 4.975 | 5.104 | 5.2551 | 5.4259 | 5.5706 | 5.7377 | 5.8134 | 5.8877 | 5.9428 | 5.9897 |  |  | 54004 | 5.8274 | 5.865 | 5.8638 | 5.9385 | 6.0449 | 6.1715 | 6.2817 | 6.3652 | 6.405 | 6.4389 | 6.4612 | 6.5223
54005 | 65.5696 | 68.9587 | 70.0457 | 71.862 | 73.9896 | 76.3938 | 78.4311 | 80.7844 | 81.8492 | 82.895 | 83.6717 | 84.332 |  |  | 54005 | 79.7528 | 80.2671 | 80.2508 | 81.2726 | 82.7293 | 84.4614 | 85.9706 | 87.1131 | 87.6569 | 88.1209 | 88.4263 | 89.2631
54006 | 0.79372 | 0.83474 | 0.8479 | 0.86989 | 0.89564 | 0.92474 | 0.94941 | 0.97789 | 0.99078 | 1.0034 | 1.0128 | 1.0208 |  |  | 54006 | 44.9967 | 45.2869 | 45.2777 | 45.8542 | 46.6761 | 47.6533 | 48.5048 | 49.1494 | 49.4562 | 49.718 | 49.8903 | 50.3625
54007 | 44.5717 | 46.8755 | 47.6144 | 48.8491 | 50.2953 | 51.9296 | 53.3145 | 54.9142 | 55.638 | 56.3489 | 56.8769 | 57.3257 |  |  | 54007 | 93.3435 | 93.9454 | 93.9264 | 95.1223 | 96.8272 | 98.8544 | 100.6209 | 101.9581 | 102.5945 | 103.1375 | 103.4949 | 104.4745
55001 | 95.7784 | 100.7289 | 102.3167 | 104.9698 | 108.0776 | 111.5895 | 114.5654 | 118.0028 | 119.5582 | 121.0858 | 122.2204 | 123.1848 |  |  | 55001 | 48.2655 | 48.5767 | 48.5669 | 49.1853 | 50.0669 | 51.1151 | 52.0285 | 52.7199 | 53.049 | 53.3298 | 53.5146 | 54.021
55002 | 36.9578 | 38.868 | 39.4807 | 40.5044 | 41.7036 | 43.0587 | 44.2071 | 45.5335 | 46.1336 | 46.7231 | 47.1609 | 47.533 |  |  | 55002 | 28.3072 | 28.4898 | 28.484 | 28.8467 | 29.3637 | 29.9785 | 30.5142 | 30.9197 | 31.1127 | 31.2774 | 31.3858 | 31.6828
55003 | 28.802 | 30.2906 | 30.7681 | 31.5659 | 32.5005 | 33.5566 | 34.4515 | 35.4852 | 35.9529 | 36.4123 | 36.7535 | 37.0435 |  |  | 55003 | 16.4553 | 16.5614 | 16.5581 | 16.7689 | 17.0694 | 17.4268 | 17.7382 | 17.9739 | 18.0861 | 18.1819 | 18.2449 | 18.4176
56001 | 10.9863 | 11.5542 | 11.7363 | 12.0406 | 12.3971 | 12.8 | 13.1413 | 13.5356 | 13.714 | 13.8892 | 14.0194 | 14.13 |  |  | 56001 | 8.7278 | 8.784 | 8.7823 | 8.8941 | 9.0535 | 9.243 | 9.4082 | 9.5332 | 9.5927 | 9.6435 | 9.6769 | 9.7685
56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56003 | 34.8986 | 36.7024 | 37.281 | 38.2477 | 39.38 | 40.6597 | 41.744 | 42.9965 | 43.5632 | 44.1198 | 44.5332 | 44.8846 |  |  | 56003 | 46.207 | 46.5049 | 46.4955 | 47.0875 | 47.9315 | 48.935 | 49.8095 | 50.4714 | 50.7865 | 51.0553 | 51.2322 | 51.7171
56004 | 202.7049 | 213.1821 | 216.5427 | 222.1575 | 228.7349 | 236.1674 | 242.4657 | 249.7407 | 253.0324 | 256.2655 | 258.6667 | 260.7078 |  |  | 56004 | 142.6258 | 143.5455 | 143.5165 | 145.3438 | 147.9489 | 151.0464 | 153.7455 | 155.7887 | 156.7612 | 157.5909 | 158.137 | 159.6337
57003 | 18.3166 | 19.2634 | 19.567 | 20.0744 | 20.6687 | 21.3403 | 21.9094 | 22.5668 | 22.8643 | 23.1564 | 23.3734 | 23.5578 |  |  | 57003 | 35.5948 | 35.8243 | 35.817 | 36.2731 | 36.9232 | 37.6963 | 38.3699 | 38.8798 | 39.1225 | 39.3295 | 39.4658 | 39.8394
57004 | 102.6323 | 107.9371 | 109.6386 | 112.4814 | 115.8117 | 119.5749 | 122.7638 | 126.4472 | 128.1139 | 129.7508 | 130.9666 | 132 |  |  | 57004 | 161.9496 | 162.9939 | 162.9609 | 165.0358 | 167.9938 | 171.511 | 174.5758 | 176.8958 | 178.0001 | 178.9421 | 179.5623 | 181.2617
57005 | 28.6109 | 30.0897 | 30.564 | 31.3565 | 32.2849 | 33.334 | 34.2229 | 35.2498 | 35.7144 | 36.1707 | 36.5097 | 36.7977 |  |  | 57005 | 45.9634 | 46.2598 | 46.2504 | 46.8393 | 47.6789 | 48.6771 | 49.5469 | 50.2053 | 50.5187 | 50.7861 | 50.9621 | 51.4444
57006 | 101.612 | 106.864 | 108.5485 | 111.3631 | 114.6603 | 118.386 | 121.5432 | 125.19 | 126.8401 | 128.4608 | 129.6645 | 130.6876 |  |  | 57006 | 222.0546 | 223.4865 | 223.4413 | 226.2862 | 230.3421 | 235.1646 | 239.3669 | 242.5479 | 244.062 | 245.3537 | 246.204 | 248.5342
61021 | 77.5847 | 81.5948 | 82.881 | 85.0301 | 87.5476 | 90.3923 | 92.803 | 95.5875 | 96.8474 | 98.0848 | 99.0039 | 99.7851 |  |  | 61021 | 164.7031 | 165.7651 | 165.7316 | 167.8418 | 170.8501 | 174.4271 | 177.544 | 179.9034 | 181.0265 | 181.9846 | 182.6153 | 184.3436
61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61023 | 67.2378 | 70.7131 | 71.8278 | 73.6903 | 75.8721 | 78.3374 | 80.4266 | 82.8397 | 83.9316 | 85.004 | 85.8005 | 86.4775 |  |  | 61023 | 134.9448 | 135.815 | 135.7875 | 137.5164 | 139.9812 | 142.9119 | 145.4657 | 147.3988 | 148.3189 | 149.1039 | 149.6207 | 151.0367
61024 | 116.6441 | 122.6731 | 124.6069 | 127.8379 | 131.6228 | 135.8997 | 139.524 | 143.7103 | 145.6045 | 147.4649 | 148.8467 | 150.0212 |  |  | 61024 | 173.3389 | 174.4566 | 174.4213 | 176.6421 | 179.8082 | 183.5727 | 186.8531 | 189.3362 | 190.5181 | 191.5265 | 192.1902 | 194.0092
61025 | 73.4165 | 77.2111 | 78.4283 | 80.4619 | 82.8441 | 85.5361 | 87.8172 | 90.4521 | 91.6443 | 92.8152 | 93.6849 | 94.4242 |  |  | 61025 | 154.4457 | 155.4416 | 155.4101 | 157.3889 | 160.2099 | 163.564 | 166.4869 | 168.6993 | 169.7525 | 170.6509 | 171.2423 | 172.863
61026 | 99.804 | 104.9626 | 106.6172 | 109.3817 | 112.6202 | 116.2796 | 119.3806 | 122.9626 | 124.5833 | 126.1751 | 127.3574 | 128.3623 |  |  | 61026 | 107.8538 | 108.5493 | 108.5274 | 109.9092 | 111.8791 | 114.2215 | 116.2626 | 117.8076 | 118.543 | 119.1704 | 119.5834 | 120.7152
61027 | 92.5037 | 97.2849 | 98.8185 | 101.3808 | 104.3824 | 107.7742 | 110.6484 | 113.9683 | 115.4705 | 116.9459 | 118.0417 | 118.9731 |  |  | 61027 | 203.5776 | 204.8904 | 204.8489 | 207.4571 | 211.1755 | 215.5967 | 219.4494 | 222.3657 | 223.7538 | 224.938 | 225.7176 | 227.8538
61028 | 101.8239 | 107.0869 | 108.775 | 111.5955 | 114.8995 | 118.633 | 121.7968 | 125.4512 | 127.1048 | 128.7288 | 129.935 | 130.9603 |  |  | 61028 | 247.9779 | 249.5769 | 249.5264 | 252.7035 | 257.2329 | 262.6183 | 267.3112 | 270.8636 | 272.5544 | 273.9969 | 274.9465 | 277.5487
61029 | 49.3435 | 51.894 | 52.712 | 54.0788 | 55.6799 | 57.4892 | 59.0223 | 60.7933 | 61.5945 | 62.3816 | 62.9661 | 63.4629 |  |  | 61029 | 113.3237 | 114.0545 | 114.0314 | 115.4833 | 117.5532 | 120.0143 | 122.1589 | 123.7823 | 124.555 | 125.2142 | 125.6482 | 126.8373
61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 61030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61037 | 51.8625 | 54.5431 | 55.4029 | 56.8395 | 58.5224 | 60.424 | 62.0354 | 63.8967 | 64.7389 | 65.5661 | 66.1805 | 66.7027 |  |  | 61037 | 89.0883 | 89.6627 | 89.6446 | 90.786 | 92.4132 | 94.348 | 96.0339 | 97.3102 | 97.9176 | 98.4359 | 98.777 | 99.7119
61039 | 106.6754 | 112.1891 | 113.9576 | 116.9125 | 120.3739 | 124.2853 | 127.5998 | 131.4284 | 133.1607 | 134.8621 | 136.1258 | 137.1999 |  |  | 61039 | 143.698 | 144.6246 | 144.5953 | 146.4363 | 149.061 | 152.1818 | 154.9012 | 156.9598 | 157.9396 | 158.7755 | 159.3257 | 160.8336
61040 | 103.0312 | 108.3565 | 110.0646 | 112.9185 | 116.2617 | 120.0395 | 123.2408 | 126.9386 | 128.6117 | 130.255 | 131.4755 | 132.5129 |  |  | 61040 | 183.8212 | 185.0065 | 184.9691 | 187.3242 | 190.6818 | 194.6739 | 198.1526 | 200.7859 | 202.0393 | 203.1087 | 203.8125 | 205.7415
61041 | 67.9365 | 71.4479 | 72.5742 | 74.456 | 76.6604 | 79.1514 | 81.2623 | 83.7005 | 84.8037 | 85.8873 | 86.6921 | 87.3761 |  |  | 61041 | 143.8673 | 144.795 | 144.7657 | 146.6089 | 149.2367 | 152.3612 | 155.0838 | 157.1447 | 158.1257 | 158.9626 | 159.5135 | 161.0232
61043 | 132.6268 | 139.4819 | 141.6806 | 145.3544 | 149.6579 | 154.5208 | 158.6417 | 163.4016 | 165.5554 | 167.6707 | 169.2418 | 170.5772 |  |  | 61043 | 247.5499 | 249.1462 | 249.0958 | 252.2673 | 256.7889 | 262.1651 | 266.8499 | 270.3961 | 272.0841 | 273.5241 | 274.472 | 277.0697
62004 | 71.7159 | 75.4227 | 76.6116 | 78.5981 | 80.9252 | 83.5548 | 85.783 | 88.3569 | 89.5215 | 90.6653 | 91.5149 | 92.237 |  |  | 62004 | 186.5274 | 187.7302 | 187.6922 | 190.082 | 193.489 | 197.5399 | 201.0698 | 203.7419 | 205.0137 | 206.0988 | 206.813 | 208.7704
62005 | 65.1572 | 68.525 | 69.6052 | 71.41 | 73.5242 | 75.9133 | 77.9378 | 80.2763 | 81.3344 | 82.3736 | 83.1455 | 83.8015 |  |  | 62005 | 139.2146 | 140.1123 | 140.0839 | 141.8675 | 144.4103 | 147.4337 | 150.0683 | 152.0626 | 153.0119 | 153.8217 | 154.3548 | 155.8156
62006 | 45.6024 | 47.9595 | 48.7155 | 49.9787 | 51.4584 | 53.1305 | 54.5474 | 56.1841 | 56.9246 | 57.6519 | 58.1922 | 58.6513 |  |  | 62006 | 112.976 | 113.7045 | 113.6816 | 115.129 | 117.1925 | 119.6461 | 121.7841 | 123.4025 | 124.1729 | 124.8301 | 125.2627 | 126.4482
62008 | 40.0046 | 42.0724 | 42.7356 | 43.8437 | 45.1418 | 46.6086 | 47.8516 | 49.2873 | 49.937 | 50.575 | 51.0489 | 51.4517 |  |  | 62008 | 241.9296 | 243.4897 | 243.4404 | 246.54 | 250.9589 | 256.213 | 260.7914 | 264.2572 | 265.9068 | 267.3141 | 268.2405 | 270.7792
62009 | 74.0513 | 77.8788 | 79.1065 | 81.1577 | 83.5605 | 86.2757 | 88.5766 | 91.2342 | 92.4368 | 93.6179 | 94.4951 | 95.2407 |  |  | 62009 | 126.6865 | 127.5034 | 127.4776 | 129.1007 | 131.4147 | 134.166 | 136.5635 | 138.3783 | 139.2421 | 139.9791 | 140.4642 | 141.7936
62010 | 57.9101 | 60.9033 | 61.8634 | 63.4675 | 65.3465 | 67.4699 | 69.2692 | 71.3476 | 72.288 | 73.2117 | 73.8977 | 74.4808 |  |  | 62010 | 117.6461 | 118.4048 | 118.3808 | 119.8881 | 122.0369 | 124.5919 | 126.8183 | 128.5036 | 129.3058 | 129.9902 | 130.4407 | 131.6752
62013 | 133.037 | 139.9132 | 142.1188 | 145.8038 | 150.1207 | 154.9987 | 159.1323 | 163.9069 | 166.0673 | 168.1892 | 169.7652 | 171.1047 |  |  | 62013 | 174.727 | 175.8537 | 175.8182 | 178.0567 | 181.2482 | 185.0428 | 188.3495 | 190.8525 | 192.0439 | 193.0603 | 193.7293 | 195.5629
65060 | 27.0639 | 28.4628 | 28.9114 | 29.6611 | 30.5393 | 31.5316 | 32.3725 | 33.3438 | 33.7833 | 34.215 | 34.5356 | 34.8081 |  |  | 65060 | 42.2075 | 42.4797 | 42.4711 | 43.0119 | 43.7828 | 44.6994 | 45.4982 | 46.1028 | 46.3906 | 46.6362 | 46.7978 | 47.2407
65061 | 64.1256 | 67.4401 | 68.5032 | 70.2794 | 72.3602 | 74.7115 | 76.7039 | 79.0054 | 80.0467 | 81.0695 | 81.8291 | 82.4748 |  |  | 65061 | 126.5403 | 127.3563 | 127.3305 | 128.9517 | 131.263 | 134.0112 | 136.4059 | 138.2186 | 139.0814 | 139.8175 | 140.3021 | 141.63
65062 | 74.8979 | 78.7691 | 80.0108 | 82.0855 | 84.5158 | 87.262 | 89.5892 | 92.2772 | 93.4935 | 94.6881 | 95.5753 | 96.3295 |  |  | 65062 | 154.9499 | 155.9491 | 155.9175 | 157.9027 | 160.7329 | 164.098 | 167.0304 | 169.2501 | 170.3067 | 171.208 | 171.8014 | 173.4273
65063 | 24.581 | 25.8515 | 26.259 | 26.9399 | 27.7375 | 28.6388 | 29.4026 | 30.2848 | 30.6839 | 31.076 | 31.3672 | 31.6147 |  |  | 65063 | 56.0412 | 56.4026 | 56.3912 | 57.1092 | 58.1328 | 59.3499 | 60.4104 | 61.2132 | 61.5954 | 61.9213 | 62.1359 | 62.724
65064 | 42.2914 | 44.4773 | 45.1785 | 46.3499 | 47.7222 | 49.2729 | 50.5869 | 52.1047 | 52.7915 | 53.466 | 53.967 | 54.3929 |  |  | 65064 | 98.7814 | 99.4184 | 99.3983 | 100.6638 | 102.4681 | 104.6134 | 106.4828 | 107.8979 | 108.5714 | 109.1461 | 109.5243 | 110.5609
65065 | 65.6334 | 69.0258 | 70.1139 | 71.9319 | 74.0616 | 76.4681 | 78.5074 | 80.863 | 81.9288 | 82.9756 | 83.7531 | 84.414 |  |  | 65065 | 152.1583 | 153.1394 | 153.1085 | 155.0579 | 157.8371 | 161.1416 | 164.0211 | 166.2008 | 167.2383 | 168.1235 | 168.7061 | 170.3028
65066 | 95.097 | 100.0123 | 101.5889 | 104.223 | 107.3088 | 110.7957 | 113.7504 | 117.1634 | 118.7077 | 120.2245 | 121.351 | 122.3085 |  |  | 65066 | 112.1587 | 112.8819 | 112.8591 | 114.296 | 116.3446 | 118.7804 | 120.903 | 122.5097 | 123.2745 | 123.9269 | 124.3564 | 125.5333
65067 | 43.9403 | 46.2115 | 46.9399 | 48.1571 | 49.5828 | 51.194 | 52.5593 | 54.1363 | 54.8498 | 55.5506 | 56.0712 | 56.5136 |  |  | 65067 | 68.2223 | 68.6622 | 68.6483 | 69.5223 | 70.7684 | 72.2501 | 73.5411 | 74.5184 | 74.9836 | 75.3805 | 75.6417 | 76.3576
66101 | 29.2753 | 30.7885 | 31.2738 | 32.0847 | 33.0347 | 34.1081 | 35.0177 | 36.0684 | 36.5438 | 37.0107 | 37.3575 | 37.6523 |  |  | 66101 | 57.172 | 57.5407 | 57.529 | 58.2615 | 59.3058 | 60.5474 | 61.6294 | 62.4484 | 62.8382 | 63.1708 | 63.3897 | 63.9896
66102 | 67.0886 | 70.5562 | 71.6684 | 73.5268 | 75.7037 | 78.1636 | 80.2481 | 82.6559 | 83.7453 | 84.8154 | 85.6101 | 86.2856 |  |  | 66102 | 160.4443 | 161.4789 | 161.4463 | 163.5018 | 166.4324 | 169.9169 | 172.9532 | 175.2516 | 176.3456 | 177.279 | 177.8933 | 179.577
66103 | 66.273 | 69.6985 | 70.7972 | 72.6329 | 74.7833 | 77.2134 | 79.2725 | 81.651 | 82.7273 | 83.7843 | 84.5694 | 85.2367 |  |  | 66103 | 176.0305 | 177.1656 | 177.1297 | 179.385 | 182.6003 | 186.4232 | 189.7545 | 192.2762 | 193.4765 | 194.5005 | 195.1745 | 197.0217
66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66105 | 48.9091 | 51.4371 | 52.2479 | 53.6027 | 55.1897 | 56.9831 | 58.5027 | 60.258 | 61.0523 | 61.8324 | 62.4117 | 62.9042 |  |  | 66105 | 108.9455 | 109.648 | 109.6259 | 111.0216 | 113.0116 | 115.3776 | 117.4393 | 119 | 119.7429 | 120.3766 | 120.7938 | 121.937
66106 | 74.5928 | 78.4483 | 79.6849 | 81.7511 | 84.1715 | 86.9066 | 89.2242 | 91.9013 | 93.1127 | 94.3024 | 95.186 | 95.9371 |  |  | 66106 | 156.7789 | 157.7899 | 157.758 | 159.7666 | 162.6302 | 166.035 | 169.002 | 171.2479 | 172.3169 | 173.2289 | 173.8293 | 175.4745
66107 | 39.9121 | 41.975 | 42.6367 | 43.7423 | 45.0373 | 46.5008 | 47.7409 | 49.1733 | 49.8215 | 50.458 | 50.9308 | 51.3327 |  |  | 66107 | 103.524 | 104.1915 | 104.1704 | 105.4968 | 107.3877 | 109.6359 | 111.5951 | 113.0781 | 113.784 | 114.3862 | 114.7826 | 115.869
66108 | 1.2419 | 1.3061 | 1.3267 | 1.3611 | 1.4014 | 1.4469 | 1.4855 | 1.5301 | 1.5502 | 1.5701 | 1.5848 | 1.5973 |  |  | 66108 | 1.3711 | 1.38 | 1.3797 | 1.3973 | 1.4223 | 1.4521 | 1.478 | 1.4977 | 1.507 | 1.515 | 1.5203 | 1.5347
66109 | 26.9355 | 28.3277 | 28.7743 | 29.5204 | 30.3944 | 31.382 | 32.219 | 33.1857 | 33.6231 | 34.0527 | 34.3718 | 34.643 |  |  | 66109 | 58.3488 | 58.725 | 58.7131 | 59.4607 | 60.5264 | 61.7936 | 62.8979 | 63.7337 | 64.1316 | 64.471 | 64.6944 | 65.3067
66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67081 | 68.7366 | 72.2894 | 73.429 | 75.3329 | 77.5633 | 80.0837 | 82.2194 | 84.6863 | 85.8025 | 86.8988 | 87.7131 | 88.4052 |  |  | 67081 | 125.9139 | 126.7258 | 126.7002 | 128.3134 | 130.6132 | 133.3478 | 135.7306 | 137.5344 | 138.393 | 139.1254 | 139.6076 | 140.9289
67082 | 185.3443 | 194.9242 | 197.9969 | 203.1309 | 209.145 | 215.941 | 221.6998 | 228.3517 | 231.3616 | 234.3177 | 236.5133 | 238.3795 |  |  | 67082 | 130.5967 | 131.4388 | 131.4123 | 133.0854 | 135.4708 | 138.3071 | 140.7786 | 142.6494 | 143.5399 | 144.2996 | 144.7997 | 146.1701
67083 | 102.1326 | 107.4116 | 109.1048 | 111.9338 | 115.2478 | 118.9927 | 122.166 | 125.8315 | 127.4901 | 129.1191 | 130.3289 | 131.3573 |  |  | 67083 | 118.7513 | 119.517 | 119.4928 | 121.0142 | 123.1833 | 125.7623 | 128.0096 | 129.7107 | 130.5204 | 131.2112 | 131.666 | 132.9121
67084 | 141.5752 | 148.8927 | 151.2398 | 155.1614 | 159.7553 | 164.9464 | 169.3452 | 174.4263 | 176.7254 | 178.9834 | 180.6606 | 182.0861 |  |  | 67084 | 141.8243 | 142.7388 | 142.71 | 144.527 | 147.1175 | 150.1975 | 152.8815 | 154.9132 | 155.8802 | 156.7052 | 157.2483 | 158.7366
67085 | 61.0409 | 64.1959 | 65.2079 | 66.8987 | 68.8794 | 71.1175 | 73.0141 | 75.2049 | 76.1961 | 77.1697 | 77.8928 | 78.5074 |  |  | 67085 | 111.7148 | 112.4351 | 112.4124 | 113.8437 | 115.8842 | 118.3103 | 120.4245 | 122.0248 | 122.7866 | 123.4364 | 123.8642 | 125.0365
67086 | 81.4059 | 85.6135 | 86.9631 | 89.218 | 91.8595 | 94.8444 | 97.3738 | 100.2954 | 101.6174 | 102.9157 | 103.8801 | 104.6998 |  |  | 67086 | 176.3224 | 177.4594 | 177.4235 | 179.6825 | 182.9031 | 186.7324 | 190.0692 | 192.5951 | 193.7974 | 194.823 | 195.4982 | 197.3485
67087 | 83.5547 | 87.8733 | 89.2586 | 91.573 | 94.2842 | 97.3479 | 99.944 | 102.9427 | 104.2996 | 105.6322 | 106.622 | 107.4633 |  |  | 67087 | 151.1564 | 152.1311 | 152.1003 | 154.0369 | 156.7979 | 160.0806 | 162.9412 | 165.1065 | 166.1372 | 167.0165 | 167.5953 | 169.1815
67088 | 44.8626 | 47.1814 | 47.9252 | 49.1678 | 50.6236 | 52.2685 | 53.6624 | 55.2726 | 56.0011 | 56.7166 | 57.2481 | 57.6998 |  |  | 67088 | 90.0355 | 90.6161 | 90.5978 | 91.7513 | 93.3958 | 95.3512 | 97.055 | 98.3448 | 98.9587 | 99.4825 | 99.8273 | 100.7721
67089 | 53.0605 | 55.803 | 56.6827 | 58.1524 | 59.8741 | 61.8197 | 63.4683 | 65.3727 | 66.2343 | 67.0806 | 67.7092 | 68.2434 |  |  | 67089 | 105.3305 | 106.0097 | 105.9883 | 107.3377 | 109.2616 | 111.5492 | 113.5425 | 115.0514 | 115.7696 | 116.3823 | 116.7856 | 117.8909
67090 | 178.7527 | 187.9919 | 190.9554 | 195.9067 | 201.707 | 208.2612 | 213.8152 | 220.2306 | 223.1334 | 225.9844 | 228.102 | 229.9018 |  |  | 67090 | 251.4886 | 253.1103 | 253.0591 | 256.2811 | 260.8746 | 266.3364 | 271.0957 | 274.6983 | 276.4131 | 277.8761 | 278.8391 | 281.4781
67091 | 52.2038 | 54.902 | 55.7675 | 57.2135 | 58.9074 | 60.8215 | 62.4436 | 64.3171 | 65.1649 | 65.9975 | 66.6159 | 67.1416 |  |  | 67091 | 132.0003 | 132.8514 | 132.8246 | 134.5157 | 136.9268 | 139.7935 | 142.2915 | 144.1825 | 145.0825 | 145.8504 | 146.3559 | 147.741
80001 | 55.6534 | 58.5299 | 59.4526 | 60.9941 | 62.8 | 64.8406 | 66.5698 | 68.5672 | 69.471 | 70.3586 | 71.0179 | 71.5782 |  |  | 80001 | 83.1996 | 83.736 | 83.7191 | 84.785 | 86.3047 | 88.1116 | 89.6861 | 90.878 | 91.4453 | 91.9293 | 92.2479 | 93.1209
80002 | 126.5233 | 133.0629 | 135.1604 | 138.6651 | 142.7705 | 147.4097 | 151.3409 | 155.8818 | 157.9364 | 159.9544 | 161.4532 | 162.7272 |  |  | 80002 | 124.2372 | 125.0383 | 125.013 | 126.6047 | 128.874 | 131.5721 | 133.9232 | 135.703 | 136.5501 | 137.2728 | 137.7485 | 139.0522
80003 | 149.2169 | 156.9295 | 159.4033 | 163.5365 | 168.3784 | 173.8497 | 178.486 | 183.8413 | 186.2645 | 188.6444 | 190.412 | 191.9145 |  |  | 80003 | 185.0742 | 186.2676 | 186.2299 | 188.601 | 191.9815 | 196.0008 | 199.5033 | 202.1545 | 203.4165 | 204.4931 | 205.2018 | 207.1439
80004 | 42.6497 | 44.8541 | 45.5612 | 46.7426 | 48.1265 | 49.6903 | 51.0155 | 52.5462 | 53.2388 | 53.919 | 54.4242 | 54.8537 |  |  | 80004 | 102.487 | 103.1478 | 103.127 | 104.44 | 106.312 | 108.5377 | 110.4773 | 111.9454 | 112.6442 | 113.2404 | 113.6329 | 114.7083
80005 | 57.6495 | 60.6293 | 61.585 | 63.1819 | 65.0525 | 67.1663 | 68.9575 | 71.0266 | 71.9627 | 72.8822 | 73.5651 | 74.1456 |  |  | 80005 | 151.6009 | 152.5785 | 152.5476 | 154.4899 | 157.259 | 160.5514 | 163.4204 | 165.5921 | 166.6258 | 167.5077 | 168.0882 | 169.679
80006 | 105.5634 | 111.0197 | 112.7698 | 115.6938 | 119.1192 | 122.9898 | 126.2698 | 130.0584 | 131.7727 | 133.4564 | 134.7069 | 135.7698 |  |  | 80006 | 105.7283 | 106.4101 | 106.3886 | 107.7431 | 109.6743 | 111.9704 | 113.9713 | 115.4859 | 116.2068 | 116.8219 | 117.2267 | 118.3362
80007 | 73.8071 | 77.622 | 78.8456 | 80.89 | 83.285 | 85.9912 | 88.2845 | 90.9334 | 92.132 | 93.3092 | 94.1835 | 94.9266 |  |  | 80007 | 160.291 | 161.3246 | 161.292 | 163.3456 | 166.2734 | 169.7545 | 172.788 | 175.0842 | 176.1771 | 177.1096 | 177.7234 | 179.4054
80008 | 66.0278 | 69.4405 | 70.5352 | 72.3641 | 74.5066 | 76.9276 | 78.9792 | 81.3489 | 82.4211 | 83.4742 | 84.2564 | 84.9212 |  |  | 80008 | 155.3915 | 156.3935 | 156.3619 | 158.3527 | 161.191 | 164.5657 | 167.5064 | 169.7325 | 170.792 | 171.6959 | 172.291 | 173.9216
80009 | 71.292 | 74.9768 | 76.1587 | 78.1335 | 80.4468 | 83.0608 | 85.276 | 87.8346 | 88.9923 | 90.1294 | 90.9739 | 91.6918 |  |  | 80009 | 161.127 | 162.166 | 162.1332 | 164.1976 | 167.1406 | 170.6399 | 173.6891 | 175.9973 | 177.096 | 178.0333 | 178.6503 | 180.3411
80010 | 68.9707 | 72.5356 | 73.679 | 75.5895 | 77.8275 | 80.3564 | 82.4994 | 84.9747 | 86.0947 | 87.1948 | 88.0118 | 88.7063 |  |  | 80010 | 198.2147 | 199.4928 | 199.4525 | 201.992 | 205.6124 | 209.9172 | 213.6683 | 216.5078 | 217.8593 | 219.0124 | 219.7714 | 221.8514
80011 | 98.9533 | 104.0678 | 105.7083 | 108.4493 | 111.6602 | 115.2884 | 118.363 | 121.9144 | 123.5213 | 125.0996 | 126.2718 | 127.2681 |  |  | 80011 | 158.456 | 159.4778 | 159.4455 | 161.4756 | 164.3699 | 167.8111 | 170.8099 | 173.0798 | 174.1602 | 175.082 | 175.6888 | 177.3515
81001 | 27.3077 | 28.7191 | 29.1718 | 29.9283 | 30.8143 | 31.8156 | 32.6641 | 33.6442 | 34.0876 | 34.5232 | 34.8466 | 35.1216 |  |  | 81001 | 48.6829 | 48.9968 | 48.9869 | 49.6106 | 50.4998 | 51.5571 | 52.4784 | 53.1758 | 53.5078 | 53.791 | 53.9774 | 54.4882
81002 | 47.2751 | 49.7186 | 50.5024 | 51.8119 | 53.3459 | 55.0793 | 56.5482 | 58.2449 | 59.0126 | 59.7666 | 60.3266 | 60.8026 |  |  | 81002 | 63.3213 | 63.7296 | 63.7167 | 64.528 | 65.6846 | 67.0598 | 68.2581 | 69.1652 | 69.5969 | 69.9653 | 70.2078 | 70.8722
81003 | 94.6792 | 99.5728 | 101.1425 | 103.765 | 106.8372 | 110.3088 | 113.2506 | 116.6486 | 118.1861 | 119.6962 | 120.8177 | 121.771 |  |  | 81003 | 184.7729 | 185.9643 | 185.9267 | 188.294 | 191.6689 | 195.6818 | 199.1785 | 201.8254 | 203.0853 | 204.1602 | 204.8677 | 206.8066
82001 | 83.7917 | 88.1226 | 89.5118 | 91.8328 | 94.5516 | 97.624 | 100.2275 | 103.2348 | 104.5955 | 105.9319 | 106.9245 | 107.7682 |  |  | 82001 | 72.0984 | 72.5633 | 72.5486 | 73.4723 | 74.7892 | 76.355 | 77.7194 | 78.7523 | 79.2439 | 79.6633 | 79.9394 | 80.6959
82002 | 67.6282 | 71.1237 | 72.2449 | 74.1181 | 76.3126 | 78.7923 | 80.8935 | 83.3207 | 84.4189 | 85.4975 | 86.2987 | 86.9796 |  |  | 82002 | 226.7505 | 228.2127 | 228.1665 | 231.0716 | 235.2133 | 240.1377 | 244.4289 | 247.6772 | 249.2233 | 250.5423 | 251.4106 | 253.79
82003 | 84.1736 | 88.5242 | 89.9197 | 92.2513 | 94.9826 | 98.0689 | 100.6843 | 103.7053 | 105.0722 | 106.4147 | 107.4118 | 108.2594 |  |  | 82003 | 116.2159 | 116.9652 | 116.9416 | 118.4305 | 120.5533 | 123.0772 | 125.2765 | 126.9413 | 127.7338 | 128.4098 | 128.8548 | 130.0743
82004 | 51.5741 | 54.2398 | 55.0948 | 56.5234 | 58.1969 | 60.088 | 61.6904 | 63.5414 | 64.3789 | 65.2015 | 65.8124 | 66.3317 |  |  | 82004 | 43.9727 | 44.2562 | 44.2473 | 44.8107 | 45.6138 | 46.5688 | 47.401 | 48.0309 | 48.3307 | 48.5865 | 48.7549 | 49.2163
82005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 82005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82006 | 73.5525 | 77.3542 | 78.5736 | 80.611 | 82.9976 | 85.6946 | 87.9799 | 90.6197 | 91.8141 | 92.9872 | 93.8585 | 94.5991 |  |  | 82006 | 185.6625 | 186.8597 | 186.8219 | 189.2006 | 192.5918 | 196.6239 | 200.1375 | 202.7972 | 204.0631 | 205.1432 | 205.8541 | 207.8024
82007 | 39.1009 | 41.1219 | 41.7702 | 42.8533 | 44.122 | 45.5557 | 46.7706 | 48.1739 | 48.8089 | 49.4325 | 49.8957 | 50.2894 |  |  | 82007 | 40.1992 | 40.4584 | 40.4503 | 40.9653 | 41.6995 | 42.5726 | 43.3333 | 43.9092 | 44.1833 | 44.4171 | 44.5711 | 44.9929
82008 | 37.5177 | 39.4568 | 40.0788 | 41.118 | 42.3354 | 43.7111 | 44.8768 | 46.2233 | 46.8325 | 47.4309 | 47.8754 | 48.2531 |  |  | 82008 | 26.5165 | 26.6875 | 26.6821 | 27.0218 | 27.5061 | 28.082 | 28.5838 | 28.9637 | 29.1445 | 29.2987 | 29.4003 | 29.6785
84121 | 104.4823 | 109.8826 | 111.6148 | 114.5089 | 117.8992 | 121.7302 | 124.9766 | 128.7264 | 130.4231 | 132.0895 | 133.3272 | 134.3793 |  |  | 84121 | 49.1438 | 49.4607 | 49.4507 | 50.0804 | 50.978 | 52.0453 | 52.9753 | 53.6793 | 54.0144 | 54.3003 | 54.4884 | 55.0041
84122 | 175.4869 | 184.5573 | 187.4666 | 192.3275 | 198.0218 | 204.4563 | 209.9089 | 216.207 | 219.0568 | 221.8557 | 223.9345 | 225.7015 |  |  | 84122 | 9.755 | 9.8179 | 9.816 | 9.9409 | 10.1191 | 10.331 | 10.5156 | 10.6553 | 10.7218 | 10.7786 | 10.8159 | 10.9183
85001 | 121.0101 | 127.2648 | 129.2709 | 132.6229 | 136.5494 | 140.9865 | 144.7464 | 149.0894 | 151.0545 | 152.9845 | 154.418 | 155.6365 |  |  | 85001 | 183.5816 | 184.7654 | 184.728 | 187.08 | 190.4332 | 194.4201 | 197.8943 | 200.5242 | 201.776 | 202.8439 | 203.5469 | 205.4733
85002 | 168.0463 | 176.7321 | 179.5181 | 184.1729 | 189.6257 | 195.7874 | 201.0088 | 207.0399 | 209.7688 | 212.4491 | 214.4398 | 216.1318 |  |  | 85002 | 166.6459 | 167.7205 | 167.6866 | 169.8216 | 172.8654 | 176.4846 | 179.6383 | 182.0255 | 183.1618 | 184.1312 | 184.7694 | 186.5181
85003 | 32.793 | 34.4879 | 35.0316 | 35.9399 | 37.004 | 38.2064 | 39.2253 | 40.4023 | 40.9348 | 41.4578 | 41.8463 | 42.1765 |  |  | 85003 | 95.9252 | 96.5437 | 96.5242 | 97.7532 | 99.5053 | 101.5886 | 103.4039 | 104.7781 | 105.4321 | 105.9901 | 106.3575 | 107.3641
85004 | 31.2263 | 32.8403 | 33.358 | 34.2229 | 35.2361 | 36.3811 | 37.3513 | 38.472 | 38.9791 | 39.4772 | 39.8471 | 40.1615 |  |  | 85004 | 61.7053 | 62.1032 | 62.0906 | 62.8811 | 64.0082 | 65.3483 | 66.5161 | 67.4 | 67.8207 | 68.1797 | 68.416 | 69.0635
85005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85005 | 277.6444 | 279.4347 | 279.3782 | 282.9353 | 288.0066 | 294.0363 | 299.2906 | 303.268 | 305.1611 | 306.7762 | 307.8394 | 310.7529
85006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85006 | 192.5578 | 193.7995 | 193.7603 | 196.2273 | 199.7444 | 203.9263 | 207.5704 | 210.3289 | 211.6418 | 212.762 | 213.4993 | 215.5199
85007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85007 | 345.3587 | 347.5857 | 347.5154 | 351.94 | 358.2481 | 365.7485 | 372.2842 | 377.2316 | 379.5865 | 381.5955 | 382.9179 | 386.542
85008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85008 | 186.5192 | 187.722 | 187.684 | 190.0736 | 193.4805 | 197.5312 | 201.061 | 203.733 | 205.0048 | 206.0898 | 206.804 | 208.7612
90019 | 35.1989 | 37.0183 | 37.6018 | 38.5768 | 39.7189 | 41.0096 | 42.1032 | 43.3665 | 43.9381 | 44.4995 | 44.9165 | 45.2709 |  |  | 90019 | 36.0106 | 36.2428 | 36.2355 | 36.6969 | 37.3546 | 38.1367 | 38.8182 | 39.334 | 39.5796 | 39.789 | 39.9269 | 40.3048
90020 | 34.6767 | 36.4691 | 37.044 | 38.0045 | 39.1297 | 40.4012 | 41.4786 | 42.7232 | 43.2863 | 43.8394 | 44.2501 | 44.5993 |  |  | 90020 | 46.7082 | 47.0094 | 46.9999 | 47.5983 | 48.4514 | 49.4658 | 50.3498 | 51.0189 | 51.3374 | 51.6091 | 51.7879 | 52.2781
90021 | 27.376 | 28.791 | 29.2448 | 30.0031 | 30.8914 | 31.8952 | 32.7458 | 33.7283 | 34.1729 | 34.6095 | 34.9338 | 35.2094 |  |  | 90021 | 40.6287 | 40.8907 | 40.8824 | 41.4029 | 42.145 | 43.0274 | 43.7963 | 44.3783 | 44.6553 | 44.8917 | 45.0472 | 45.4736
90023 | 71.3049 | 74.9904 | 76.1726 | 78.1477 | 80.4614 | 83.0759 | 85.2914 | 87.8505 | 89.0085 | 90.1457 | 90.9904 | 91.7084 |  |  | 90023 | 107.2401 | 107.9316 | 107.9098 | 109.2837 | 111.2425 | 113.5715 | 115.6009 | 117.1372 | 117.8684 | 118.4922 | 118.9029 | 120.0282
90024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 90024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91001 | 124.8322 | 131.2844 | 133.354 | 136.8118 | 140.8623 | 145.4395 | 149.3182 | 153.7984 | 155.8255 | 157.8166 | 159.2953 | 160.5523 |  |  | 91001 | 163.633 | 164.6882 | 164.6549 | 166.7513 | 169.7401 | 173.2938 | 176.3905 | 178.7346 | 179.8504 | 180.8022 | 181.4288 | 183.1459
91002 | 71.3442 | 75.0318 | 76.2146 | 78.1908 | 80.5058 | 83.1217 | 85.3385 | 87.899 | 89.0576 | 90.1955 | 91.0406 | 91.759 |  |  | 91002 | 49.5111 | 49.8303 | 49.8202 | 50.4546 | 51.3589 | 52.4342 | 53.3711 | 54.0804 | 54.418 | 54.706 | 54.8956 | 55.4151
91003 | 122.9881 | 129.345 | 131.384 | 134.7907 | 138.7815 | 143.291 | 147.1124 | 151.5264 | 153.5236 | 155.4852 | 156.9421 | 158.1805 |  |  | 91003 | 179.048 | 180.2026 | 180.1661 | 182.46 | 185.7304 | 189.6189 | 193.0073 | 195.5722 | 196.7931 | 197.8346 | 198.5202 | 200.3991
91004 | 102.7793 | 108.0916 | 109.7955 | 112.6425 | 115.9775 | 119.746 | 122.9395 | 126.6282 | 128.2973 | 129.9365 | 131.1541 | 132.1889 |  |  | 91004 | 128.3091 | 129.1364 | 129.1103 | 130.7542 | 133.0978 | 135.8844 | 138.3126 | 140.1506 | 141.0255 | 141.7719 | 142.2632 | 143.6096
91005 | 63.0409 | 66.2993 | 67.3444 | 69.0906 | 71.1361 | 73.4476 | 75.4064 | 77.6689 | 78.6926 | 79.6981 | 80.4449 | 81.0796 |  |  | 91005 | 130.7204 | 131.5633 | 131.5367 | 133.2115 | 135.5991 | 138.4381 | 140.9119 | 142.7845 | 143.6758 | 144.4363 | 144.9368 | 146.3085
91006 | 121.6621 | 127.9505 | 129.9674 | 133.3374 | 137.2851 | 141.7461 | 145.5263 | 149.8927 | 151.8683 | 153.8088 | 155.25 | 156.475 |  |  | 91006 | 259.1662 | 260.8373 | 260.7846 | 264.105 | 268.8387 | 274.4672 | 279.3718 | 283.0844 | 284.8516 | 286.3592 | 287.3516 | 290.0712
91007 | 81.8289 | 86.0584 | 87.415 | 89.6816 | 92.3368 | 95.3372 | 97.8797 | 100.8165 | 102.1454 | 103.4505 | 104.4199 | 105.2438 |  |  | 91007 | 174.9971 | 176.1255 | 176.0899 | 178.3319 | 181.5283 | 185.3288 | 188.6406 | 191.1475 | 192.3407 | 193.3587 | 194.0288 | 195.8651
91008 | 68.8823 | 72.4426 | 73.5846 | 75.4926 | 77.7277 | 80.2534 | 82.3936 | 84.8658 | 85.9844 | 87.083 | 87.899 | 88.5926 |  |  | 91008 | 157.2194 | 158.2332 | 158.2012 | 160.2155 | 163.0872 | 166.5016 | 169.4769 | 171.7291 | 172.8011 | 173.7157 | 174.3177 | 175.9675
91009 | 78.2928 | 82.3396 | 83.6375 | 85.8062 | 88.3467 | 91.2174 | 93.65 | 96.46 | 97.7314 | 98.9801 | 99.9076 | 100.6959 |  |  | 91009 | 164.0962 | 165.1543 | 165.1209 | 167.2232 | 170.2205 | 173.7843 | 176.8897 | 179.2405 | 180.3594 | 181.3139 | 181.9423 | 183.6643
91010 | 74.4226 | 78.2692 | 79.5031 | 81.5645 | 83.9794 | 86.7082 | 89.0206 | 91.6916 | 92.9002 | 94.0872 | 94.9688 | 95.7182 |  |  | 91010 | 179.1394 | 180.2946 | 180.2581 | 182.5532 | 185.8252 | 189.7157 | 193.1059 | 195.6721 | 196.8936 | 197.9356 | 198.6216 | 200.5014
91011 | 84.5095 | 88.8775 | 90.2786 | 92.6195 | 95.3616 | 98.4603 | 101.0861 | 104.1191 | 105.4915 | 106.8394 | 107.8405 | 108.6914 |  |  | 91011 | 100.3084 | 100.9552 | 100.9348 | 102.2199 | 104.0521 | 106.2305 | 108.1288 | 109.5658 | 110.2498 | 110.8333 | 111.2174 | 112.27
91012 | 88.5541 | 93.1312 | 94.5993 | 97.0522 | 99.9257 | 103.1726 | 105.9241 | 109.1023 | 110.5403 | 111.9527 | 113.0017 | 113.8934 |  |  | 91012 | 62.6708 | 63.0749 | 63.0621 | 63.8651 | 65.0098 | 66.3708 | 67.5568 | 68.4546 | 68.8819 | 69.2465 | 69.4865 | 70.1441
93001 | 121.6033 | 127.8886 | 129.9046 | 133.273 | 137.2188 | 141.6776 | 145.4559 | 149.8202 | 151.7949 | 153.7344 | 155.175 | 156.3994 |  |  | 93001 | 113.3972 | 114.1284 | 114.1054 | 115.5582 | 117.6294 | 120.0921 | 122.2381 | 123.8626 | 124.6358 | 125.2954 | 125.7297 | 126.9196
93002 | 166.7711 | 175.391 | 178.1558 | 182.7753 | 188.1867 | 194.3016 | 199.4834 | 205.4687 | 208.1769 | 210.8369 | 212.8124 | 214.4916 |  |  | 93002 | 122.9452 | 123.738 | 123.713 | 125.2882 | 127.5338 | 130.2039 | 132.5305 | 134.2918 | 135.1301 | 135.8453 | 136.3161 | 137.6062
93003 | 111.5598 | 117.326 | 119.1755 | 122.2657 | 125.8856 | 129.9761 | 133.4424 | 137.4462 | 139.2579 | 141.0372 | 142.3587 | 143.482 |  |  | 93003 | 112.2118 | 112.9354 | 112.9125 | 114.3502 | 116.3997 | 118.8367 | 120.9603 | 122.5677 | 123.3329 | 123.9856 | 124.4153 | 125.5928
93004 | 93.8952 | 98.7483 | 100.3049 | 102.9058 | 105.9525 | 109.3954 | 112.3128 | 115.6826 | 117.2074 | 118.705 | 119.8173 | 120.7627 |  |  | 93004 | 114.9188 | 115.6598 | 115.6365 | 117.1088 | 119.2078 | 121.7036 | 123.8784 | 125.5246 | 126.3082 | 126.9767 | 127.4167 | 128.6226
93005 | 80.7522 | 84.9261 | 86.2648 | 88.5016 | 91.1219 | 94.0828 | 96.5919 | 99.49 | 100.8014 | 102.0894 | 103.0459 | 103.859 |  |  | 93005 | 120.65 | 121.428 | 121.4034 | 122.9491 | 125.1529 | 127.7731 | 130.0563 | 131.7847 | 132.6073 | 133.3092 | 133.7712 | 135.0372
93006 | 68.6768 | 72.2265 | 73.365 | 75.2674 | 77.4958 | 80.014 | 82.1478 | 84.6126 | 85.7278 | 86.8232 | 87.6368 | 88.3283 |  |  | 93006 | 68.3 | 68.7404 | 68.7265 | 69.6015 | 70.8491 | 72.3324 | 73.6249 | 74.6033 | 75.069 | 75.4663 | 75.7279 | 76.4446
94001 | 88.2024 | 92.7613 | 94.2236 | 96.6668 | 99.5288 | 102.7629 | 105.5034 | 108.669 | 110.1013 | 111.5081 | 112.5529 | 113.441 |  |  | 94001 | 60.3174 | 60.7064 | 60.6941 | 61.4669 | 62.5686 | 63.8785 | 65.02 | 65.8841 | 66.2954 | 66.6462 | 66.8772 | 67.5101
94002 | 159.1807 | 167.4083 | 170.0472 | 174.4565 | 179.6216 | 185.4582 | 190.4041 | 196.1171 | 198.702 | 201.2409 | 203.1266 | 204.7293 |  |  | 94002 | 185.8407 | 187.0391 | 187.0012 | 189.3822 | 192.7766 | 196.8126 | 200.3296 | 202.9918 | 204.259 | 205.3401 | 206.0517 | 208.0018
95001 | 19.6049 | 20.6182 | 20.9432 | 21.4863 | 22.1224 | 22.8413 | 23.4504 | 24.154 | 24.4724 | 24.7851 | 25.0173 | 25.2147 |  |  | 95001 | 29.5581 | 29.7487 | 29.7427 | 30.1214 | 30.6613 | 31.3032 | 31.8626 | 32.286 | 32.4876 | 32.6595 | 32.7727 | 33.0828
96202 | 85.7145 | 90.1449 | 91.5659 | 93.9401 | 96.7214 | 99.8643 | 102.5275 | 105.6038 | 106.9957 | 108.3628 | 109.3782 | 110.2413 |  |  | 96202 | 105.147 | 105.825 | 105.8036 | 107.1507 | 109.0712 | 111.3548 | 113.3446 | 114.8509 | 115.5678 | 116.1795 | 116.5821 | 117.6855
97001 | 15.0997 | 15.8801 | 16.1304 | 16.5487 | 17.0387 | 17.5923 | 18.0615 | 18.6034 | 18.8486 | 19.0894 | 19.2683 | 19.4203 |  |  | 97001 | 31.3483 | 31.5504 | 31.544 | 31.9456 | 32.5182 | 33.199 | 33.7923 | 34.2414 | 34.4551 | 34.6375 | 34.7575 | 35.0865
97002 | 18.9829 | 19.9641 | 20.2788 | 20.8046 | 21.4206 | 22.1166 | 22.7064 | 23.3877 | 23.696 | 23.9987 | 24.2236 | 24.4148 |  |  | 97002 | 38.1278 | 38.3737 | 38.3659 | 38.8544 | 39.5508 | 40.3789 | 41.1004 | 41.6466 | 41.9066 | 42.1284 | 42.2744 | 42.6745
97013 | 17.1512 | 18.0376 | 18.322 | 18.7971 | 19.3536 | 19.9825 | 20.5154 | 21.1309 | 21.4094 | 21.683 | 21.8862 | 22.0589 |  |  | 97013 | 31.3377 | 31.5398 | 31.5334 | 31.9349 | 32.5073 | 33.1879 | 33.7809 | 34.2298 | 34.4435 | 34.6258 | 34.7458 | 35.0746
97014 | 186.1898 | 195.8134 | 198.9001 | 204.0575 | 210.099 | 216.926 | 222.7111 | 229.3934 | 232.4169 | 235.3866 | 237.5922 | 239.4669 |  |  | 97014 | 221.7492 | 223.1791 | 223.134 | 225.975 | 230.0253 | 234.8412 | 239.0377 | 242.2143 | 243.7263 | 245.0163 | 245.8654 | 248.1924
98001 | 37.2375 | 39.1622 | 39.7795 | 40.811 | 42.0193 | 43.3846 | 44.5416 | 45.8781 | 46.4828 | 47.0767 | 47.5178 | 47.8928 |  |  | 98001 | 50.1956 | 50.5193 | 50.509 | 51.1521 | 52.069 | 53.1591 | 54.109 | 54.8281 | 55.1704 | 55.4624 | 55.6546 | 56.1813
98002 | 35.3108 | 37.136 | 37.7214 | 38.6994 | 39.8452 | 41.14 | 42.2371 | 43.5044 | 44.0778 | 44.641 | 45.0593 | 45.4148 |  |  | 98002 | 67.6353 | 68.0714 | 68.0577 | 68.9242 | 70.1596 | 71.6284 | 72.9084 | 73.8773 | 74.3385 | 74.7319 | 74.9909 | 75.7007
98003 | 22.1026 | 23.245 | 23.6115 | 24.2237 | 24.9409 | 25.7513 | 26.4381 | 27.2313 | 27.5903 | 27.9428 | 28.2046 | 28.4272 |  |  | 98003 | 41.2281 | 41.494 | 41.4856 | 42.0138 | 42.7668 | 43.6622 | 44.4424 | 45.033 | 45.3142 | 45.554 | 45.7119 | 46.1445
99981 | 25.1962 | 26.4985 | 26.9162 | 27.6142 | 28.4317 | 29.3556 | 30.1385 | 31.0427 | 31.4519 | 31.8538 | 32.1523 | 32.406 |  |  | 99981 | 44.781 | 45.0697 | 45.0606 | 45.6343 | 46.4523 | 47.4248 | 48.2723 | 48.9138 | 49.2191 | 49.4796 | 49.6511 | 50.121
99982 | 17.6328 | 18.5441 | 18.8365 | 19.3249 | 19.897 | 20.5436 | 21.0914 | 21.7243 | 22.0106 | 22.2918 | 22.5007 | 22.6783 |  |  | 99982 | 25.3663 | 25.5299 | 25.5247 | 25.8497 | 26.313 | 26.8639 | 27.344 | 27.7074 | 27.8803 | 28.0279 | 28.125 | 28.3912
99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 99983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18131A | 115.2398 | 121.1961 | 123.1066 | 126.2987 | 130.0381 | 134.2635 | 137.8441 | 141.9801 | 143.8515 | 145.6895 | 147.0546 | 148.2149 |  |  | 18131A | 16.3296 | 16.4349 | 16.4316 | 16.6408 | 16.9391 | 17.2937 | 17.6027 | 17.8367 | 17.948 | 18.043 | 18.1055 | 18.2769
18131B | 136.5923 | 143.6523 | 145.9168 | 149.7004 | 154.1326 | 159.1409 | 163.385 | 168.2872 | 170.5054 | 172.684 | 174.3021 | 175.6774 |  |  | 18131B | 170.9133 | 172.0154 | 171.9806 | 174.1703 | 177.2921 | 181.0039 | 184.2384 | 186.6868 | 187.8522 | 188.8464 | 189.5009 | 191.2944
18132A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18132A | 180.0495 | 181.2105 | 181.1739 | 183.4806 | 186.7693 | 190.6795 | 194.0869 | 196.6662 | 197.8939 | 198.9412 | 199.6307 | 201.52
18132B | 38.3985 | 40.3832 | 41.0198 | 42.0835 | 43.3294 | 44.7374 | 45.9305 | 47.3086 | 47.9321 | 48.5446 | 48.9994 | 49.3861 |  |  | 18132B | 36.3824 | 36.617 | 36.6096 | 37.0758 | 37.7403 | 38.5304 | 39.219 | 39.7401 | 39.9882 | 40.1999 | 40.3392 | 40.721
18133A | 36.9659 | 38.8765 | 39.4893 | 40.5133 | 41.7128 | 43.0682 | 44.2167 | 45.5434 | 46.1437 | 46.7333 | 47.1712 | 47.5434 |  |  | 18133A | 35.2062 | 35.4333 | 35.4261 | 35.8771 | 36.5202 | 37.2848 | 37.9511 | 38.4554 | 38.6955 | 38.9003 | 39.0351 | 39.4045
18133B | 20.299 | 21.3482 | 21.6847 | 22.247 | 22.9056 | 23.6499 | 24.2807 | 25.0092 | 25.3388 | 25.6626 | 25.903 | 26.1074 |  |  | 18133B | 38.315 | 38.5621 | 38.5543 | 39.0452 | 39.745 | 40.5771 | 41.3022 | 41.8511 | 42.1123 | 42.3352 | 42.4819 | 42.884
18134A | 30.0382 | 31.5907 | 32.0887 | 32.9208 | 33.8955 | 34.9969 | 35.9302 | 37.0082 | 37.496 | 37.9751 | 38.331 | 38.6334 |  |  | 18134A | 62.8694 | 63.2748 | 63.262 | 64.0675 | 65.2158 | 66.5812 | 67.771 | 68.6716 | 69.1003 | 69.466 | 69.7067 | 70.3665
18134B | 14.5779 | 15.3314 | 15.5731 | 15.9769 | 16.4499 | 16.9845 | 17.4374 | 17.9606 | 18.1974 | 18.4299 | 18.6026 | 18.7493 |  |  | 18134B | 43.2383 | 43.5171 | 43.5083 | 44.0622 | 44.852 | 45.791 | 46.6093 | 47.2287 | 47.5235 | 47.775 | 47.9406 | 48.3943
18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18135A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18135B | 58.2306 | 61.2404 | 62.2058 | 63.8187 | 65.7082 | 67.8433 | 69.6526 | 71.7425 | 72.6881 | 73.6169 | 74.3067 | 74.893 |  |  | 18135B | 102.0212 | 102.6791 | 102.6583 | 103.9654 | 105.8288 | 108.0445 | 109.9752 | 111.4367 | 112.1323 | 112.7258 | 113.1165 | 114.187
18136A | 34.014 | 35.7721 | 36.336 | 37.2782 | 38.3819 | 39.6291 | 40.6859 | 41.9067 | 42.459 | 43.0015 | 43.4045 | 43.747 |  |  | 18136A | 102.181 | 102.8399 | 102.8191 | 104.1282 | 105.9945 | 108.2137 | 110.1474 | 111.6112 | 112.3079 | 112.9023 | 113.2936 | 114.3658
18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18141B | 111.1759 | 116.9222 | 118.7653 | 121.8449 | 125.4523 | 129.5288 | 132.9831 | 136.9732 | 138.7786 | 140.5518 | 141.8688 | 142.9882 |  |  | 18141B | 179.7419 | 180.9009 | 180.8643 | 183.1671 | 186.4502 | 190.3537 | 193.7553 | 196.3301 | 197.5557 | 198.6013 | 199.2896 | 201.1757
18142A | 8.175 | 8.5975 | 8.733 | 8.9595 | 9.2248 | 9.5245 | 9.7785 | 10.0719 | 10.2047 | 10.335 | 10.4319 | 10.5142 |  |  | 18142A | 21.5986 | 21.7379 | 21.7335 | 22.0102 | 22.4047 | 22.8738 | 23.2825 | 23.5919 | 23.7392 | 23.8648 | 23.9475 | 24.1742
18142B | 22.0395 | 23.1786 | 23.544 | 24.1545 | 24.8696 | 25.6777 | 26.3625 | 27.1535 | 27.5114 | 27.8629 | 28.124 | 28.3459 |  |  | 18142B | 35.5204 | 35.7494 | 35.7422 | 36.1973 | 36.8461 | 37.6175 | 38.2897 | 38.7985 | 39.0407 | 39.2474 | 39.3834 | 39.7561
18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18143B | 85.3335 | 89.7441 | 91.1588 | 93.5225 | 96.2914 | 99.4203 | 102.0717 | 105.1343 | 106.5201 | 107.8811 | 108.892 | 109.7512 |  |  | 18143B | 227.1272 | 228.5918 | 228.5455 | 231.4554 | 235.604 | 240.5366 | 244.8349 | 248.0886 | 249.6373 | 250.9585 | 251.8282 | 254.2116
18144A | 40.5557 | 42.6519 | 43.3242 | 44.4476 | 45.7636 | 47.2506 | 48.5107 | 49.9662 | 50.6248 | 51.2717 | 51.7521 | 52.1604 |  |  | 18144A | 104.3569 | 105.0298 | 105.0086 | 106.3455 | 108.2517 | 110.518 | 112.493 | 113.9879 | 114.6995 | 115.3065 | 115.7061 | 116.8012
18144B | 53.5145 | 56.2805 | 57.1677 | 58.6501 | 60.3865 | 62.3487 | 64.0115 | 65.9321 | 66.8011 | 67.6546 | 68.2886 | 68.8274 |  |  | 18144B | 147.5615 | 148.513 | 148.483 | 150.3735 | 153.0688 | 156.2734 | 159.066 | 161.1798 | 162.186 | 163.0444 | 163.6094 | 165.1579
18145A | 31.5009 | 33.1291 | 33.6513 | 34.5239 | 35.546 | 36.7011 | 37.6798 | 38.8104 | 39.3219 | 39.8244 | 40.1975 | 40.5147 |  |  | 18145A | 55.5256 | 55.8837 | 55.8724 | 56.5837 | 57.5979 | 58.8038 | 59.8546 | 60.65 | 61.0287 | 61.3517 | 61.5643 | 62.1469
18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18146A | 70.4956 | 74.1393 | 75.308 | 77.2607 | 79.5482 | 82.133 | 84.3234 | 86.8534 | 87.9982 | 89.1226 | 89.9577 | 90.6675 |  |  | 18146A | 187.0952 | 188.3016 | 188.2636 | 190.6606 | 194.0779 | 198.1412 | 201.6819 | 204.3621 | 205.6378 | 206.7262 | 207.4426 | 209.4059
18146B | 93.4583 | 98.2889 | 99.8383 | 102.4271 | 105.4596 | 108.8864 | 111.7903 | 115.1444 | 116.6621 | 118.1527 | 119.2599 | 120.2009 |  |  | 18146B | 268.7607 | 270.4937 | 270.439 | 273.8823 | 278.7913 | 284.6281 | 289.7143 | 293.5644 | 295.397 | 296.9604 | 297.9895 | 300.8098
Substation
Feeder
Zone
Additional Information