## Disclaimer
TasNetworks - Annual Planning Report 2019 - Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2019.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Methodology
Fault level and sequence impedances
We calculate fault currents at transmission network substations in accordance with the recommendations of Australian Standard AS 3851-1991 – “The calculation of short-circuit currents in three-phase AC systems”. From this, the maximum fault currents calculated at 1.1 pu voltage and the minimum at 0.9 pu voltage. The Thevenin impedance is defined as the source impedance back to the generators, and large motors where considered. This method thus defines the extreme envelope for all fault currents and is appropriate to be used for future planning. We recognise that at particular network locations the actual envelope could be smaller but this would need confirmation with detailed local studies.
Figure B–1 illustrates the AC and DC components that make up fault currents. The size and rate of decay of the DC component is a function of the ratio between the reactance (X) and the resistance (R) of the impedance between the faulted point of the system and the generation feeding the fault. This ratio is defined as the X/R ratio of the system, with the DC component decaying with time constant X/2πfR.
The maximum current that a circuit breaker will be exposed to is defined as the Peak Make Current. During fault conditions, the current a circuit breaker is expected to break is known as the RMS Break Current. This is defined as the RMS of the symmetrical AC component of the fault current plus the offset by the DC component at that point.
Figure B–1: Components of AC fault current

## Maximum
Maximum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 3.9116 | 3.6654 | 0.05305 | 0.1392 | 2.624 | 0.05506 | 0.14244 | 2.587 | 0.03218 | 0.17417 | 5.412
Arthurs Lake | 6.6 | 19.0425 | 0.0027 | 0.05213 | 0.50532 | 9.694 | 0.06326 | 0.55676 | 8.8 | 0.74984 | 0 | 0
Avoca | 110 | 1.8388 | 1.2096 | 0.1512 | 0.27915 | 1.846 | 0.1513 | 0.28053 | 1.854 | 0.22866 | 0.78723 | 3.443
Avoca | 22 | 3.6055 | 1.5852 | 0.1757 | 0.79025 | 4.498 | 0.1758 | 0.79163 | 4.503 | 0 | 3.9308 | >50
Boyer | 110 | 10.9321 | 6.9366 | 0.00913 | 0.05243 | 5.743 | 0.00944 | 0.05458 | 5.782 | 0.02837 | 0.14021 | 4.941
Boyer (A & B) | 6.6 | 27.5317 | 10.635 | 0.01933 | 0.35152 | 18.183 | 0.01961 | 0.35348 | 18.026 | 0 | 2.0289 | >50
Boyer (D & E) | 6.6 | 35.6646 | 16.4542 | 0.01011 | 0.27106 | 26.815 | 0.01366 | 0.31552 | 23.106 | 0.00132 | 1.177 | >50
Boyer (F) | 6.6 | 28.9393 | 12.4283 | 0.00702 | 0.33346 | 47.51 | 0.00707 | 0.33465 | 47.363 | 0.00077 | 1.6618 | >50
Boyer (G) | 6.6 | 24.398 | 11.8191 | 0.00955 | 0.39579 | 41.427 | 0.00947 | 0.3941 | 41.601 | 0.00606 | 1.6618 | >50
Bridgewater | 110 | 7.7509 | 5.0877 | 0.01486 | 0.07369 | 4.958 | 0.01489 | 0.07512 | 5.044 | 0.04698 | 0.18609 | 3.961
Bridgewater | 11 | 14.1588 | 6.0489 | 0.02045 | 0.41102 | 20.103 | 0.02048 | 0.41245 | 20.144 | 0 | 2.0661 | >50
Bridgewater1 | 11 | 7.8159 | 3.1086 | 0.03696 | 0.74459 | 20.144 | 0.03699 | 0.74602 | 20.167 | 0 | 4.1322 | >50
Burnie | 220 | 5.5366 | 4.376 | 0.00796 | 0.05245 | 6.588 | 0.00796 | 0.05303 | 6.662 | 0.01348 | 0.09372 | 6.954
Burnie | 110 | 8.5032 | 5.4597 | 0.01081 | 0.06824 | 6.312 | 0.01084 | 0.06858 | 6.325 | 0.02486 | 0.18263 | 7.345
Burnie | 22 | 11.9513 | 5.6818 | 0.01716 | 0.24519 | 14.288 | 0.01719 | 0.24553 | 14.282 | 0 | 1.0599 | >50
Butlers Gorge | 110 | 4.8643 | 4.3179 | 0.04357 | 0.11181 | 2.566 | 0.04504 | 0.11584 | 2.572 | 0.02774 | 0.16085 | 5.798
Chapel Street | 220 | 8.6615 | 8.2683 | 0.00371 | 0.03342 | 9.001 | 0.00377 | 0.03455 | 9.157 | 0.00305 | 0.03718 | 12.192
Chapel Street | 110 | 15.5805 | 16.4534 | 0.00411 | 0.03716 | 9.042 | 0.00416 | 0.03853 | 9.267 | 0.00203 | 0.03002 | 14.784
Chapel Street | 11 | 15.8598 | 9.0362 | 0.01346 | 0.36706 | 27.27 | 0.01351 | 0.36843 | 27.275 | 0 | 1.1984 | >50
Chapel Street1 | 11 | 8.3598 | 4.6096 | 0.02281 | 0.69646 | 30.533 | 0.02286 | 0.69783 | 30.529 | 0 | 2.3967 | >50
Comalco | 220 | 12.6006 | 14.9489 | 0.00194 | 0.02305 | 11.901 | 0.00198 | 0.02396 | 12.074 | 0.00075 | 0.01129 | 15.115
Creek Road | 110 | 14.9695 | 14.5185 | 0.00453 | 0.03865 | 8.542 | 0.00458 | 0.04004 | 8.751 | 0.00574 | 0.04076 | 7.096
Creek Road | 33 | 14.2867 | 5.9262 | 0.00694 | 0.13574 | 19.569 | 0.00699 | 0.13713 | 19.626 | 0 | 0.71003 | >50
Creek Road2 | 33 | 10.528 | 4.094 | 0.00823 | 0.18425 | 22.4 | 0.00828 | 0.18564 | 22.431 | 0 | 1.0529 | >50
Derby | 110 | 3.9041 | 2.064 | 0.026 | 0.14826 | 5.702 | 0.02665 | 0.15205 | 5.706 | 0.15769 | 0.52751 | 3.345
Derby | 22 | 4.3579 | 1.2924 | 0.046 | 0.67266 | 14.623 | 0.04665 | 0.67645 | 14.501 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 3.3672 | 2.532 | 0.07253 | 0.15739 | 2.17 | 0.07372 | 0.16119 | 2.186 | 0.08363 | 0.33348 | 3.987
Derwent Bridge | 22 | 4.2319 | 1.8546 | 0.08823 | 0.68379 | 7.75 | 0.08942 | 0.68759 | 7.689 | 0 | 3.345 | >50
Devonport | 110 | 7.259 | 4.8294 | 0.011 | 0.08036 | 7.307 | 0.01097 | 0.08044 | 7.335 | 0.03148 | 0.20102 | 6.386
Devonport | 22 | 11.8738 | 4.2262 | 0.01687 | 0.24736 | 14.665 | 0.01684 | 0.24744 | 14.697 | 0 | 1.5947 | >50
Electrona | 110 | 6.322 | 3.8799 | 0.02633 | 0.0883 | 3.354 | 0.02637 | 0.08967 | 3.4 | 0.05299 | 0.25988 | 4.905
Electrona | 11 | 16.8918 | 6.7797 | 0.0365 | 0.34293 | 9.395 | 0.03655 | 0.3443 | 9.42 | 0 | 1.8895 | >50
Electrona1 | 11 | 9.9939 | 3.2507 | 0.05053 | 0.5807 | 11.493 | 0.05057 | 0.58207 | 11.51 | 0 | 4.2124 | >50
Emu Bay | 110 | 7.8696 | 5.0157 | 0.01318 | 0.0735 | 5.578 | 0.01321 | 0.07384 | 5.59 | 0.03165 | 0.19931 | 6.298
Emu Bay | 11 | 15.3393 | 6.3365 | 0.02315 | 0.38237 | 16.516 | 0.02318 | 0.38271 | 16.508 | 0 | 2.0166 | >50
Emu Bay1,3 | 11 | 8.5062 | 3.2561 | 0.03318 | 0.69 | 20.797 | 0.03321 | 0.69034 | 20.788 | 0 | 4.0331 | >50
Farrell | 220 | 9.712 | 10.1427 | 0.00187 | 0.0303 | 16.195 | 0.00195 | 0.03161 | 16.249 | 0.00298 | 0.02504 | 8.403
Farrell | 110 | 8.2249 | 10.1962 | 0.00232 | 0.07186 | 30.928 | 0.00238 | 0.07154 | 30.12 | 0.00131 | 0.03049 | 23.261
George Town | 220 | 13.1653 | 15.7404 | 0.00175 | 0.02207 | 12.634 | 0.00179 | 0.02298 | 12.806 | 0.00065 | 0.01034 | 16.032
George Town | 110 | 14.9005 | 16.7611 | 0.00159 | 0.03902 | 24.473 | 0.00166 | 0.0405 | 24.463 | 0.00053 | 0.02457 | 46.084
George Town | 22 | 10.1799 | 5.6888 | 0.00581 | 0.28579 | 49.174 | 0.00587 | 0.28726 | 48.914 | 0 | 0.96143 | >50
Gordon | 220 | 7.3438 | 8.3258 | 0.00253 | 0.03952 | 15.613 | 0.00247 | 0.03966 | 16.037 | 0.00063 | 0.02546 | 40.371
Gordon | 22 | 2.1094 | 0.1997 | 0.07063 | 1.3768 | 19.493 | 0.07057 | 1.377 | 19.511 | 0 | 40.9333 | >50
Hadspen | 220 | 12.636 | 11.6082 | 0.00233 | 0.02298 | 9.88 | 0.00237 | 0.02389 | 10.069 | 0.00437 | 0.028 | 6.404
Hadspen | 110 | 14.7157 | 14.5095 | 0.00347 | 0.03954 | 11.41 | 0.00356 | 0.04099 | 11.503 | 0.00369 | 0.03977 | 10.784
Hadspen | 22 | 10.1293 | 5.4019 | 0.00773 | 0.28824 | 37.266 | 0.00783 | 0.28969 | 36.986 | 0 | 1.0441 | >50
Hampshire | 110 | 3.6163 | 2.1617 | 0.0432 | 0.15661 | 3.625 | 0.04323 | 0.15695 | 3.63 | 0.10795 | 0.47827 | 4.43
Huon River | 110 | 2.6603 | 1.6678 | 0.08754 | 0.20072 | 2.293 | 0.08759 | 0.20208 | 2.307 | 0.1685 | 0.58711 | 3.484
Huon River | 11 | 7.9878 | 3.6024 | 0.10344 | 0.72192 | 6.979 | 0.10349 | 0.72328 | 6.989 | 0 | 3.4017 | >50
Kermandie | 110 | 3.2932 | 1.9902 | 0.06653 | 0.16391 | 2.464 | 0.06658 | 0.16527 | 2.482 | 0.13259 | 0.50775 | 3.829
Kermandie | 11 | 8.8456 | 11.5975 | 0.09444 | 0.65176 | 6.901 | 0.09449 | 0.65313 | 6.912 | 0.03778 | 0.18486 | 4.893
Kingston | 110 | 8.6039 | 5.1263 | 0.01503 | 0.06602 | 4.393 | 0.01508 | 0.06739 | 4.47 | 0.0356 | 0.20112 | 5.649
Kingston | 33 | 7.3195 | 2.1138 | 0.01928 | 0.26459 | 13.725 | 0.01933 | 0.26596 | 13.762 | 0 | 2.2251 | >50
Kingston | 11 | 14.6465 | 6.02 | 0.02603 | 0.39688 | 15.248 | 0.02608 | 0.39825 | 15.273 | 0 | 2.1075 | >50
Kingston1 | 11 | 8.0333 | 3.0849 | 0.03693 | 0.72422 | 19.612 | 0.03698 | 0.72559 | 19.623 | 0 | 4.2149 | >50
Knights Rd | 110 | 5.7766 | 3.5664 | 0.02763 | 0.09699 | 3.51 | 0.02768 | 0.09835 | 3.553 | 0.05882 | 0.28121 | 4.781
Knights Rd | 11 | 10.4553 | 3.6005 | 0.03373 | 0.55615 | 16.487 | 0.03378 | 0.55752 | 16.504 | 0 | 3.7397 | >50
Liapootah | 220 | 9.6972 | 9.5642 | 0.00306 | 0.02992 | 9.767 | 0.00331 | 0.0318 | 9.605 | 0.00304 | 0.02927 | 9.621
Lindisfarne | 220 | 6.2682 | 6.4334 | 0.00455 | 0.04628 | 10.175 | 0.00463 | 0.04757 | 10.271 | 0.00508 | 0.04132 | 8.135
Lindisfarne | 110 | 13.9834 | 11.9594 | 0.00504 | 0.04136 | 8.206 | 0.00509 | 0.04272 | 8.396 | 0.00982 | 0.06071 | 6.18
Lindisfarne | 33 | 8.5302 | 10.9394 | 0.01404 | 0.22726 | 16.187 | 0.01409 | 0.22862 | 16.229 | 0 | 0.07602 | >50
Meadowbank | 110 | 9.099 | 7.3123 | 0.01381 | 0.06252 | 4.528 | 0.01436 | 0.06527 | 4.544 | 0.01219 | 0.1078 | 8.842
Meadowbank | 22 | 5.0628 | 3.9727 | 0.03821 | 0.57412 | 15.026 | 0.03876 | 0.57687 | 14.882 | 0 | 1.0475 | >50
Mornington | 110 | 11.2943 | 7.6923 | 0.007 | 0.05111 | 7.299 | 0.00705 | 0.05247 | 7.442 | 0.02261 | 0.12069 | 5.337
Mornington | 33 | 8.0027 | 2.1518 | 0.01123 | 0.24244 | 21.592 | 0.01128 | 0.24379 | 21.622 | 0 | 2.2216 | >50
Mowbray | 110 | 11.63 | 11.3833 | 0.00505 | 0.04999 | 9.889 | 0.00521 | 0.05162 | 9.913 | 0.00628 | 0.0515 | 8.194
Mowbray | 22 | 9.8226 | 4.3907 | 0.00986 | 0.29727 | 30.151 | 0.01001 | 0.2989 | 29.855 | 0 | 1.3999 | >50
New Norfolk | 110 | 12.1165 | 7.7773 | 0.00823 | 0.04732 | 5.753 | 0.00851 | 0.0494 | 5.805 | 0.02126 | 0.12451 | 5.855
New Norfolk | 22 | 7.8905 | 3.7798 | 0.01673 | 0.36837 | 22.025 | 0.01701 | 0.37045 | 21.778 | 0 | 1.5702 | >50
Newton | 110 | 2.1755 | 1.6235 | 0.06509 | 0.2639 | 4.054 | 0.06514 | 0.26358 | 4.046 | 0.12951 | 0.53386 | 4.122
Newton | 11 | 6.5644 | 0.2241 | 0.09379 | 0.8959 | 9.552 | 0.09384 | 0.89558 | 9.543 | 78.7191 | 4.6116 | 0.059
Newton | 22 | 3.2631 | 1.4336 | 0.09379 | 0.9012 | 9.609 | 0.09384 | 0.90088 | 9.6 | 0 | 4.3822 | >50
North Hobart | 110 | 14.034 | 13.3537 | 0.00649 | 0.041 | 6.321 | 0.00654 | 0.04239 | 6.485 | 0.01072 | 0.04531 | 4.225
North Hobart | 11 | 11.5777 | 6.1756 | 0.0098 | 0.50306 | 51.336 | 0.00985 | 0.50446 | 51.212 | 0 | 1.8223 | >50
Norwood | 110 | 12.1502 | 11.0071 | 0.00494 | 0.04783 | 9.682 | 0.00506 | 0.04936 | 9.76 | 0.01019 | 0.06077 | 5.964
Norwood | 22 | 9.2638 | 5.6182 | 0.01216 | 0.31513 | 25.915 | 0.01228 | 0.31666 | 25.793 | 0 | 0.92802 | >50
Palmerston | 220 | 14.0347 | 14.4405 | 0.00175 | 0.02072 | 11.86 | 0.0018 | 0.02168 | 12.014 | 0.00194 | 0.01798 | 9.281
Palmerston | 110 | 13.9724 | 14.3241 | 0.00432 | 0.04156 | 9.614 | 0.00442 | 0.04294 | 9.721 | 0.00282 | 0.03722 | 13.201
Palmerston | 22 | 9.684 | 3.3828 | 0.0154 | 0.30101 | 19.551 | 0.01549 | 0.30239 | 19.52 | 0 | 1.9849 | >50
Paloona | 110 | 9.4353 | 9.5267 | 0.00853 | 0.06185 | 7.252 | 0.00858 | 0.06216 | 7.241 | 0.00239 | 0.06047 | 25.281
Port Latta | 110 | 3.8237 | 1.9131 | 0.04884 | 0.14534 | 2.976 | 0.04883 | 0.14556 | 2.981 | 0.17858 | 0.586 | 3.282
Port Latta | 22 | 8.3248 | 3.266 | 0.06214 | 0.34661 | 5.578 | 0.06212 | 0.34683 | 5.583 | 0 | 1.9964 | >50
Que | 110 | 4.107 | 3.383 | 0.02751 | 0.14133 | 5.137 | 0.02757 | 0.14101 | 5.115 | 0.06654 | 0.22774 | 3.423
Que | 22 | 3.9431 | 1.7467 | 0.04581 | 0.74843 | 16.336 | 0.04587 | 0.74811 | 16.311 | 0 | 3.5806 | >50
Queenstown | 110 | 3.0573 | 2.3678 | 0.02099 | 0.19227 | 9.16 | 0.02104 | 0.19195 | 9.122 | 0.07413 | 0.35591 | 4.801
Queenstown | 22 | 6.5535 | 3.396 | 0.02934 | 0.45019 | 15.343 | 0.02939 | 0.44987 | 15.305 | 0 | 1.7111 | >50
Queenstown | 11 | 12.9986 | 6.7403 | 0.02866 | 0.45401 | 15.841 | 0.02871 | 0.45369 | 15.801 | 0 | 1.7235 | >50
Railton | 110 | 9.1616 | 6.6988 | 0.00677 | 0.06391 | 9.439 | 0.00674 | 0.06399 | 9.495 | 0.03089 | 0.13202 | 4.274
Railton | 22 | 8.6266 | 3.8594 | 0.0139 | 0.34099 | 24.539 | 0.01386 | 0.34107 | 24.6 | 0 | 1.6062 | >50
Risdon | 110 | 14.4061 | 12.6708 | 0.00491 | 0.04014 | 8.176 | 0.00496 | 0.04151 | 8.374 | 0.00923 | 0.05497 | 5.954
Risdon | 33 | 11.2868 | 4.5896 | 0.00805 | 0.17188 | 21.355 | 0.0081 | 0.17325 | 21.399 | 0 | 0.92423 | >50
Risdon | 11 | 20.7885 | 3.271 | 0.00921 | 0.27028 | 29.348 | 0.00926 | 0.27164 | 29.346 | 4.8476 | 1.1631 | 0.24
Rokeby | 110 | 8.6388 | 5.4851 | 0.01014 | 0.06668 | 6.574 | 0.01019 | 0.06804 | 6.677 | 0.03457 | 0.1792 | 5.184
Rokeby | 11 | 14.723 | 6.115 | 0.01956 | 0.39528 | 20.213 | 0.0196 | 0.39633 | 20.233 | 0 | 2.0661 | >50
Rokeby1 | 11 | 7.9116 | 3.1184 | 0.03204 | 0.73578 | 22.962 | 0.03209 | 0.73714 | 22.971 | 0 | 4.1322 | >50
Rosebery | 110 | 7.367 | 7.7279 | 0.00545 | 0.08008 | 14.685 | 0.0055 | 0.07976 | 14.489 | 0.0152 | 0.06821 | 4.487
Rosebery | 44 | 4.3008 | 1.8391 | 0.0165 | 0.34333 | 20.804 | 0.01655 | 0.34301 | 20.72 | 0 | 1.7249 | >50
Rosebery | 22 | 2.6803 | 2.2292 | 0.0778 | 1.1003 | 14.142 | 0.07785 | 1.1 | 14.129 | 0 | 1.7755 | >50
Savage River | 110 | 1.8838 | 1.2325 | 0.08666 | 0.30171 | 3.481 | 0.08672 | 0.30139 | 3.476 | 0.18428 | 0.79105 | 4.293
Savage River | 22 | 5.6741 | 3.1571 | 0.10016 | 0.51136 | 5.105 | 0.10022 | 0.51104 | 5.099 | 0 | 1.7799 | >50
Scottsdale | 110 | 5.2519 | 3.3487 | 0.02249 | 0.10932 | 4.861 | 0.02276 | 0.11143 | 4.895 | 0.07968 | 0.28927 | 3.63
Scottsdale | 22 | 12.2023 | 6.7278 | 0.02819 | 0.23852 | 8.461 | 0.02846 | 0.24063 | 8.454 | 0 | 0.82645 | >50
Sheffield | 220 | 13.4702 | 13.5382 | 0.00169 | 0.02173 | 12.832 | 0.0017 | 0.02244 | 13.17 | 0.0027 | 0.02061 | 7.642
Sheffield | 110 | 12.7315 | 13.8285 | 0.0031 | 0.04614 | 14.868 | 0.00307 | 0.04622 | 15.047 | 0.00233 | 0.03509 | 15.089
Smithton | 110 | 4.2639 | 1.7468 | 0.03629 | 0.13251 | 3.652 | 0.03626 | 0.13269 | 3.659 | 0.2161 | 0.6986 | 3.233
Smithton | 22 | 7.8527 | 8.1988 | 0.04299 | 0.37051 | 8.619 | 0.04296 | 0.37069 | 8.629 | 0 | 0.3271 | >50
Sorell | 110 | 5.101 | 3.1006 | 0.02954 | 0.11034 | 3.735 | 0.02959 | 0.1117 | 3.775 | 0.06565 | 0.32775 | 4.992
Sorell | 22 | 8.6008 | 2.9125 | 0.02229 | 0.338 | 15.163 | 0.02234 | 0.33936 | 15.192 | 0 | 2.3232 | >50
St Leonards | 110 | 11.3193 | 10.8413 | 0.00518 | 0.05136 | 9.917 | 0.00531 | 0.05293 | 9.968 | 0.00886 | 0.05624 | 6.345
St Leonards | 22 | 9.4136 | 2.5505 | 0.00858 | 0.31023 | 36.163 | 0.00871 | 0.3118 | 35.8 | 0 | 2.8144 | >50
St Marys | 110 | 1.1336 | 0.7219 | 0.25386 | 0.44807 | 1.765 | 0.25396 | 0.44945 | 1.77 | 0.43405 | 1.338 | 3.083
St Marys | 22 | 3.0612 | 4.2174 | 0.28689 | 0.90932 | 3.17 | 0.28698 | 0.9107 | 3.173 | 0 | 0.1754 | >50
Starwood | 110 | 10.3682 | 9.3496 | 0.00959 | 0.0553 | 5.764 | 0.00966 | 0.05678 | 5.881 | 0.01814 | 0.07087 | 3.906
Tarraleah | 110 | 11.4037 | 12.4416 | 0.00772 | 0.05054 | 6.548 | 0.00844 | 0.05387 | 6.385 | 0.00202 | 0.03499 | 17.334
Temco | 110 | 13.1713 | 12.3968 | 0.00332 | 0.04406 | 13.253 | 0.00339 | 0.04554 | 13.45 | 0.00717 | 0.05055 | 7.053
Trevallyn | 110 | 12.8325 | 12.7838 | 0.0045 | 0.04531 | 10.08 | 0.00466 | 0.04698 | 10.074 | 0.00341 | 0.04425 | 12.985
Trevallyn | 22 | 14.134 | 5.8926 | 0.00733 | 0.20658 | 28.188 | 0.0075 | 0.20825 | 27.778 | 0 | 1.0725 | >50
Trevallyn2 | 22 | 10.1676 | 4.0147 | 0.00875 | 0.28721 | 32.842 | 0.00891 | 0.28888 | 32.409 | 0 | 1.6071 | >50
Triabunna | 110 | 1.6553 | 1.1439 | 0.23949 | 0.25797 | 1.077 | 0.23953 | 0.25933 | 1.083 | 0.31947 | 0.78556 | 2.459
Triabunna | 22 | 5.0595 | 2.8052 | 0.24949 | 0.51897 | 2.08 | 0.24953 | 0.52033 | 2.085 | 0 | 2.0362 | >50
Tungatinah | 110 | 11.6105 | 12.7878 | 0.00727 | 0.04969 | 6.837 | 0.00796 | 0.05298 | 6.66 | 0.00124 | 0.03311 | 26.615
Tungatinah | 22 | 5.0162 | 1.4523 | 0.02767 | 0.58049 | 20.981 | 0.02836 | 0.58378 | 20.588 | 0 | 4.8574 | >50
Ulverstone | 110 | 6.6498 | 4.7932 | 0.01943 | 0.08634 | 4.443 | 0.01947 | 0.08666 | 4.45 | 0.04326 | 0.18605 | 4.301
Ulverstone | 22 | 9.153 | 4.5902 | 0.02698 | 0.32034 | 11.873 | 0.02702 | 0.32066 | 11.866 | 0 | 1.2813 | >50
Waddamana | 220 | 10.8078 | 9.8769 | 0.00258 | 0.02686 | 10.428 | 0.00269 | 0.0282 | 10.464 | 0.00534 | 0.03289 | 6.155
Waddamana | 110 | 8.8719 | 6.2884 | 0.01367 | 0.06425 | 4.698 | 0.01394 | 0.0664 | 4.763 | 0.02629 | 0.1421 | 5.406
Waddamana | 22 | 1.8378 | 2.3036 | 0.15167 | 1.5782 | 10.406 | 0.15194 | 1.5804 | 10.402 | 0 | 0.624 | >50
Warratah Tee | 110 | 2.5531 | 1.7987 | 0.05737 | 0.22439 | 3.911 | 0.05743 | 0.22407 | 3.902 | 0.12566 | 0.50801 | 4.043
Wesley Vale | 110 | 6.7126 | 3.8158 | 0.01408 | 0.08658 | 6.151 | 0.01404 | 0.08666 | 6.17 | 0.04709 | 0.28352 | 6.02
Wesley Vale | 22 | 7.2 | 2.9 | 0.028 | 0.404 | 14.398 | 0.028 | 0.403 | 14.169 | 0 | 2.192 | >50
Notes on above maximum fault levels • The 22 kV super feeders between Mowbray and Trevallyn substations are kept open to reduce fault level at both substations. 1 11 kV buses at Bridgewater, Chapel Street, Electrona, Emu Bay, Kingston and Rokeby substations are operated normally-open due to exceedance of 13 kA fault level. In open position the fault levels are well below 13 kA. 2 At Creek Road and Trevallyn substations the supply transformer incoming circuit breaker is operated open due to exceedance of 13 kA fault level. It is only opened when fault level exceeds 13 kA. 3 At Emu Bay Substation, 0.82 mH/Phase reactors are installed on feeders 19, 20, 21, 23 and 24 to limit the downstream distribution fault currents. With these reactors, when the 11 kV bus coupler is closed, fault current is below 13.0 kA. We are investigating the opportunity to operate the bus coupler at this substation closed. The maximum fault currents on the feeders with the reactors in service and bus coupler closed are listed below:
Maximum fault levels
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name [feeder number] | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Emu Bay [19] | 11 | 9.8 | 5.4 | 0.02315 | 0.59097 | 25.5279 | 0.02318 | 0.5913 | 25.5091 | 0 | 2.0158 | >50
Emu Bay [20] | 11 | 9.9 | 5.4 | 0.02315 | 0.58237 | 25.1564 | 0.02318 | 0.58271 | 25.1385 | 0 | 2.0158 | >50
Emu Bay [21] | 11 | 9.9 | 5.4 | 0.02315 | 0.58237 | 25.1564 | 0.02318 | 0.58271 | 25.1385 | 0 | 2.0158 | >50
Emu Bay [23] | 11 | 9.9 | 5.4 | 0.02315 | 0.58237 | 25.1564 | 0.02318 | 0.58271 | 25.1385 | 0 | 2.0158 | >50
Emu Bay [24] | 11 | 9.7 | 5.4 | 0.02315 | 0.59527 | 25.7136 | 0.02318 | 0.59561 | 25.695 | 0 | 2.0158 | >50

## Minimum
Minimum fault levels in Tasmanian substations
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Arthurs Lake | 110 | 2.3895 | 2.0686 | 0.06341 | 0.18666 | 2.944 | 0.06358 | 0.19091 | 3.003 | 0.08325 | 0.27244 | 3.273
Arthurs Lake | 6.6 | 11.1415 | 0 | 0.08221 | 0.69986 | 8.513 | 0.08238 | 0.70411 | 8.547 | 0 | 0 | 0
Avoca | 110 | 1.3214 | 0.9229 | 0.15605 | 0.32051 | 2.054 | 0.15622 | 0.32476 | 2.079 | 0.22866 | 0.78723 | 3.443
Avoca | 22 | 2.7678 | 1.2596 | 0.18055 | 0.83161 | 4.606 | 0.18072 | 0.83586 | 4.625 | 0 | 3.9308 | >50
Boyer | 110 | 4.3872 | 3.9375 | 0.01697 | 0.10771 | 6.347 | 0.01742 | 0.11111 | 6.379 | 0.02837 | 0.14021 | 4.941
Boyer (A & B) | 6.6 | 11.3352 | 4.8123 | 0.04196 | 0.69389 | 16.537 | 0.04214 | 0.6976 | 16.556 | 0 | 3.52 | >50
Boyer (D & E) | 6.6 | 10.7188 | 6.2204 | 0.03365 | 0.74307 | 22.083 | 0.0341 | 0.74647 | 21.892 | 0.0053 | 2.355 | >50
Boyer (F) | 6.6 | 10.9574 | 7.6652 | 0.03535 | 0.72678 | 20.557 | 0.0358 | 0.73018 | 20.394 | 0.00077 | 1.6626 | >50
Boyer (G) | 6.6 | 10.8735 | 7.6374 | 0.03494 | 0.73242 | 20.962 | 0.03539 | 0.73582 | 20.792 | 0.00607 | 1.6626 | >50
Bridgewater | 110 | 1.3963 | 0.9788 | 0.11092 | 0.32444 | 2.925 | 0.11127 | 0.32761 | 2.944 | 0.15411 | 0.76623 | 4.972
Bridgewater | 11 | 5.9732 | 2.5019 | 0.02059 | 0.80062 | 38.888 | 0.02078 | 0.80338 | 38.655 | 0 | 4.1322 | >50
Burnie | 220 | 0.8535 | 0.9894 | 0.04069 | 0.28055 | 6.895 | 0.04075 | 0.28391 | 6.967 | 0.01633 | 0.16263 | 9.958
Burnie | 110 | 2.3908 | 1.761 | 0.03959 | 0.1985 | 5.014 | 0.03965 | 0.20187 | 5.091 | 0.08554 | 0.4074 | 4.763
Burnie | 22 | 4.9139 | 2.3366 | 0.03143 | 0.4914 | 15.635 | 0.03149 | 0.49476 | 15.711 | 0 | 2.1198 | >50
Butlers Gorge | 110 | 2.5855 | 2.2967 | 0.06083 | 0.17352 | 2.853 | 0.0622 | 0.17934 | 2.883 | 0.06389 | 0.23932 | 3.746
Chapel Street | 220 | 2.4433 | 3.0211 | 0.01244 | 0.09708 | 7.805 | 0.01267 | 0.0998 | 7.876 | 0.00314 | 0.0389 | 12.393
Chapel Street | 110 | 5.327 | 6.7543 | 0.01103 | 0.08912 | 8.081 | 0.0112 | 0.09177 | 8.194 | 0.00203 | 0.03018 | 14.86
Chapel Street | 11 | 6.3736 | 3.6035 | 0.02938 | 0.74996 | 25.526 | 0.02959 | 0.75273 | 25.442 | 0 | 2.4793 | >50
Comalco | 220 | 3.506 | 4.7146 | 0.00651 | 0.06691 | 10.28 | 0.00668 | 0.07112 | 10.646 | 0.00075 | 0.01129 | 15.115
Creek Road | 110 | 5.1312 | 6.1605 | 0.01179 | 0.09248 | 7.841 | 0.01202 | 0.09533 | 7.931 | 0.00596 | 0.04324 | 7.253
Creek Road | 33 | 6.7867 | 3.0618 | 0.0144 | 0.23451 | 16.289 | 0.01461 | 0.23729 | 16.247 | 0 | 1.0903 | >50
Derby | 110 | 1.9092 | 1.3637 | 0.04889 | 0.24648 | 5.042 | 0.04901 | 0.25002 | 5.102 | 0.15769 | 0.52751 | 3.345
Derby | 22 | 3.4543 | 1.038 | 0.04621 | 0.68399 | 14.803 | 0.04682 | 0.68883 | 14.711 | 0 | 5.4706 | >50
Derwent Bridge | 110 | 1.8647 | 1.6719 | 0.0956 | 0.23817 | 2.491 | 0.09612 | 0.2417 | 2.515 | 0.08363 | 0.33348 | 3.987
Derwent Bridge | 22 | 3.097 | 1.4701 | 0.1113 | 0.76457 | 6.869 | 0.11182 | 0.7681 | 6.869 | 0 | 3.345 | >50
Devonport | 110 | 2.1309 | 1.9021 | 0.04412 | 0.22277 | 5.049 | 0.04419 | 0.22613 | 5.118 | 0.05762 | 0.30027 | 5.212
Devonport | 22 | 6.0794 | 2.041 | 0.02645 | 0.39712 | 15.015 | 0.02651 | 0.40048 | 15.107 | 0 | 2.7584 | >50
Electrona | 110 | 1.9864 | 1.4034 | 0.066 | 0.2316 | 3.509 | 0.06621 | 0.23437 | 3.54 | 0.1307 | 0.5222 | 3.995
Electrona | 11 | 7.1633 | 3.0135 | 0.0488 | 0.666 | 13.649 | 0.049 | 0.66877 | 13.648 | 0 | 3.4264 | >50
Emu Bay | 110 | 1.6744 | 1.5103 | 0.07326 | 0.27957 | 3.816 | 0.07332 | 0.28293 | 3.859 | 0.10703 | 0.36472 | 3.408
Emu Bay1 | 11 | 6.3211 | 2.5578 | 0.03764 | 0.74458 | 19.78 | 0.03783 | 0.74904 | 19.798 | 0 | 4.0331 | >50
Farrell | 220 | 1.6867 | 2.2949 | 0.01667 | 0.14249 | 8.545 | 0.01674 | 0.14585 | 8.714 | 0.00282 | 0.02589 | 9.181
Farrell | 110 | 2.3001 | 3.0636 | 0.014 | 0.20992 | 15 | 0.01406 | 0.21329 | 15.173 | 0.00225 | 0.04969 | 22.052
George Town | 220 | 3.1008 | 4.2729 | 0.00909 | 0.07752 | 8.524 | 0.00916 | 0.08089 | 8.832 | 0.00063 | 0.01047 | 16.677
George Town | 110 | 4.3566 | 5.6792 | 0.00688 | 0.10797 | 15.692 | 0.00705 | 0.11219 | 15.907 | 0.00039 | 0.02842 | >50
George Town | 22 | 3.9769 | 2.1528 | 0.01569 | 0.59241 | 37.756 | 0.01586 | 0.59662 | 37.612 | 0 | 2.095 | >50
Gordon | 220 | 1.3283 | 1.8476 | 0.02499 | 0.17826 | 7.132 | 0.0252 | 0.18081 | 7.176 | 0.0005 | 0.02585 | >50
Gordon | 22 | 1.6152 | 0.162 | 0.08544 | 1.4643 | 17.138 | 0.08567 | 1.4672 | 17.127 | 0 | 40.9333 | >50
Hadspen | 220 | 3.6814 | 4.3396 | 0.00611 | 0.0638 | 10.441 | 0.00629 | 0.06795 | 10.807 | 0.00466 | 0.03047 | 6.542
Hadspen | 110 | 4.7475 | 5.5789 | 0.01081 | 0.10049 | 9.293 | 0.01092 | 0.10409 | 9.528 | 0.00483 | 0.05208 | 10.784
Hadspen | 22 | 4.1112 | 2.1833 | 0.01727 | 0.58322 | 33.774 | 0.01739 | 0.58676 | 33.743 | 0 | 2.126 | >50
Hampshire | 110 | 2.09 | 1.5175 | 0.05092 | 0.22587 | 4.436 | 0.05098 | 0.22923 | 4.496 | 0.10795 | 0.47827 | 4.43
Huon River | 110 | 1.7832 | 1.2488 | 0.09411 | 0.25121 | 2.669 | 0.09432 | 0.25398 | 2.693 | 0.1685 | 0.58711 | 3.484
Huon River | 11 | 6.1297 | 2.8776 | 0.10933 | 0.76534 | 7 | 0.10955 | 0.76866 | 7.017 | 0 | 3.4017 | >50
Kermandie | 110 | 2.1118 | 1.4645 | 0.0731 | 0.2144 | 2.933 | 0.07331 | 0.21717 | 2.962 | 0.13259 | 0.50775 | 3.829
Kermandie | 11 | 3.9744 | 5.1332 | 0.12462 | 1.1858 | 9.515 | 0.12484 | 1.1891 | 9.526 | 0.0738 | 0.3757 | 5.091
Kingston | 110 | 3.3851 | 2.7206 | 0.03003 | 0.13809 | 4.598 | 0.03024 | 0.14086 | 4.658 | 0.0457 | 0.23778 | 5.203
Kingston | 33 | 3.095 | 0.873 | 0.03 | 0.51431 | 17.145 | 0.0302 | 0.51708 | 17.119 | 0 | 4.4475 | >50
Kingston | 11 | 6.1074 | 2.4646 | 0.04302 | 0.77475 | 18.01 | 0.04323 | 0.77806 | 17.997 | 0 | 4.2149 | >50
Knights Rd | 110 | 2.2347 | 1.6092 | 0.06179 | 0.20495 | 3.317 | 0.06199 | 0.20772 | 3.351 | 0.11862 | 0.44552 | 3.756
Knights Rd | 11 | 4.4577 | 1.4798 | 0.04582 | 1.0621 | 23.179 | 0.04604 | 1.0654 | 23.142 | 0 | 7.4793 | >50
Liapootah | 220 | 2.8542 | 3.57 | 0.01096 | 0.08304 | 7.574 | 0.01112 | 0.08537 | 7.676 | 0.00283 | 0.03093 | 10.935
Lindisfarne | 220 | 2.3458 | 2.8704 | 0.01136 | 0.1013 | 8.918 | 0.01155 | 0.10383 | 8.991 | 0.00487 | 0.04322 | 8.871
Lindisfarne | 110 | 5.0358 | 5.4936 | 0.01159 | 0.09429 | 8.132 | 0.01179 | 0.09709 | 8.234 | 0.01198 | 0.06746 | 5.633
Lindisfarne | 33 | 3.404 | 4.3809 | 0.02895 | 0.46753 | 16.15 | 0.02913 | 0.47022 | 16.141 | 0 | 0.1526 | >50
Meadowbank | 110 | 3.4548 | 3.5827 | 0.02652 | 0.13585 | 5.123 | 0.02817 | 0.14151 | 5.023 | 0.01309 | 0.11728 | 8.963
Meadowbank | 22 | 3.7977 | 3.1056 | 0.0447 | 0.62807 | 14.051 | 0.04577 | 0.63264 | 13.823 | 0 | 1.0475 | >50
Mornington | 110 | 4.3557 | 4.0118 | 0.01468 | 0.10884 | 7.415 | 0.01486 | 0.11153 | 7.505 | 0.02461 | 0.13322 | 5.412
Mornington | 33 | 3.3064 | 0.8839 | 0.02111 | 0.48177 | 22.823 | 0.02129 | 0.48447 | 22.754 | 0 | 4.4456 | >50
Mowbray | 110 | 3.8735 | 3.5993 | 0.01394 | 0.12307 | 8.83 | 0.01406 | 0.12661 | 9.006 | 0.03134 | 0.14577 | 4.651
Mowbray | 22 | 4.0455 | 1.2101 | 0.02123 | 0.59257 | 27.908 | 0.02135 | 0.59611 | 27.916 | 0 | 4.7583 | >50
New Norfolk | 110 | 4.0512 | 3.6779 | 0.02053 | 0.11629 | 5.664 | 0.02119 | 0.12021 | 5.672 | 0.02694 | 0.14764 | 5.48
New Norfolk | 22 | 3.2115 | 1.549 | 0.03283 | 0.74407 | 22.666 | 0.03328 | 0.74747 | 22.462 | 0 | 3.1405 | >50
Newton | 110 | 1.3774 | 1.1574 | 0.07404 | 0.34277 | 4.629 | 0.07384 | 0.34423 | 4.662 | 0.12951 | 0.53386 | 4.122
Newton | 11 | 4.8773 | 0.1779 | 0.10089 | 0.95746 | 9.49 | 0.10094 | 0.95941 | 9.504 | 78.7191 | 4.6116 | 0.059
Newton | 22 | 2.4334 | 1.1401 | 0.10471 | 0.98882 | 9.443 | 0.10477 | 0.99218 | 9.47 | 0 | 4.3822 | >50
North Hobart | 110 | 5.1957 | 6.1505 | 0.01292 | 0.09116 | 7.058 | 0.01313 | 0.09394 | 7.157 | 0.01072 | 0.04531 | 4.225
North Hobart | 11 | 4.6031 | 2.4895 | 0.02068 | 1.0293 | 49.767 | 0.0209 | 1.0327 | 49.404 | 0 | 3.6487 | >50
Norwood | 110 | 4.7012 | 5.3049 | 0.01143 | 0.10141 | 8.874 | 0.01155 | 0.10495 | 9.088 | 0.01092 | 0.06283 | 5.754
Norwood | 22 | 3.412 | 1.4423 | 0.02882 | 0.70247 | 24.374 | 0.02894 | 0.70601 | 24.395 | 0 | 3.5806 | >50
Palmerston | 220 | 3.8785 | 4.8743 | 0.00553 | 0.06046 | 10.929 | 0.00571 | 0.06447 | 11.288 | 0.00199 | 0.01939 | 9.738
Palmerston | 110 | 4.147 | 4.7026 | 0.01922 | 0.11422 | 5.941 | 0.01941 | 0.11814 | 6.087 | 0.00828 | 0.07045 | 8.513
Palmerston | 22 | 3.836 | 1.3482 | 0.02917 | 0.61332 | 21.023 | 0.02934 | 0.61757 | 21.048 | 0 | 4.0097 | >50
Paloona | 110 | 1.5408 | 1.9464 | 0.07931 | 0.3039 | 3.832 | 0.07937 | 0.30726 | 3.871 | 0.01724 | 0.11366 | 6.594
Port Latta | 110 | 0.9754 | 0.768 | 0.19239 | 0.45731 | 2.377 | 0.19245 | 0.46067 | 2.394 | 0.29013 | 0.84765 | 2.922
Port Latta | 22 | 3.5613 | 1.2064 | 0.10785 | 0.65279 | 6.053 | 0.10804 | 0.65725 | 6.083 | 0 | 4.5455 | >50
Que | 110 | 2.0846 | 2.0629 | 0.03843 | 0.22894 | 5.957 | 0.0385 | 0.23231 | 6.034 | 0.06654 | 0.22774 | 3.423
Que | 22 | 2.8875 | 1.3807 | 0.05673 | 0.83604 | 14.736 | 0.0568 | 0.83941 | 14.779 | 0 | 3.5806 | >50
Queenstown | 110 | 1.7707 | 1.5932 | 0.02994 | 0.27114 | 9.056 | 0.02974 | 0.2726 | 9.166 | 0.07413 | 0.35591 | 4.801
Queenstown | 22 | 2.9992 | 1.0287 | 0.05191 | 0.80509 | 15.509 | 0.05197 | 0.80845 | 15.555 | 0 | 5.4421 | >50
Queenstown | 11 | 6.0134 | 2.8702 | 0.04725 | 0.80336 | 17.002 | 0.04731 | 0.80672 | 17.05 | 0 | 3.4471 | >50
Railton | 110 | 3.3009 | 3.2149 | 0.01746 | 0.14556 | 8.335 | 0.01753 | 0.14892 | 8.497 | 0.04058 | 0.15073 | 3.715
Railton | 22 | 3.5262 | 1.5528 | 0.02478 | 0.66776 | 26.953 | 0.02497 | 0.67222 | 26.924 | 0 | 3.2121 | >50
Risdon | 110 | 5.1093 | 5.6365 | 0.01143 | 0.09292 | 8.128 | 0.01161 | 0.09559 | 8.234 | 0.01057 | 0.06386 | 6.041
Risdon | 33 | 5.53 | 2.4342 | 0.01513 | 0.28795 | 19.035 | 0.01532 | 0.29067 | 18.978 | 0 | 1.3863 | >50
Risdon | 11 | 10.4998 | 1.7842 | 0.01726 | 0.43926 | 25.454 | 0.01745 | 0.44199 | 25.334 | 7.2714 | 1.737 | 0.239
Rokeby | 110 | 4.1331 | 3.4507 | 0.01585 | 0.11464 | 7.233 | 0.01603 | 0.11734 | 7.319 | 0.03442 | 0.17856 | 5.187
Rokeby | 11 | 6.0342 | 2.4921 | 0.0373 | 0.78447 | 21.029 | 0.03749 | 0.78771 | 21.009 | 0 | 4.1322 | >50
Rosebery | 110 | 2.7323 | 3.3144 | 0.01954 | 0.17603 | 9.007 | 0.01961 | 0.1794 | 9.15 | 0.0184 | 0.0788 | 4.282
Rosebery | 44 | 1.7401 | 0.7495 | 0.03847 | 0.6942 | 18.043 | 0.03854 | 0.69756 | 18.101 | 0 | 3.4499 | >50
Rosebery | 22 | 2.0112 | 1.714 | 0.0862 | 1.1642 | 13.506 | 0.08626 | 1.1661 | 13.52 | 0 | 1.7755 | >50
Savage River | 110 | 1.2057 | 0.8972 | 0.09758 | 0.38932 | 3.99 | 0.09765 | 0.39269 | 4.022 | 0.18428 | 0.79105 | 4.293
Savage River | 22 | 2.9574 | 1.3996 | 0.12458 | 0.80862 | 6.491 | 0.12465 | 0.81199 | 6.514 | 0 | 3.5599 | >50
Scottsdale | 110 | 1.883 | 1.3668 | 0.05717 | 0.24829 | 4.343 | 0.05729 | 0.25183 | 4.396 | 0.15047 | 0.51901 | 3.449
Scottsdale | 22 | 5.5489 | 2.8581 | 0.04507 | 0.42995 | 9.54 | 0.04519 | 0.43349 | 9.592 | 0 | 1.6529 | >50
Sheffield | 220 | 2.3647 | 3.1469 | 0.01276 | 0.10168 | 7.966 | 0.01284 | 0.10505 | 8.184 | 0.00286 | 0.02252 | 7.875
Sheffield | 110 | 3.5709 | 4.5353 | 0.01255 | 0.13494 | 10.754 | 0.01261 | 0.1383 | 10.968 | 0.00341 | 0.0456 | 13.373
Smithton | 110 | 1.1505 | 0.8279 | 0.15928 | 0.3893 | 2.444 | 0.15934 | 0.39266 | 2.464 | 0.29456 | 0.86096 | 2.923
Smithton | 22 | 3.2237 | 3.3402 | 0.09831 | 0.72429 | 7.368 | 0.0985 | 0.72875 | 7.399 | 0 | 0.6541 | >50
Sorell | 110 | 2.8674 | 2.1403 | 0.03842 | 0.16234 | 4.225 | 0.0386 | 0.16503 | 4.275 | 0.06565 | 0.32775 | 4.992
Sorell | 22 | 3.483 | 1.2079 | 0.04528 | 0.6852 | 15.133 | 0.04546 | 0.68789 | 15.131 | 0 | 4.5662 | >50
St Leonards | 110 | 3.9954 | 4.5876 | 0.01398 | 0.11926 | 8.529 | 0.0141 | 0.1228 | 8.707 | 0.0139 | 0.06885 | 4.954
St Leonards | 22 | 3.8836 | 1.0503 | 0.01747 | 0.61743 | 35.336 | 0.01759 | 0.62097 | 35.294 | 0 | 5.6136 | >50
St Marys | 110 | 0.8509 | 0.5633 | 0.25871 | 0.48943 | 1.892 | 0.25888 | 0.49368 | 1.907 | 0.43405 | 1.338 | 3.083
St Marys | 22 | 1.6253 | 2.1772 | 0.32431 | 1.4124 | 4.355 | 0.32448 | 1.4167 | 4.366 | 0 | 0.3508 | >50
Starwood | 110 | 4.3231 | 4.8399 | 0.01528 | 0.11097 | 7.264 | 0.01534 | 0.11433 | 7.452 | 0.01814 | 0.07087 | 3.906
Tarraleah | 110 | 3.636 | 4.6329 | 0.02793 | 0.12862 | 4.605 | 0.02845 | 0.13215 | 4.645 | 0.0031 | 0.04336 | 13.983
Temco | 110 | 4.5203 | 5.1697 | 0.01015 | 0.10378 | 10.224 | 0.01032 | 0.10799 | 10.462 | 0.01005 | 0.06005 | 5.973
Trevallyn | 110 | 4.674 | 5.6144 | 0.01078 | 0.10208 | 9.473 | 0.0109 | 0.10562 | 9.693 | 0.00325 | 0.04745 | 14.614
Trevallyn | 22 | 7.1476 | 3.1545 | 0.01456 | 0.33529 | 23.024 | 0.01468 | 0.33883 | 23.076 | 0 | 1.6071 | >50
Triabunna | 110 | 1.2201 | 0.8872 | 0.24519 | 0.30594 | 1.248 | 0.24538 | 0.30863 | 1.258 | 0.31947 | 0.78556 | 2.459
Triabunna | 22 | 2.7472 | 1.238 | 0.26455 | 0.82097 | 3.103 | 0.26474 | 0.8242 | 3.113 | 0 | 4.0723 | >50
Tungatinah | 110 | 3.6672 | 4.8297 | 0.02735 | 0.1276 | 4.665 | 0.02787 | 0.13113 | 4.705 | 0.00124 | 0.03311 | 26.615
Tungatinah | 22 | 3.6247 | 1.1618 | 0.04775 | 0.6584 | 13.788 | 0.04827 | 0.66193 | 13.714 | 0 | 4.8574 | >50
Ulverstone | 110 | 1.9205 | 1.7839 | 0.05613 | 0.24564 | 4.376 | 0.05619 | 0.249 | 4.431 | 0.07491 | 0.29732 | 3.969
Ulverstone | 22 | 3.8734 | 1.6107 | 0.03906 | 0.60706 | 15.541 | 0.03925 | 0.61153 | 15.579 | 0 | 3.1694 | >50
Waddamana | 220 | 3.1399 | 3.743 | 0.0086 | 0.07565 | 8.795 | 0.00875 | 0.07799 | 8.91 | 0.0052 | 0.03663 | 7.044
Waddamana | 110 | 2.5665 | 2.4957 | 0.04368 | 0.18127 | 4.15 | 0.04439 | 0.18543 | 4.177 | 0.03577 | 0.19506 | 5.453
Waddamana | 22 | 1.455 | 1.8343 | 0.16272 | 1.6368 | 10.059 | 0.16302 | 1.6399 | 10.059 | 0 | 0.624 | >50
Warratah Tee | 110 | 1.5151 | 1.2458 | 0.06829 | 0.312 | 4.569 | 0.06836 | 0.31537 | 4.614 | 0.12566 | 0.50801 | 4.043
Wesley Vale | 110 | 2.4921 | 1.9821 | 0.03216 | 0.1915 | 5.954 | 0.03223 | 0.19486 | 6.047 | 0.0582 | 0.33577 | 5.77
Wesley Vale | 22 | 3.2 | 1.3 | 0.051 | 0.767 | 14.814 | 0.052 | 0.76 | 15.51 | 0 | 4.382 | >50
Notes on above minimum fault levels 1 The reactors installed on feeders from Emu Bay Substation to reduce maximum fault level (see notes 'Maximum' tab) also reduce the minimum fault level. The minimum fault currents on the feeders with the reactors in service and bus coupler closed are listed below:
Minimum fault levels
Bus | Voltage | Fault Level (kA) |  | Sequence Impedances in PU
Name [feeder number] | [kV] | 3 phase | 1 phase to ground | Positive |  |  | Negative |  |  | Zero
|  |  |  | R | X | X/R | R | X | X/R | R | X | X/R
Emu Bay [19] | 11 | 4.952 | 2.3489 | 0.03764 | 0.95318 | 25.3235 | 0.03783 | 0.95764 | 25.3142 | 0 | 4.0331 | >50
Emu Bay [20] | 11 | 4.997 | 2.3566 | 0.03764 | 0.94458 | 25.0951 | 0.03783 | 0.94904 | 25.087 | 0 | 4.0331 | >50
Emu Bay [21] | 11 | 4.997 | 2.3566 | 0.03764 | 0.94458 | 25.0951 | 0.03783 | 0.94904 | 25.087 | 0 | 4.0331 | >50
Emu Bay [23] | 11 | 4.997 | 2.3566 | 0.03764 | 0.94458 | 25.0951 | 0.03783 | 0.94904 | 25.087 | 0 | 4.0331 | >50
Emu Bay [24] | 11 | 4.9291 | 2.3449 | 0.03764 | 0.9576 | 25.4411 | 0.03783 | 0.96206 | 25.4313 | 0 | 4.0331 | >50