## Disclaimer
TasNetworks – Annual Planning Report 2019 – Supplementary Information
This information contained in this file forms part of TasNetworks Annual Planning Report 2019.
This Annual Planning Report (APR) has been prepared and published by Tasmanian Networks Pty Ltd (TasNetworks) solely for the purposes of TasNetworks’ compliance with regulatory obligations, including sections 5.12.2 and 5.13.2 of the National Electricity Rules and our transmission licence. The APR sets out network planning proposals, scenarios and forecasts as at the date of publication, which may change at any time or not eventuate. It has been prepared in good faith, including information and assumptions provided by third parties without further verification. It may not contain all information on the subject matter. Nothing in this APR should be taken as a recommendation in respect of any possible investment. Anyone considering using the information contained in this document should independently verify the currency, reliability, accuracy and completeness of the information. Accordingly, reliance should not be placed on the information contained in this document and TasNetworks makes no representation or warranty as to the reliability, accuracy or completeness of the information, or its suitability for any purpose other than the purpose for which it has been prepared. To the maximum extent permitted by law, TasNetworks, its employees, agents and consultants will have no liability for any loss or damage arising out of, or in connection with, the statements, opinions or other information in this document (including liability by reason of negligence or negligent misstatement).

## Assumptions + methodology
Tasmanian energy Tasmanian maximum demand | The data in these tabs is presented in Chapter 3 of this APR; specifically Figure 3-4 (Tasmanian energy) and Figure 3-5 (Tasmanian maximum demand). Our forecast methodology is presented in Section 3.2.2 of this APR.
Tx-Dx connection points Zone subs & sub-trans lines | Substation and sub-transmission line capacity - The substation (total or firm) capacity is generally the capacity of the supply transformers, however may be limited by substation terminal equipment. Generally, for transmission substations the short-term rating is the four-hour rating of the transformers. For zone substation supply transformers and sub-transmission lines we apply generic short-term overload capabilities of 30% and 20%, respectively. Maximum demand forecast - The methodology and assumptions used in developing the forecasts is presented in Section 6.2.2 of this APR. We do not forecast reactive power and power factor values - our forecast model uses the actual value from the preceeding year. As all zone substations are radially supplied, the zone substation maximum demand forecasts also apply to the sub-transmission lines supplying them. Hours exceeding - We forecast future load profiles by taking the preceeding year's load profile and growing it by the ratio of the forecast maximum demand of that profile to the recorded maximum demand of that profile. That is, if the maximum demand is forecast to grow at 1.1%pa, the energy is multiplied by 1.1%pa also. As all points on the load profile are forecast to grow at the same rate, the value of hours exceeding 95% of peak load will not grow over the forecast period (as that value also grows at the maximum demand growth rate). Load transfer capacity - The load transfer capacities show the capability of the distribution network for the load transer. They do not taken in account the capability of loading beyond the continuous rating of the supply transformer(s) at any given site and do not indicate long term period transfers but for periods of about one day. The analysis uses (in some cases) data from 2009, winter peak loadings, operational knowledge of past successful transfers, and medium-voltage limits (~6 per cent) tolerances. We do not currently forecast load transfer capacities unless for a specific study. Embedded generation capacity - The values provided are for known existing embedded generation. We do not currently forecast embedded generation capacity at connection point, sub-transmission or zone substation level. Individual embedded generating units over 0.5 MW are detailed in Appendix B of this APR.
Distribution line max. demand | The methodology and assumptions used in developing the distribution line maximum demand forecasts are detailed in Section 6.2.2 of this APR.

## Tasmanian energy
Tasmanian forecast energy, (GWh) 2019 forecast
| Actual | Fast growth scenaio | Neutral growth scenaio | Slow growth scenaio
Financial year | Energy generation scenario
| Actual | Fast growth | Neutral growth | Slow growth
2006-07 | 10738.7
2007-08 | 11008.3
2008-09 | 10964.2
2009–10 | 10846.6
2010–11 | 10912.9
2011–12 | 10529.4
2012–13 | 10518.8
2013–14 | 10466.2
2014–15 | 10477.3
2015–16 | 10357
2016–17 | 10398
2017–18 | 10776
2018–19 |  | 10862 | 10846 | 10831
2019–20 |  | 10920 | 10879 | 10430
2020–21 |  | 11013 | 10944 | 10461
2021–22 |  | 11126 | 11020 | 10495
2022–23 |  | 11225 | 10930 | 10408
2023–24 |  | 11291 | 10989 | 10261
2024–25 |  | 11395 | 11062 | 10276
2025–26 |  | 11406 | 10990 | 9519
2026–27 |  | 11547 | 10938 | 9531
2027–28 |  | 11698 | 11010 | 9542
2028–29 |  | 11826 | 11047 | 9548

## Tasmanian maximum demand
Tasmanian forecast maximum demand, (MW) 2019 forecast | [12 empty] | Fast growth scenario, 10% POE | Fast growth scenario, 50% POE | Fast growth scenario, 90% POE | Neutral growth scenario, 10% POE | Neutral growth scenario, 50% POE | Neutral growth scenario, 90% POE | Slow growth scenario, 10% POE | Slow growth scenario, 50% POE | Slow growth scenario, 90% POE
|  | Fast growth scenario, 10% POE | Fast growth scenario, 50% POE | Fast growth scenario, 90% POE | Neutral growth scenario, 10% POE | Neutral growth scenario, 50% POE | Neutral growth scenario, 90% POE | Slow growth scenario, 10% POE | Slow growth scenario, 50% POE | Slow growth scenario, 90% POE |  | Winter
| Summer | [10 empty] | Winter
Year | Actual | Fast growth |  |  | Neutral growth |  |  | Slow growth |  |  | Year | Actual | Fast growth |  |  | Neutral growth |  |  | Slow growth
|  | 10% POE | 50% POE | 90% POE | 10% POE | 50% POE | 90% POE | 10% POE | 50% POE | 90% POE |  |  | 10% POE | 50% POE | 90% POE | 10% POE | 50% POE | 90% POE | 10% POE | 50% POE | 90% POE
2006-07 | 1393.4 | [9 empty] | 2007 | 1802.5
2007-08 | 1425.1 | [9 empty] | 2008 | 1861
2008-09 | 1475.3 | [9 empty] | 2009 | 1752.6
2009–10 | 1403.8 | [9 empty] | 2010 | 1769.2
2010–11 | 1445.5 | [9 empty] | 2011 | 1794.8
2011-12 | 1408.8 | [9 empty] | 2012 | 1662.4
2012-13 | 1331.6 | [9 empty] | 2013 | 1703.1
2013-14 | 1366.8 | [9 empty] | 2014 | 1689.5
2014-15 | 1325.58 | [9 empty] | 2015 | 1752.1
2015-16 | 1348 | [9 empty] | 2016 | 1650.2
2016-17 | 1318.2834 | [9 empty] | 2017 | 1739.6
2017-18 | 1358.7649 | 1405.522 | 1377.709 | 1355.918 | 1404.533 | 1376.969 | 1355.804 | 1406.738 | 1377.017 | 1354.432 | 2018 | 1733.1 | 1767.8 | 1735 | 1700.5 | 1768.8 | 1731.2 | 1700.3 | 1771.9 | 1735.3 | 1699.6
2018-19 |  | 1417.901 | 1386.422 | 1364.461 | 1411.118 | 1384.293 | 1361.746 | 1411.321 | 1381.642 | 1360.037 | 2019 |  | 1785.1 | 1746.7 | 1713.6 | 1787 | 1744.4 | 1712 | 1777.1 | 1740.2 | 1710.7
2019-20 |  | 1427.925 | 1397.841 | 1375.784 | 1423.68 | 1391.941 | 1371.625 | 1360.685 | 1331.888 | 1308.489 | 2020 |  | 1801.5 | 1764.4 | 1730.2 | 1792 | 1756.7 | 1724.9 | 1729.3 | 1689.1 | 1656
2020-21 |  | 1440.055 | 1410.743 | 1389.228 | 1434.772 | 1402.417 | 1378.548 | 1365.905 | 1336.475 | 1313.228 | 2021 |  | 1815.8 | 1778.2 | 1745.4 | 1803.2 | 1766 | 1734.6 | 1732.2 | 1693.9 | 1660.5
2021-22 |  | 1457.813 | 1426.278 | 1403.364 | 1442.409 | 1411.175 | 1389.321 | 1371.054 | 1341.43 | 1318.37 | 2022 |  | 1827.8 | 1793.6 | 1758.6 | 1816 | 1775.8 | 1744.4 | 1736.8 | 1697.9 | 1666.5
2022-23 |  | 1466.366 | 1436.927 | 1412.947 | 1431.34 | 1400.18 | 1377.856 | 1361.371 | 1330.92 | 1307.324 | 2023 |  | 1841.9 | 1803.2 | 1772.4 | 1798.3 | 1761.3 | 1726.9 | 1720.2 | 1682 | 1650.4
2023-24 |  | 1472.622 | 1443.515 | 1419.629 | 1439.284 | 1406.615 | 1384.063 | 1341.04 | 1309.279 | 1288.102 | 2024 |  | 1855.2 | 1814 | 1781.8 | 1806.5 | 1769.6 | 1737.7 | 1697.1 | 1660.6 | 1630.2
2024-25 |  | 1485.903 | 1454.801 | 1431.341 | 1445.894 | 1416.049 | 1395.228 | 1345.157 | 1314.134 | 1290.977 | 2025 |  | 1868.2 | 1830.3 | 1797.2 | 1818.8 | 1779.2 | 1748 | 1698.6 | 1663.1 | 1629.7
2025-26 |  | 1484.908 | 1456.122 | 1432.77 | 1438.728 | 1406.932 | 1384.978 | 1245.521 | 1214.353 | 1189.86 | 2026 |  | 1869.9 | 1831.9 | 1796.9 | 1806.3 | 1768.2 | 1737.1 | 1584.8 | 1549.6 | 1520.1
2026-27 |  | 1503.845 | 1472.381 | 1448.979 | 1427.895 | 1399.256 | 1377.204 | 1249.206 | 1216.183 | 1192.576 | 2027 |  | 1888.9 | 1851.6 | 1820.2 | 1799 | 1760.5 | 1727.7 | 1588.8 | 1550.1 | 1520.6
2027-28 |  | 1516.676 | 1487.948 | 1464.785 | 1439.64 | 1409.733 | 1386.228 | 1246.753 | 1217.496 | 1196.388 | 2028 |  | 1913.3 | 1874.6 | 1840.9 | 1811.3 | 1772.9 | 1740.8 | 1592.8 | 1554 | 1522
2028-29 |  | 1536.002 | 1505.11 | 1483.138 | 1442.242 | 1415.098 | 1390.663 | 1250.655 | 1218.25 | 1196.628 | 2029 |  | 1935.5 | 1894.2 | 1861.3 | 1815 | 1779.3 | 1747.9 | 1592.5 | 1555.8 | 1524.6

## Tx-Dx connection points
[5 empty] | Planning area |  |  |  | Central
| Transmission-distribution connection point: |  |  |  | Supplying |  |  |  | Distribution lines
| Arthurs Lake[1] |  |  |  | Voltage |  |  |  | 110/6.6 kV
[5 empty] | Number of transformers |  |  |  | 1
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | ALSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Firm delivery | Substation capacity (winter and summer) (MVA) | ALSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | ALSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(peak season) | ALMaximum demand forecast(peak season)Maximum demand (MW) | 0.52148 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612
| Reactive power (coincident) (MVAr) | Maximum demand forecast(peak season) | ALMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.057384 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296
(Winter peak) | Maximum demand (MVA) | Maximum demand forecast(peak season) | ALMaximum demand forecast(peak season)Maximum demand (MVA) | 0.52463 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954
| Power factor (coincident) | Maximum demand forecast(peak season) | ALMaximum demand forecast(peak season)Power factor (coincident) | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
Maximum demand forecast | Maximum demand (MW) | Maximum demand forecast(non-peak season) | ALMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.025146 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554
(Summer) | Reactive power (coincident) (MVAr) | Maximum demand forecast(non-peak season) | ALMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.043047 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577
Hours exceeding | 95% of maximum demand | Hours exceeding | ALHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Regional diversity factor | Summer | Regional diversity factor | ALRegional diversity factorSummer | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103
| Winter | Regional diversity factor | ALRegional diversity factorWinter | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568
Load transfer capacity (MVA) | Wayatinah | Load transfer capacity (MVA)1 | ALLoad transfer capacity (MVA)1 | 0.1
|  | Load transfer capacity (MVA)2 | ALLoad transfer capacity (MVA)2
|  | Load transfer capacity (MVA)3 | ALLoad transfer capacity (MVA)3
|  | Load transfer capacity (MVA)4 | ALLoad transfer capacity (MVA)4
|  | Load transfer capacity (MVA)5 | ALLoad transfer capacity (MVA)5
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | ALEmbedded generation capacity (MVA)Units less than 100 kVA
| Units greater than 100 kVA | Embedded generation capacity (MVA) | ALEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.6
| Notes |  |  | [1] Arthurs Lake Substation supplies both distribution and generation-pump load customers. The distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity.
|  |  |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2028 | 2029
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | 0.52463 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 |  | 0.56954 | 0.56954

## T-D data (hidden)
[6 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 14
[6 empty] | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | Load transfer point | Non-peaking season | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Substation | Comment
Arthurs Lake[1] | AL | AL | Substation capacity (winter and summer) (MVA) | Total | ALSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | Arthurs Lake[1] | Central | Distribution lines | 110/6.6 kV | 1 | Winter | Arthurs Lake[1] | [1] Arthurs Lake Substation supplies both distribution and generation-pump load customers. The distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity.
Avoca | AV | AL | Substation capacity (winter and summer) (MVA) | Firm delivery | ALSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Avoca | Eastern | Distribution lines | 110/22 kV | 1 | Summer | Devonport | [1] Load reduction following planned transfer of load to Wesley Vale Substation, as detailed in Section 6.5.1 of this APR.
Bridgewater | BW | AL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ALSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Bridgewater | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Knights Road | [1] We propose to replace the supply transformers due to asset condition in 2024 with new units of standard size, as detailed in Section 6.10.3 of this APR.
Burnie | BU | AL | Maximum demand forecast(peak season) | Maximum demand (MW) | ALMaximum demand forecast(peak season)Maximum demand (MW) | 0.52148 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 | 0.56612 |  |  | Burnie | North West | Distribution lines | 110/22 kV | 2 | Winter | Lindisfarne | [1] We propose to replace the supply transformers due to asset condition by 2019 with new units of standard size, as detailed in Section 6.9.1 of this APR.
Chapel Street | CS | AL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.057384 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 | 0.062296 |  |  | Chapel Street | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter | Port Latta[1] | [1] Port Latta Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2022, with new standard units, as detailed in Section 6.5.3 of this APR.
Creek Road | CR | AL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ALMaximum demand forecast(peak season)Maximum demand (MVA) | 0.52463 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 |  |  | Creek Road | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter | Railton | [1] Substation was winter peaking in 2017, however is forecast to become summer peaking from 2018. [2] From summer 2022, load is forecast to exceed the firm rating of the substation, however will be addressed by the proposed connection point at Sheffield Substation, as detailed in Sections 6.5.2 and 6.5.4 of this APR. Note: AEMO did not prepare a forecast for the proposed connection point.
Derby | DE | AL | Maximum demand forecast(peak season) | Power factor (coincident) | ALMaximum demand forecast(peak season)Power factor (coincident) | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 | 0.994 |  |  | Derby | Northern | Distribution lines | 110/22 kV | 1 | Summer | Rosebery (44 kV)[1] | [1] Rosebery Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to install a third supply transformer in 2018 due to forecast increase in demand, as detaild in Section 6.4.2 of this APR. Note: the demand increase is from large customers and was not captured in AEMO's connection point forecast.
Derwent Bridge | DB | AL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ALMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.025146 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 | 0.036554 |  | Winter | Derwent Bridge | Central | Distribution lines | 110/22 kV | 1 | Winter | Savage River[1] | [1] Savage River Substation supplies both distribution and transmission-connected customers. For reasons of confidentiality, the distribution component only is shown for load forecast and hours exceeding 95% of peak load. Total substation load is used for hours exceeding firm capacity. [2] We propose to replace the supply transformers due to condition in 2025, with new standard units, as detailed in Section 6.4.3 of this APR.
Devonport | DP | AL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ALMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.043047 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 | 0.062577 |  | Winter | Devonport | North West | Distribution lines | 110/22 kV | 3 | Winter | St Marys | [1] Load exceeds substation firm rating, as detailed in Section 6.8.3.1 of this APR. However, we propose to replace the supply transformers due to condition in 2023, with new standard units providing sufficient capacity for the substation forecast load, detailed in Section 6.8.2 of this APR.
Electrona | EL | AL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ALMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.049853 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 |  | Winter | Electrona | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter | Tungatinah | [1] Supply transformer is rated to 25 MVA, but substation is limited to 13 MVA by bay conductor.
Emu Bay | EB | AL | Hours exceeding | 95% of maximum demand | ALHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | Emu Bay | North West | Distribution lines | 110/11 kV | 2 | Winter | Waddamana | [1] Waddamana transformer rated to 5 MVA, but substation is limited to 3.8 MVA by 22 kV combined voltage-current transformer.
George Town | GT | AL | Hours exceeding | Firm capacity (continuous rating) | ALHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | George Town | Northern | Distribution lines | 110/22 kV | 2 | Winter | Wesley Vale | [1] Planned conversion from 11 kV to 22 kV supply and associated load increase following transfer of load from Devonport Substation, as detailed in Section 6.5.1 of this APR. [2] Diversity factor assumed to be same as at Devonport Substation from 2017 following load transfer from Devonport Substation. This will be reviewed following next winter and summer periods.
Hadspen | HA | AL | Hours exceeding | Firm capacity (short-term rating) | ALHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Hadspen | Northern | Distribution lines | 110/22 kV | 2 | Winter
Huon River | HR | AL | Regional diversity factor | Summer | ALRegional diversity factorSummer | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 | 0.60103 |  |  | Huon River | Kingston-South | Distribution lines | 110/11 kV | 1 | Winter
Kermandie | KE | AL | Regional diversity factor | Winter | ALRegional diversity factorWinter | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 | 0.91568 |  |  | Kermandie | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Kingston (11 kV) | KI11 | AL | Load transfer capacity (MVA) | 1 | ALLoad transfer capacity (MVA)1 | 0.1 | [11 empty] | Wayatinah |  | Kingston (11 kV) | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Kingston (33 kV) | KI33 | AL | Load transfer capacity (MVA) | 2 | ALLoad transfer capacity (MVA)2 | [14 empty] | Kingston (33 kV) | Kingston-South | Sub-transmission lines | 110/33 kV | 2 | Winter
Knights Road | KR | AL | Load transfer capacity (MVA) | 3 | ALLoad transfer capacity (MVA)3 | [14 empty] | Knights Road | Kingston-South | Distribution lines | 110/11 kV | 2 | Winter
Lindisfarne | LF | AL | Load transfer capacity (MVA) | 4 | ALLoad transfer capacity (MVA)4 | [14 empty] | Lindisfarne | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Meadowbank | MB | AL | Load transfer capacity (MVA) | 5 | ALLoad transfer capacity (MVA)5 | [14 empty] | Meadowbank | Central | Distribution lines | 110/22 kV | 1 | Summer
Mornington | MT | AL | Embedded generation capacity (MVA) | Units less than 100 kVA | ALEmbedded generation capacity (MVA)Units less than 100 kVA | 0 | [13 empty] | Mornington | Greater Hobart | Sub-transmission lines | 110/33 kV | 2 | Winter
Mowbray | MY | AL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ALEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.6 | [13 empty] | Mowbray | Northern | Distribution lines | 110/22 kV | 2 | Winter
New Norfolk | NN | AV | Substation capacity (winter and summer) (MVA) | Total | AVSubstation capacity (winter and summer) (MVA)Total | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | New Norfolk | Central | Distribution lines | 110/22 kV | 2 | Winter
Newton | NT | AV | Substation capacity (winter and summer) (MVA) | Firm delivery | AVSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Newton | West Cost | Distribution lines | 110/22 kV | 1 | Summer
North Hobart | NH | AV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | AVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | North Hobart | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Norwood | NW | AV | Maximum demand forecast(peak season) | Maximum demand (MW) | AVMaximum demand forecast(peak season)Maximum demand (MW) | 6.9237 | 7.7097 | 7.653 | 7.5792 | 7.4017 | 7.3898 | 7.3912 | 7.3814 | 7.4922 | 7.5535 | 7.5308 | 7.5082 |  |  | Norwood | Northern | Distribution lines | 110/22 kV | 2 | Winter
Palmerston | PM | AV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.2634 | 2.5204 | 2.5018 | 2.4777 | 2.4197 | 2.4158 | 2.4162 | 2.413 | 2.4493 | 2.4693 | 2.4619 | 2.4545 |  |  | Palmerston | Northern | Distribution lines | 110/22 kV | 2 | Summer
Port Latta[1] | PL | AV | Maximum demand forecast(peak season) | Maximum demand (MVA) | AVMaximum demand forecast(peak season)Maximum demand (MVA) | 7.2843 | 8.1112 | 8.0515 | 7.974 | 7.7871 | 7.7747 | 7.7762 | 7.7659 | 7.8824 | 7.9468 | 7.923 | 7.8992 |  |  | Port Latta[1] | North West | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Summer
Queenstown | QT | AV | Maximum demand forecast(peak season) | Power factor (coincident) | AVMaximum demand forecast(peak season)Power factor (coincident) | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 |  |  | Queenstown | West Coast | Distribution lines | 110/22 kV | 2 | Winter
Railton | RA | AV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | AVMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.6566 | 6.0745 | 6.0494 | 6.0051 | 5.8935 | 5.8797 | 5.8563 | 5.8725 | 5.925 | 5.9869 | 5.9769 | 5.9669 |  | Winter | Railton | North West | Distribution lines | 110/22 kV | 2 | Summer
Risdon | RI | AV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | AVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.1975 | 1.0928 | 1.0883 | 1.0803 | 1.0603 | 1.0578 | 1.0536 | 1.0565 | 1.0659 | 1.0771 | 1.0753 | 1.0735 |  | Winter | Risdon | Greater Hobart | Sub-transmission lines | 110/33 kV | 3 | Winter
Rokeby | RK | AV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | AVMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.7635 | 6.172 | 6.1465 | 6.1015 | 5.9881 | 5.9741 | 5.9503 | 5.9668 | 6.0201 | 6.083 | 6.0729 | 6.0627 |  | Winter | Rokeby | Greater Hobart | Distribution lines | 110/11 kV | 2 | Winter
Rosebery (22 kV) | RB22 | AV | Hours exceeding | 95% of maximum demand | AVHours exceeding95% of maximum demand | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 |  |  | Rosebery (22 kV) | West Coast | Distribution lines | 44/22 kV | 2 | Winter
Rosebery (44 kV)[1] | RB44 | AV | Hours exceeding | Firm capacity (continuous rating) | AVHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Rosebery (44 kV)[1] | West Coast | Distribution lines and transmission-connected customer | 110/44 kV | 2 | Winter
Savage River[1] | SR | AV | Hours exceeding | Firm capacity (short-term rating) | AVHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 |  |  | Savage River[1] | West Coast | Distribution lines and transmission-connected customer | 110/22 kV | 2 | Winter
Scottsdale | SD | AV | Regional diversity factor | Summer | AVRegional diversity factorSummer | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 | 0.25754 |  |  | Scottsdale | Northern | Distribution lines | 110/22 kV | 2 | Summer
Smithton | ST | AV | Regional diversity factor | Winter | AVRegional diversity factorWinter | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 | 0.55044 |  |  | Smithton | North West | Distribution lines | 110/22 kV | 2 | Winter
Sorell | SO | AV | Load transfer capacity (MVA) | 1 | AVLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Palmerston |  | Sorell | Eastern | Distribution lines | 110/22 kV | 2 | Winter
St Leonards | SL | AV | Load transfer capacity (MVA) | 2 | AVLoad transfer capacity (MVA)2 | 4.6 | [11 empty] | St Marys |  | St Leonards | Northern | Distribution lines | 110/22 kV | 2 | Winter
St Marys | SM | AV | Load transfer capacity (MVA) | 3 | AVLoad transfer capacity (MVA)3 | [14 empty] | St Marys | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Trevallyn | TR | AV | Load transfer capacity (MVA) | 4 | AVLoad transfer capacity (MVA)4 | [14 empty] | Trevallyn | Northern | Distribution lines | 110/22 kV | 3 | Winter
Triabunna | TB | AV | Load transfer capacity (MVA) | 5 | AVLoad transfer capacity (MVA)5 | [14 empty] | Triabunna | Eastern | Distribution lines | 110/22 kV | 2 | Winter
Tungatinah | TU | AV | Embedded generation capacity (MVA) | Units less than 100 kVA | AVEmbedded generation capacity (MVA)Units less than 100 kVA | 0.5812 | [13 empty] | Tungatinah | Central | Distribution lines | 110/22 kV | 1 | Winter
Ulverstone | UL | AV | Embedded generation capacity (MVA) | Units greater than 100 kVA | AVEmbedded generation capacity (MVA)Units greater than 100 kVA | 5 | [13 empty] | Ulverstone | North West | Distribution lines | 110/22 kV | 2 | Winter
Waddamana | WA | BU | Substation capacity (winter and summer) (MVA) | Total | BUSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  |  | Waddamana | Central | Distribution lines | 110/22 kV | 1 | Winter
Wesley Vale | WV | BU | Substation capacity (winter and summer) (MVA) | Firm delivery | BUSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | Wesley Vale | North West | Distribution lines | 110/22 kV [1] | 2 | Winter
|  | BU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | BU | Maximum demand forecast(peak season) | Maximum demand (MW) | BUMaximum demand forecast(peak season)Maximum demand (MW) | 59.3003 | 56.8454 | 55.7983 | 54.8382 | 53.503 | 52.8893 | 52.2326 | 51.9699 | 52.0614 | 52.2655 | 52.2655 | 52.2655
|  | BU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 6.2453 | 5.9867 | 5.8764 | 5.7753 | 5.6347 | 5.5701 | 5.5009 | 5.4732 | 5.4829 | 5.5044 | 5.5044 | 5.5044
|  | BU | Maximum demand forecast(peak season) | Maximum demand (MVA) | BUMaximum demand forecast(peak season)Maximum demand (MVA) | 59.6283 | 57.1598 | 56.1069 | 55.1415 | 53.7989 | 53.1818 | 52.5215 | 52.2573 | 52.3493 | 52.5545 | 52.5545 | 52.5545
|  | BU | Maximum demand forecast(peak season) | Power factor (coincident) | BUMaximum demand forecast(peak season)Power factor (coincident) | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945 | 0.9945
|  | BU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BUMaximum demand forecast(non-peak season)Maximum demand (MW) | 40.064 | 41.1569 | 40.4246 | 39.7936 | 38.6915 | 38.1459 | 37.6676 | 37.1317 | 37.1954 | 37.0014 | 37.0014 | 37.0014 |  | Summer
|  | BU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 10.1803 | 10.458 | 10.2719 | 10.1116 | 9.8316 | 9.6929 | 9.5714 | 9.4352 | 9.4514 | 9.4021 | 9.4021 | 9.4021 |  | Summer
|  | BU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BUMaximum demand forecast(non-peak season)Maximum demand (MVA) | 41.3372 | 42.4649 | 41.7092 | 41.0582 | 39.921 | 39.3581 | 38.8646 | 38.3117 | 38.3774 | 38.1772 | 38.1772 | 38.1772 |  | Summer
|  | BU | Hours exceeding | 95% of maximum demand | BUHours exceeding95% of maximum demand | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
|  | BU | Hours exceeding | Firm capacity (continuous rating) | BUHours exceedingFirm capacity (continuous rating)
|  | BU | Hours exceeding | Firm capacity (short-term rating) | BUHours exceedingFirm capacity (short-term rating)
|  | BU | Regional diversity factor | Summer | BURegional diversity factorSummer | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533 | 0.93533
|  | BU | Regional diversity factor | Winter | BURegional diversity factorWinter | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006 | 0.99006
|  | BU | Load transfer capacity (MVA) | 1 | BULoad transfer capacity (MVA)1 | 8.8 | [11 empty] | Port Latta
|  | BU | Load transfer capacity (MVA) | 2 | BULoad transfer capacity (MVA)2 | 8.8 | [11 empty] | Ulverstone
|  | BU | Load transfer capacity (MVA) | 3 | BULoad transfer capacity (MVA)3
|  | BU | Load transfer capacity (MVA) | 4 | BULoad transfer capacity (MVA)4
|  | BU | Load transfer capacity (MVA) | 5 | BULoad transfer capacity (MVA)5
|  | BU | Embedded generation capacity (MVA) | Units less than 100 kVA | BUEmbedded generation capacity (MVA)Units less than 100 kVA | 7.5227
|  | BU | Embedded generation capacity (MVA) | Units greater than 100 kVA | BUEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.1353
|  | BW | Substation capacity (winter and summer) (MVA) | Total | BWSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | BW | Substation capacity (winter and summer) (MVA) | Firm delivery | BWSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | BW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | BW | Maximum demand forecast(peak season) | Maximum demand (MW) | BWMaximum demand forecast(peak season)Maximum demand (MW) | 33.6575 | 31.2372 | 30.8991 | 30.4654 | 29.6955 | 29.4232 | 29.1035 | 28.9811 | 29.0354 | 29.1321 | 28.8839 | 28.6378
|  | BW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.2867 | 2.1223 | 2.0993 | 2.0698 | 2.0175 | 1.999 | 1.9773 | 1.969 | 1.9727 | 1.9792 | 1.9624 | 1.9457
|  | BW | Maximum demand forecast(peak season) | Maximum demand (MVA) | BWMaximum demand forecast(peak season)Maximum demand (MVA) | 33.7351 | 31.3092 | 30.9703 | 30.5356 | 29.764 | 29.491 | 29.1706 | 29.048 | 29.1023 | 29.1992 | 28.9505 | 28.7038
|  | BW | Maximum demand forecast(peak season) | Power factor (coincident) | BWMaximum demand forecast(peak season)Power factor (coincident) | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977 | 0.9977
|  | BW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | BWMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.7318 | 20.1261 | 19.7842 | 19.4066 | 18.8315 | 18.6376 | 18.4905 | 18.3235 | 18.4571 | 18.4657 | 18.4657 | 18.4657 |  | Summer
|  | BW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | BWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.8513 | 1.6391 | 1.6113 | 1.5805 | 1.5337 | 1.5179 | 1.5059 | 1.4923 | 1.5032 | 1.5039 | 1.5039 | 1.5039 |  | Summer
|  | BW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BWMaximum demand forecast(non-peak season)Maximum demand (MVA) | 22.807 | 20.1928 | 19.8497 | 19.4709 | 18.8939 | 18.6993 | 18.5517 | 18.3842 | 18.5182 | 18.5268 | 18.5268 | 18.5268 |  | Summer
|  | BW | Hours exceeding | 95% of maximum demand | BWHours exceeding95% of maximum demand | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | BW | Hours exceeding | Firm capacity (continuous rating) | BWHours exceedingFirm capacity (continuous rating)
|  | BW | Hours exceeding | Firm capacity (short-term rating) | BWHours exceedingFirm capacity (short-term rating)
|  | BW | Regional diversity factor | Summer | BWRegional diversity factorSummer | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349 | 0.7349
|  | BW | Regional diversity factor | Winter | BWRegional diversity factorWinter | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045 | 0.5045
|  | BW | Load transfer capacity (MVA) | 1 | BWLoad transfer capacity (MVA)1 | 4.6 | [11 empty] | Claremont
|  | BW | Load transfer capacity (MVA) | 2 | BWLoad transfer capacity (MVA)2 | 3.1 | [11 empty] | Derwent Park
|  | BW | Load transfer capacity (MVA) | 3 | BWLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | New Norfolk
|  | BW | Load transfer capacity (MVA) | 4 | BWLoad transfer capacity (MVA)4
|  | BW | Load transfer capacity (MVA) | 5 | BWLoad transfer capacity (MVA)5
|  | BW | Embedded generation capacity (MVA) | Units less than 100 kVA | BWEmbedded generation capacity (MVA)Units less than 100 kVA | 5.0568
|  | BW | Embedded generation capacity (MVA) | Units greater than 100 kVA | BWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | CR | Substation capacity (winter and summer) (MVA) | Total | CRSubstation capacity (winter and summer) (MVA)Total | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | CR | Substation capacity (winter and summer) (MVA) | Firm delivery | CRSubstation capacity (winter and summer) (MVA)Firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | CR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
|  | CR | Maximum demand forecast(peak season) | Maximum demand (MW) | CRMaximum demand forecast(peak season)Maximum demand (MW) | 85.5949 | 94.8119 | 94.7782 | 94.7944 | 94.0692 | 94.5448 | 94.8835 | 95.8815 | 97.4865 | 99.2697 | 99.8274 | 100.3881
|  | CR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 16.1316 | 17.8687 | 17.8624 | 17.8654 | 17.7287 | 17.8184 | 17.8822 | 18.0703 | 18.3728 | 18.7089 | 18.814 | 18.9196
|  | CR | Maximum demand forecast(peak season) | Maximum demand (MVA) | CRMaximum demand forecast(peak season)Maximum demand (MVA) | 87.1018 | 96.481 | 96.4467 | 96.4632 | 95.7252 | 96.2092 | 96.5539 | 97.5695 | 99.2027 | 101.0173 | 101.5848 | 102.1554
|  | CR | Maximum demand forecast(peak season) | Power factor (coincident) | CRMaximum demand forecast(peak season)Power factor (coincident) | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827
|  | CR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CRMaximum demand forecast(non-peak season)Maximum demand (MW) | 56.9734 | 55.0542 | 55.089 | 55.0222 | 54.3233 | 54.4754 | 54.8103 | 55.1148 | 56.348 | 57.2244 | 57.7282 | 58.2365 |  | Summer
|  | CR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 7.9518 | 7.684 | 7.6888 | 7.6795 | 7.582 | 7.6032 | 7.6499 | 7.6924 | 7.8646 | 7.9869 | 8.0572 | 8.1281 |  | Summer
|  | CR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 57.5256 | 55.5878 | 55.623 | 55.5555 | 54.8499 | 55.0035 | 55.3416 | 55.649 | 56.8942 | 57.7791 | 58.2878 | 58.8009 |  | Summer
|  | CR | Hours exceeding | 95% of maximum demand | CRHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
|  | CR | Hours exceeding | Firm capacity (continuous rating) | CRHours exceedingFirm capacity (continuous rating)
|  | CR | Hours exceeding | Firm capacity (short-term rating) | CRHours exceedingFirm capacity (short-term rating)
|  | CR | Regional diversity factor | Summer | CRRegional diversity factorSummer | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109 | 0.81109
|  | CR | Regional diversity factor | Winter | CRRegional diversity factorWinter | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459 | 0.99459
|  | CR | Load transfer capacity (MVA) | 1 | CRLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont
|  | CR | Load transfer capacity (MVA) | 2 | CRLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park
|  | CR | Load transfer capacity (MVA) | 3 | CRLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town
|  | CR | Load transfer capacity (MVA) | 4 | CRLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart
|  | CR | Load transfer capacity (MVA) | 5 | CRLoad transfer capacity (MVA)5
|  | CR | Embedded generation capacity (MVA) | Units less than 100 kVA | CREmbedded generation capacity (MVA)Units less than 100 kVA | 7.2582
|  | CR | Embedded generation capacity (MVA) | Units greater than 100 kVA | CREmbedded generation capacity (MVA)Units greater than 100 kVA | 1.065
|  | CS | Substation capacity (winter and summer) (MVA) | Total | CSSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | CS | Substation capacity (winter and summer) (MVA) | Firm delivery | CSSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | CS | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CSSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | CS | Maximum demand forecast(peak season) | Maximum demand (MW) | CSMaximum demand forecast(peak season)Maximum demand (MW) | 40.0063 | 40.1206 | 40.1466 | 40.1923 | 39.9163 | 40.1363 | 40.2906 | 40.7199 | 41.4071 | 42.1693 | 42.4292 | 42.6906
|  | CS | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.0419 | 2.0478 | 2.0491 | 2.0514 | 2.0373 | 2.0486 | 2.0564 | 2.0783 | 2.1134 | 2.1523 | 2.1656 | 2.1789
|  | CS | Maximum demand forecast(peak season) | Maximum demand (MVA) | CSMaximum demand forecast(peak season)Maximum demand (MVA) | 40.0583 | 40.1729 | 40.1989 | 40.2447 | 39.9682 | 40.1886 | 40.343 | 40.7729 | 41.461 | 42.2242 | 42.4844 | 42.7462
|  | CS | Maximum demand forecast(peak season) | Power factor (coincident) | CSMaximum demand forecast(peak season)Power factor (coincident) | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987 | 0.9987
|  | CS | Maximum demand forecast(non-peak season) | Maximum demand (MW) | CSMaximum demand forecast(non-peak season)Maximum demand (MW) | 24.9603 | 24.1849 | 24.2082 | 24.1866 | 23.8866 | 23.9593 | 24.1109 | 24.2484 | 24.7941 | 25.1829 | 25.3672 | 25.5529 |  | Summer
|  | CS | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | CSMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.93442 | 0.90539 | 0.90626 | 0.90546 | 0.89422 | 0.89695 | 0.90262 | 0.90777 | 0.9282 | 0.94275 | 0.94965 | 0.9566 |  | Summer
|  | CS | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CSMaximum demand forecast(non-peak season)Maximum demand (MVA) | 24.9778 | 24.2019 | 24.2251 | 24.2035 | 23.9033 | 23.9761 | 24.1278 | 24.2654 | 24.8115 | 25.2006 | 25.385 | 25.5708 |  | Summer
|  | CS | Hours exceeding | 95% of maximum demand | CSHours exceeding95% of maximum demand | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  | CS | Hours exceeding | Firm capacity (continuous rating) | CSHours exceedingFirm capacity (continuous rating)
|  | CS | Hours exceeding | Firm capacity (short-term rating) | CSHours exceedingFirm capacity (short-term rating)
|  | CS | Regional diversity factor | Summer | CSRegional diversity factorSummer | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053 | 0.7053
|  | CS | Regional diversity factor | Winter | CSRegional diversity factorWinter | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349 | 0.89349
|  | CS | Load transfer capacity (MVA) | 1 | CSLoad transfer capacity (MVA)1 | 13 | [11 empty] | Claremont
|  | CS | Load transfer capacity (MVA) | 2 | CSLoad transfer capacity (MVA)2 | 13 | [11 empty] | Derwent Park
|  | CS | Load transfer capacity (MVA) | 3 | CSLoad transfer capacity (MVA)3 | 3.7 | [11 empty] | New Town
|  | CS | Load transfer capacity (MVA) | 4 | CSLoad transfer capacity (MVA)4 | 7.4 | [11 empty] | North Hobart
|  | CS | Load transfer capacity (MVA) | 5 | CSLoad transfer capacity (MVA)5
|  | CS | Embedded generation capacity (MVA) | Units less than 100 kVA | CSEmbedded generation capacity (MVA)Units less than 100 kVA | 3.8869
|  | CS | Embedded generation capacity (MVA) | Units greater than 100 kVA | CSEmbedded generation capacity (MVA)Units greater than 100 kVA | 1.69
|  | DB | Substation capacity (winter and summer) (MVA) | Total | DBSubstation capacity (winter and summer) (MVA)Total | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | DB | Substation capacity (winter and summer) (MVA) | Firm delivery | DBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DB | Maximum demand forecast(peak season) | Maximum demand (MW) | DBMaximum demand forecast(peak season)Maximum demand (MW) | 0.42658 | 0.28597 | 0.28495 | 0.28311 | 0.2782 | 0.27801 | 0.27749 | 0.27898 | 0.28234 | 0.28632 | 0.28635 | 0.28638
|  | DB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.037785 | 0.025331 | 0.02524 | 0.025077 | 0.024642 | 0.024625 | 0.024579 | 0.024711 | 0.025009 | 0.025361 | 0.025364 | 0.025367
|  | DB | Maximum demand forecast(peak season) | Maximum demand (MVA) | DBMaximum demand forecast(peak season)Maximum demand (MVA) | 0.42825 | 0.28709 | 0.28607 | 0.28422 | 0.27929 | 0.2791 | 0.27858 | 0.28008 | 0.28345 | 0.28744 | 0.28747 | 0.2875
|  | DB | Maximum demand forecast(peak season) | Power factor (coincident) | DBMaximum demand forecast(peak season)Power factor (coincident) | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961 | 0.9961
|  | DB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DBMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.35547 | 0.26166 | 0.25973 | 0.25723 | 0.25121 | 0.2508 | 0.25085 | 0.25052 | 0.25428 | 0.25636 | 0.25559 | 0.25482 |  | Summer
|  | DB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.0087091 | 0.0064108 | 0.0063636 | 0.0063023 | 0.0061546 | 0.0061448 | 0.006146 | 0.0061378 | 0.00623 | 0.0062809 | 0.006262 | 0.0062432 |  | Summer
|  | DB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.35558 | 0.26174 | 0.25981 | 0.25731 | 0.25128 | 0.25088 | 0.25093 | 0.2506 | 0.25436 | 0.25644 | 0.25566 | 0.2549 |  | Summer
|  | DB | Hours exceeding | 95% of maximum demand | DBHours exceeding95% of maximum demand | 1 | bar: 3 2019 to 13 2029
|  | DB | Hours exceeding | Firm capacity (continuous rating) | DBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DB | Hours exceeding | Firm capacity (short-term rating) | DBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DB | Regional diversity factor | Summer | DBRegional diversity factorSummer | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628 | 0.61628
|  | DB | Regional diversity factor | Winter | DBRegional diversity factorWinter | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DB | Load transfer capacity (MVA) | 1 | DBLoad transfer capacity (MVA)1
|  | DB | Load transfer capacity (MVA) | 2 | DBLoad transfer capacity (MVA)2
|  | DB | Load transfer capacity (MVA) | 3 | DBLoad transfer capacity (MVA)3
|  | DB | Load transfer capacity (MVA) | 4 | DBLoad transfer capacity (MVA)4
|  | DB | Load transfer capacity (MVA) | 5 | DBLoad transfer capacity (MVA)5
|  | DB | Embedded generation capacity (MVA) | Units less than 100 kVA | DBEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | DB | Embedded generation capacity (MVA) | Units greater than 100 kVA | DBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | DE | Substation capacity (winter and summer) (MVA) | Total | DESubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | DE | Substation capacity (winter and summer) (MVA) | Firm delivery | DESubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DE | Maximum demand forecast(peak season) | Maximum demand (MW) | DEMaximum demand forecast(peak season)Maximum demand (MW) | 6.707 | 6.1034 | 6.0544 | 5.9921 | 5.8479 | 5.8346 | 5.8318 | 5.8202 | 5.9037 | 5.9479 | 5.9261 | 5.9044
|  | DE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.951 | 1.7754 | 1.7612 | 1.7431 | 1.7011 | 1.6972 | 1.6964 | 1.6931 | 1.7173 | 1.7302 | 1.7239 | 1.7175
|  | DE | Maximum demand forecast(peak season) | Maximum demand (MVA) | DEMaximum demand forecast(peak season)Maximum demand (MVA) | 6.985 | 6.3564 | 6.3054 | 6.2405 | 6.0903 | 6.0765 | 6.0736 | 6.0615 | 6.1484 | 6.1945 | 6.1718 | 6.1491
|  | DE | Maximum demand forecast(peak season) | Power factor (coincident) | DEMaximum demand forecast(peak season)Power factor (coincident) | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602 | 0.9602
|  | DE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DEMaximum demand forecast(non-peak season)Maximum demand (MW) | 3.3279 | 2.9568 | 2.9433 | 2.9204 | 2.8651 | 2.8578 | 2.8461 | 2.8537 | 2.879 | 2.9089 | 2.9034 | 2.8978 |  | Winter
|  | DE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.85564 | 0.76023 | 0.75675 | 0.75088 | 0.73666 | 0.73478 | 0.73176 | 0.73373 | 0.74024 | 0.74793 | 0.74649 | 0.74506 |  | Winter
|  | DE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 3.4361 | 3.053 | 3.039 | 3.0154 | 2.9583 | 2.9508 | 2.9386 | 2.9466 | 2.9727 | 3.0036 | 2.9978 | 2.992 |  | Winter
|  | DE | Hours exceeding | 95% of maximum demand | DEHours exceeding95% of maximum demand | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
|  | DE | Hours exceeding | Firm capacity (continuous rating) | DEHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DE | Hours exceeding | Firm capacity (short-term rating) | DEHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | DE | Regional diversity factor | Summer | DERegional diversity factorSummer | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146 | 0.60146
|  | DE | Regional diversity factor | Winter | DERegional diversity factorWinter | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248 | 0.37248
|  | DE | Load transfer capacity (MVA) | 1 | DELoad transfer capacity (MVA)1 | 5.3 | [11 empty] | Scottsdale
|  | DE | Load transfer capacity (MVA) | 2 | DELoad transfer capacity (MVA)2 | 1.6 | [11 empty] | St Marys
|  | DE | Load transfer capacity (MVA) | 3 | DELoad transfer capacity (MVA)3
|  | DE | Load transfer capacity (MVA) | 4 | DELoad transfer capacity (MVA)4
|  | DE | Load transfer capacity (MVA) | 5 | DELoad transfer capacity (MVA)5
|  | DE | Embedded generation capacity (MVA) | Units less than 100 kVA | DEEmbedded generation capacity (MVA)Units less than 100 kVA | 0.62678
|  | DE | Embedded generation capacity (MVA) | Units greater than 100 kVA | DEEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.02
|  | DP | Substation capacity (winter and summer) (MVA) | Total | DPSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | DP | Substation capacity (winter and summer) (MVA) | Firm delivery | DPSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | DP | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | DP | Maximum demand forecast(peak season) | Maximum demand (MW) | DPMaximum demand forecast(peak season)Maximum demand (MW) | 57.8138 | 50.9104 | 50.3922 | 49.8758 | 49.3741 | 48.9011 | 48.4451 | 47.9999 | 47.5547 | 47.1111 | 46.6543 | 46.2019
|  | DP | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 7.2635 | 6.3962 | 6.3311 | 6.2662 | 6.2032 | 6.1438 | 6.0865 | 6.0305 | 5.9746 | 5.9189 | 5.8615 | 5.8046
|  | DP | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPMaximum demand forecast(peak season)Maximum demand (MVA) | 58.2683 | 51.3107 | 50.7883 | 50.2679 | 49.7623 | 49.2856 | 48.826 | 48.3773 | 47.9286 | 47.4815 | 47.0211 | 46.5651
|  | DP | Maximum demand forecast(peak season) | Power factor (coincident) | DPMaximum demand forecast(peak season)Power factor (coincident) | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922 | 0.9922
|  | DP | Maximum demand forecast(non-peak season) | Maximum demand (MW) | DPMaximum demand forecast(non-peak season)Maximum demand (MW) | 39.7326 | 31.3526 | 30.6632 | 30.0947 | 29.5863 | 29.169 | 28.8446 | 28.6085 | 28.4344 | 28.2968 | 28.2968 | 28.2968 |  | Summer
|  | DP | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | DPMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 9.4613 | 7.4658 | 7.3016 | 7.1662 | 7.0452 | 6.9458 | 6.8686 | 6.8124 | 6.7709 | 6.7381 | 6.7381 | 6.7381 |  | Summer
|  | DP | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPMaximum demand forecast(non-peak season)Maximum demand (MVA) | 40.8436 | 32.2292 | 31.5206 | 30.9361 | 30.4136 | 29.9845 | 29.6511 | 29.4084 | 29.2294 | 29.088 | 29.088 | 29.088 |  | Summer
|  | DP | Hours exceeding | 95% of maximum demand | DPHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | DP | Hours exceeding | Firm capacity (continuous rating) | DPHours exceedingFirm capacity (continuous rating)
|  | DP | Hours exceeding | Firm capacity (short-term rating) | DPHours exceedingFirm capacity (short-term rating)
|  | DP | Regional diversity factor | Summer | DPRegional diversity factorSummer | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414 | 0.89414
|  | DP | Regional diversity factor | Winter | DPRegional diversity factorWinter | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714 | 0.85714
|  | DP | Load transfer capacity (MVA) | 1 | DPLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Railton
|  | DP | Load transfer capacity (MVA) | 2 | DPLoad transfer capacity (MVA)2 | 6.3 | [11 empty] | Ulverstone
|  | DP | Load transfer capacity (MVA) | 3 | DPLoad transfer capacity (MVA)3
|  | DP | Load transfer capacity (MVA) | 4 | DPLoad transfer capacity (MVA)4
|  | DP | Load transfer capacity (MVA) | 5 | DPLoad transfer capacity (MVA)5
|  | DP | Embedded generation capacity (MVA) | Units less than 100 kVA | DPEmbedded generation capacity (MVA)Units less than 100 kVA | 5.2688
|  | DP | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.76689
|  | EB | Substation capacity (winter and summer) (MVA) | Total | EBSubstation capacity (winter and summer) (MVA)Total | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
|  | EB | Substation capacity (winter and summer) (MVA) | Firm delivery | EBSubstation capacity (winter and summer) (MVA)Firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
|  | EB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
|  | EB | Maximum demand forecast(peak season) | Maximum demand (MW) | EBMaximum demand forecast(peak season)Maximum demand (MW) | 8.8919 | 9.0152 | 8.9692 | 8.8951 | 8.7228 | 8.6985 | 8.6614 | 8.684 | 8.7602 | 8.8506 | 8.831 | 8.8114
|  | EB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.8333 | 2.8726 | 2.8579 | 2.8343 | 2.7794 | 2.7717 | 2.7598 | 2.767 | 2.7913 | 2.8201 | 2.8139 | 2.8077
|  | EB | Maximum demand forecast(peak season) | Maximum demand (MVA) | EBMaximum demand forecast(peak season)Maximum demand (MVA) | 9.3323 | 9.4618 | 9.4135 | 9.3357 | 9.155 | 9.1294 | 9.0904 | 9.1142 | 9.1942 | 9.289 | 9.2684 | 9.2479
|  | EB | Maximum demand forecast(peak season) | Power factor (coincident) | EBMaximum demand forecast(peak season)Power factor (coincident) | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528 | 0.9528
|  | EB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | EBMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.7029 | 7.1659 | 7.0866 | 6.9923 | 6.8055 | 6.7782 | 6.7697 | 6.755 | 6.8523 | 6.9043 | 6.8681 | 6.832 |  | Summer
|  | EB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | EBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 3.3688 | 3.6015 | 3.5616 | 3.5142 | 3.4204 | 3.4066 | 3.4024 | 3.395 | 3.4439 | 3.47 | 3.4518 | 3.4337 |  | Summer
|  | EB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EBMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.5018 | 8.02 | 7.9312 | 7.8257 | 7.6167 | 7.5861 | 7.5766 | 7.5602 | 7.669 | 7.7272 | 7.6867 | 7.6463 |  | Summer
|  | EB | Hours exceeding | 95% of maximum demand | EBHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | EB | Hours exceeding | Firm capacity (continuous rating) | EBHours exceedingFirm capacity (continuous rating)
|  | EB | Hours exceeding | Firm capacity (short-term rating) | EBHours exceedingFirm capacity (short-term rating)
|  | EB | Regional diversity factor | Summer | EBRegional diversity factorSummer | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292 | 0.6292
|  | EB | Regional diversity factor | Winter | EBRegional diversity factorWinter | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321 | 0.90321
|  | EB | Load transfer capacity (MVA) | 1 | EBLoad transfer capacity (MVA)1
|  | EB | Load transfer capacity (MVA) | 2 | EBLoad transfer capacity (MVA)2
|  | EB | Load transfer capacity (MVA) | 3 | EBLoad transfer capacity (MVA)3
|  | EB | Load transfer capacity (MVA) | 4 | EBLoad transfer capacity (MVA)4
|  | EB | Load transfer capacity (MVA) | 5 | EBLoad transfer capacity (MVA)5
|  | EB | Embedded generation capacity (MVA) | Units less than 100 kVA | EBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.39744
|  | EB | Embedded generation capacity (MVA) | Units greater than 100 kVA | EBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | EL | Substation capacity (winter and summer) (MVA) | Total | ELSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | EL | Substation capacity (winter and summer) (MVA) | Firm delivery | ELSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | EL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ELSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | EL | Maximum demand forecast(peak season) | Maximum demand (MW) | ELMaximum demand forecast(peak season)Maximum demand (MW) | 15.9065 | 14.1268 | 14.0266 | 13.9339 | 13.731 | 13.6998 | 13.646 | 13.6845 | 13.8077 | 13.9529 | 13.9302 | 13.9075
|  | EL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.5141 | 1.3447 | 1.3352 | 1.3264 | 1.3071 | 1.3041 | 1.299 | 1.3026 | 1.3144 | 1.3282 | 1.326 | 1.3239
|  | EL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ELMaximum demand forecast(peak season)Maximum demand (MVA) | 15.9784 | 14.1907 | 14.09 | 13.9969 | 13.7931 | 13.7617 | 13.7076 | 13.7464 | 13.8701 | 14.0159 | 13.9931 | 13.9703
|  | EL | Maximum demand forecast(peak season) | Power factor (coincident) | ELMaximum demand forecast(peak season)Power factor (coincident) | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955
|  | EL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ELMaximum demand forecast(non-peak season)Maximum demand (MW) | 11.0106 | 9.6446 | 9.7327 | 9.7768 | 9.6767 | 9.6898 | 9.6963 | 9.6617 | 9.7562 | 9.7556 | 9.7546 | 9.7537 |  | Summer
|  | EL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ELMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.2218 | 1.0702 | 1.08 | 1.0849 | 1.0737 | 1.0752 | 1.0759 | 1.0721 | 1.0826 | 1.0825 | 1.0824 | 1.0823 |  | Summer
|  | EL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | ELMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.0782 | 9.7038 | 9.7925 | 9.8368 | 9.7361 | 9.7493 | 9.7558 | 9.721 | 9.8161 | 9.8155 | 9.8145 | 9.8135 |  | Summer
|  | EL | Hours exceeding | 95% of maximum demand | ELHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | EL | Hours exceeding | Firm capacity (continuous rating) | ELHours exceedingFirm capacity (continuous rating)
|  | EL | Hours exceeding | Firm capacity (short-term rating) | ELHours exceedingFirm capacity (short-term rating)
|  | EL | Regional diversity factor | Summer | ELRegional diversity factorSummer | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268 | 0.74268
|  | EL | Regional diversity factor | Winter | ELRegional diversity factorWinter | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497 | 0.89497
|  | EL | Load transfer capacity (MVA) | 1 | ELLoad transfer capacity (MVA)1 | 8 | [11 empty] | Kingston
|  | EL | Load transfer capacity (MVA) | 2 | ELLoad transfer capacity (MVA)2 | 3 | [11 empty] | Knights Road
|  | EL | Load transfer capacity (MVA) | 3 | ELLoad transfer capacity (MVA)3
|  | EL | Load transfer capacity (MVA) | 4 | ELLoad transfer capacity (MVA)4
|  | EL | Load transfer capacity (MVA) | 5 | ELLoad transfer capacity (MVA)5
|  | EL | Embedded generation capacity (MVA) | Units less than 100 kVA | ELEmbedded generation capacity (MVA)Units less than 100 kVA | 4.3506
|  | EL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ELEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.2298
|  | GT | Substation capacity (winter and summer) (MVA) | Total | GTSubstation capacity (winter and summer) (MVA)Total | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
|  | GT | Substation capacity (winter and summer) (MVA) | Firm delivery | GTSubstation capacity (winter and summer) (MVA)Firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
|  | GT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
|  | GT | Maximum demand forecast(peak season) | Maximum demand (MW) | GTMaximum demand forecast(peak season)Maximum demand (MW) | 18.9815 | 18.7182 | 18.5854 | 18.4625 | 18.1938 | 18.1524 | 18.0811 | 18.1322 | 18.2953 | 18.4877 | 18.4576 | 18.4275
|  | GT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | GT | Maximum demand forecast(peak season) | Maximum demand (MVA) | GTMaximum demand forecast(peak season)Maximum demand (MVA) | 18.9815 | 18.7182 | 18.5854 | 18.4625 | 18.1938 | 18.1524 | 18.0811 | 18.1322 | 18.2953 | 18.4877 | 18.4576 | 18.4275
|  | GT | Maximum demand forecast(peak season) | Power factor (coincident) | GTMaximum demand forecast(peak season)Power factor (coincident) | 1 | bar: 3 2019 to 13 2029
|  | GT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | GTMaximum demand forecast(non-peak season)Maximum demand (MW) | 11.6675 | 12.9176 | 12.9011 | 12.8593 | 12.6622 | 12.6445 | 12.649 | 12.634 | 12.8253 | 12.9317 | 12.8973 | 12.863 |  | Summer
|  | GT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | GTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.3137 | 2.5616 | 2.5583 | 2.55 | 2.5109 | 2.5074 | 2.5083 | 2.5053 | 2.5433 | 2.5644 | 2.5575 | 2.5507 |  | Summer
|  | GT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GTMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.8947 | 13.1691 | 13.1523 | 13.1097 | 12.9088 | 12.8907 | 12.8953 | 12.88 | 13.075 | 13.1836 | 13.1485 | 13.1135 |  | Summer
|  | GT | Hours exceeding | 95% of maximum demand | GTHours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | GT | Hours exceeding | Firm capacity (continuous rating) | GTHours exceedingFirm capacity (continuous rating)
|  | GT | Hours exceeding | Firm capacity (short-term rating) | GTHours exceedingFirm capacity (short-term rating)
|  | GT | Regional diversity factor | Summer | GTRegional diversity factorSummer | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096 | 0.95096
|  | GT | Regional diversity factor | Winter | GTRegional diversity factorWinter | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151 | 0.95151
|  | GT | Load transfer capacity (MVA) | 1 | GTLoad transfer capacity (MVA)1 | 2.1 | [11 empty] | Mowbray
|  | GT | Load transfer capacity (MVA) | 2 | GTLoad transfer capacity (MVA)2 | 2.1 | [11 empty] | Scottsdale
|  | GT | Load transfer capacity (MVA) | 3 | GTLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn
|  | GT | Load transfer capacity (MVA) | 4 | GTLoad transfer capacity (MVA)4
|  | GT | Load transfer capacity (MVA) | 5 | GTLoad transfer capacity (MVA)5
|  | GT | Embedded generation capacity (MVA) | Units less than 100 kVA | GTEmbedded generation capacity (MVA)Units less than 100 kVA | 3.8522
|  | GT | Embedded generation capacity (MVA) | Units greater than 100 kVA | GTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | HA | Substation capacity (winter and summer) (MVA) | Total | HASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | HA | Substation capacity (winter and summer) (MVA) | Firm delivery | HASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | HA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | HA | Maximum demand forecast(peak season) | Maximum demand (MW) | HAMaximum demand forecast(peak season)Maximum demand (MW) | 53.2664 | 55.5529 | 55.1137 | 54.7058 | 53.8739 | 53.7304 | 53.5067 | 53.6509 | 54.1265 | 54.6894 | 54.5755 | 54.4618
|  | HA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 4.4037 | 4.5927 | 4.5564 | 4.5227 | 4.4539 | 4.4421 | 4.4236 | 4.4355 | 4.4748 | 4.5213 | 4.5119 | 4.5025
|  | HA | Maximum demand forecast(peak season) | Maximum demand (MVA) | HAMaximum demand forecast(peak season)Maximum demand (MVA) | 53.4481 | 55.7424 | 55.3018 | 54.8924 | 54.0577 | 53.9137 | 53.6892 | 53.834 | 54.3112 | 54.876 | 54.7617 | 54.6476
|  | HA | Maximum demand forecast(peak season) | Power factor (coincident) | HAMaximum demand forecast(peak season)Power factor (coincident) | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966
|  | HA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HAMaximum demand forecast(non-peak season)Maximum demand (MW) | 36.0185 | 40.2417 | 39.9382 | 39.5601 | 38.7329 | 38.52 | 38.4396 | 38.3392 | 38.8795 | 39.164 | 39.2565 | 39.3492 |  | Summer
|  | HA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 3.7933 | 4.2381 | 4.2061 | 4.1663 | 4.0792 | 4.0568 | 4.0483 | 4.0377 | 4.0946 | 4.1246 | 4.1343 | 4.1441 |  | Summer
|  | HA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HAMaximum demand forecast(non-peak season)Maximum demand (MVA) | 36.2176 | 40.4642 | 40.159 | 39.7789 | 38.9471 | 38.7331 | 38.6522 | 38.5512 | 39.0945 | 39.3806 | 39.4736 | 39.5669 |  | Summer
|  | HA | Hours exceeding | 95% of maximum demand | HAHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | HA | Hours exceeding | Firm capacity (continuous rating) | HAHours exceedingFirm capacity (continuous rating)
|  | HA | Hours exceeding | Firm capacity (short-term rating) | HAHours exceedingFirm capacity (short-term rating)
|  | HA | Regional diversity factor | Summer | HARegional diversity factorSummer | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984 | 0.83984
|  | HA | Regional diversity factor | Winter | HARegional diversity factorWinter | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938 | 0.92938
|  | HA | Load transfer capacity (MVA) | 1 | HALoad transfer capacity (MVA)1 | 13.4 | [11 empty] | Norwood
|  | HA | Load transfer capacity (MVA) | 2 | HALoad transfer capacity (MVA)2 | 5.3 | [11 empty] | Palmerston
|  | HA | Load transfer capacity (MVA) | 3 | HALoad transfer capacity (MVA)3 | 5.3 | [11 empty] | Railton
|  | HA | Load transfer capacity (MVA) | 4 | HALoad transfer capacity (MVA)4 | 26.7 | [11 empty] | Trevallyn
|  | HA | Load transfer capacity (MVA) | 5 | HALoad transfer capacity (MVA)5
|  | HA | Embedded generation capacity (MVA) | Units less than 100 kVA | HAEmbedded generation capacity (MVA)Units less than 100 kVA | 7.2165
|  | HA | Embedded generation capacity (MVA) | Units greater than 100 kVA | HAEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.4498
|  | HR | Substation capacity (winter and summer) (MVA) | Total | HRSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | HR | Substation capacity (winter and summer) (MVA) | Firm delivery | HRSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HR | Maximum demand forecast(peak season) | Maximum demand (MW) | HRMaximum demand forecast(peak season)Maximum demand (MW) | 1.6284 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252 | 1.5252
|  | HR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.90754 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005 | 0.85005
|  | HR | Maximum demand forecast(peak season) | Maximum demand (MVA) | HRMaximum demand forecast(peak season)Maximum demand (MVA) | 1.8642 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461
|  | HR | Maximum demand forecast(peak season) | Power factor (coincident) | HRMaximum demand forecast(peak season)Power factor (coincident) | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735 | 0.8735
|  | HR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | HRMaximum demand forecast(non-peak season)Maximum demand (MW) | 1.535 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 | 1.4701 |  | Summer
|  | HR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | HRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.9392 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 | 0.89949 |  | Summer
|  | HR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HRMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.7995 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 |  | Summer
|  | HR | Hours exceeding | 95% of maximum demand | HRHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | HR | Hours exceeding | Firm capacity (continuous rating) | HRHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | HR | Hours exceeding | Firm capacity (short-term rating) | HRHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | HR | Regional diversity factor | Summer | HRRegional diversity factorSummer | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189 | 0.81189
|  | HR | Regional diversity factor | Winter | HRRegional diversity factorWinter | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561 | 0.40561
|  | HR | Load transfer capacity (MVA) | 1 | HRLoad transfer capacity (MVA)1
|  | HR | Load transfer capacity (MVA) | 2 | HRLoad transfer capacity (MVA)2
|  | HR | Load transfer capacity (MVA) | 3 | HRLoad transfer capacity (MVA)3
|  | HR | Load transfer capacity (MVA) | 4 | HRLoad transfer capacity (MVA)4
|  | HR | Load transfer capacity (MVA) | 5 | HRLoad transfer capacity (MVA)5
|  | HR | Embedded generation capacity (MVA) | Units less than 100 kVA | HREmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | HR | Embedded generation capacity (MVA) | Units greater than 100 kVA | HREmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KE | Substation capacity (winter and summer) (MVA) | Total | KESubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | KE | Substation capacity (winter and summer) (MVA) | Firm delivery | KESubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | KE | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KESubstation capacity (winter and summer) (MVA)Short-term firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | KE | Maximum demand forecast(peak season) | Maximum demand (MW) | KEMaximum demand forecast(peak season)Maximum demand (MW) | 6.9842 | 6.6454 | 6.6179 | 6.5695 | 6.4474 | 6.4324 | 6.4067 | 6.4245 | 6.4819 | 6.5496 | 6.5387 | 6.5278
|  | KE | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.1854 | 1.1279 | 1.1233 | 1.115 | 1.0943 | 1.0918 | 1.0874 | 1.0904 | 1.1002 | 1.1117 | 1.1098 | 1.1079
|  | KE | Maximum demand forecast(peak season) | Maximum demand (MVA) | KEMaximum demand forecast(peak season)Maximum demand (MVA) | 7.0841 | 6.7404 | 6.7126 | 6.6634 | 6.5396 | 6.5244 | 6.4983 | 6.5163 | 6.5746 | 6.6433 | 6.6322 | 6.6211
|  | KE | Maximum demand forecast(peak season) | Power factor (coincident) | KEMaximum demand forecast(peak season)Power factor (coincident) | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859 | 0.9859
|  | KE | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KEMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.909 | 4.768 | 4.7619 | 4.7465 | 4.6737 | 4.6672 | 4.6689 | 4.6633 | 4.7339 | 4.7732 | 4.7605 | 4.7479 |  | Summer
|  | KE | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KEMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.80873 | 0.7855 | 0.78449 | 0.78195 | 0.76997 | 0.76889 | 0.76916 | 0.76825 | 0.77988 | 0.78636 | 0.78426 | 0.78217 |  | Summer
|  | KE | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KEMaximum demand forecast(non-peak season)Maximum demand (MVA) | 4.9752 | 4.8323 | 4.8261 | 4.8105 | 4.7367 | 4.7301 | 4.7318 | 4.7262 | 4.7977 | 4.8376 | 4.8247 | 4.8118 |  | Summer
|  | KE | Hours exceeding | 95% of maximum demand | KEHours exceeding95% of maximum demand | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
|  | KE | Hours exceeding | Firm capacity (continuous rating) | KEHours exceedingFirm capacity (continuous rating)
|  | KE | Hours exceeding | Firm capacity (short-term rating) | KEHours exceedingFirm capacity (short-term rating)
|  | KE | Regional diversity factor | Summer | KERegional diversity factorSummer | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888 | 0.84888
|  | KE | Regional diversity factor | Winter | KERegional diversity factorWinter | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406 | 0.85406
|  | KE | Load transfer capacity (MVA) | 1 | KELoad transfer capacity (MVA)1 | 4.4 | [11 empty] | Knights Road
|  | KE | Load transfer capacity (MVA) | 2 | KELoad transfer capacity (MVA)2
|  | KE | Load transfer capacity (MVA) | 3 | KELoad transfer capacity (MVA)3
|  | KE | Load transfer capacity (MVA) | 4 | KELoad transfer capacity (MVA)4
|  | KE | Load transfer capacity (MVA) | 5 | KELoad transfer capacity (MVA)5
|  | KE | Embedded generation capacity (MVA) | Units less than 100 kVA | KEEmbedded generation capacity (MVA)Units less than 100 kVA | 1.5525
|  | KE | Embedded generation capacity (MVA) | Units greater than 100 kVA | KEEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KI11 | Substation capacity (winter and summer) (MVA) | Total | KI11Substation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | KI11 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI11Substation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | KI11 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI11Substation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KI11 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI11Maximum demand forecast(peak season)Maximum demand (MW) | 23.3898 | 27.1625 | 26.7202 | 26.2855 | 25.637 | 25.3021 | 24.9099 | 24.6663 | 24.5464 | 24.4337 | 24.4337 | 24.4337
|  | KI11 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.99302 | 1.1532 | 1.1344 | 1.116 | 1.0884 | 1.0742 | 1.0576 | 1.0472 | 1.0421 | 1.0373 | 1.0373 | 1.0373
|  | KI11 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(peak season)Maximum demand (MVA) | 23.4109 | 27.187 | 26.7443 | 26.3092 | 25.6601 | 25.3249 | 24.9324 | 24.6885 | 24.5685 | 24.4558 | 24.4558 | 24.4558
|  | KI11 | Maximum demand forecast(peak season) | Power factor (coincident) | KI11Maximum demand forecast(peak season)Power factor (coincident) | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991 | 0.9991
|  | KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI11Maximum demand forecast(non-peak season)Maximum demand (MW) | 17.6007 | 14.995 | 14.8319 | 14.6418 | 14.2912 | 14.1806 | 14.1319 | 14.0838 | 14.2741 | 14.3708 | 14.2486 | 14.1274 |  | Summer
|  | KI11 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI11Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | KI11 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | KI11Maximum demand forecast(non-peak season)Maximum demand (MVA) | 17.6007 | 14.995 | 14.8319 | 14.6418 | 14.2912 | 14.1806 | 14.1319 | 14.0838 | 14.2741 | 14.3708 | 14.2486 | 14.1274 |  | Summer
|  | KI11 | Hours exceeding | 95% of maximum demand | KI11Hours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | KI11 | Hours exceeding | Firm capacity (continuous rating) | KI11Hours exceedingFirm capacity (continuous rating)
|  | KI11 | Hours exceeding | Firm capacity (short-term rating) | KI11Hours exceedingFirm capacity (short-term rating)
|  | KI11 | Regional diversity factor | Summer | KI11Regional diversity factorSummer | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377 | 0.74377
|  | KI11 | Regional diversity factor | Winter | KI11Regional diversity factorWinter | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028 | 0.99028
|  | KI11 | Load transfer capacity (MVA) | 1 | KI11Load transfer capacity (MVA)1 | 7.8 | [11 empty] | Electrona
|  | KI11 | Load transfer capacity (MVA) | 2 | KI11Load transfer capacity (MVA)2 | 3.1 | [11 empty] | Knights Road
|  | KI11 | Load transfer capacity (MVA) | 3 | KI11Load transfer capacity (MVA)3 | 1.6 | [11 empty] | Sandy Bay
|  | KI11 | Load transfer capacity (MVA) | 4 | KI11Load transfer capacity (MVA)4
|  | KI11 | Load transfer capacity (MVA) | 5 | KI11Load transfer capacity (MVA)5
|  | KI11 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI11Embedded generation capacity (MVA)Units less than 100 kVA | 3.8754
|  | KI11 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI11Embedded generation capacity (MVA)Units greater than 100 kVA | 0.30004
|  | KI33 | Substation capacity (winter and summer) (MVA) | Total | KI33Substation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | KI33 | Substation capacity (winter and summer) (MVA) | Firm delivery | KI33Substation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | KI33 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KI33Substation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | KI33 | Maximum demand forecast(peak season) | Maximum demand (MW) | KI33Maximum demand forecast(peak season)Maximum demand (MW) | 11.8533 | 11.7801 | 11.8628 | 11.9067 | 11.8164 | 11.9246 | 12.0152 | 12.1889 | 12.4395 | 12.713 | 12.8364 | 12.961
|  | KI33 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.99433 | 0.98819 | 0.99513 | 0.99881 | 0.99123 | 1.0003 | 1.0079 | 1.0225 | 1.0435 | 1.0665 | 1.0768 | 1.0873
|  | KI33 | Maximum demand forecast(peak season) | Maximum demand (MVA) | KI33Maximum demand forecast(peak season)Maximum demand (MVA) | 11.8949 | 11.8215 | 11.9045 | 11.9485 | 11.8579 | 11.9665 | 12.0574 | 12.2317 | 12.4832 | 12.7577 | 12.8815 | 13.0066
|  | KI33 | Maximum demand forecast(peak season) | Power factor (coincident) | KI33Maximum demand forecast(peak season)Power factor (coincident) | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965
|  | KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KI33Maximum demand forecast(non-peak season)Maximum demand (MW) | 7.0816 | 6.614 | 6.5629 | 6.5004 | 6.3643 | 6.3291 | 6.3158 | 6.2992 | 6.3879 | 6.4346 | 6.3914 | 6.3485 |  | Summer
|  | KI33 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KI33Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.24543 | 0.22922 | 0.22745 | 0.22528 | 0.22056 | 0.21935 | 0.21888 | 0.21831 | 0.22138 | 0.223 | 0.2215 | 0.22002 |  | Summer
|  | KI33 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 7.0859 | 6.618 | 6.5668 | 6.5044 | 6.3681 | 6.3329 | 6.3196 | 6.303 | 6.3918 | 6.4385 | 6.3952 | 6.3523 |  | Summer
|  | KI33 | Hours exceeding | 95% of maximum demand | KI33Hours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | KI33 | Hours exceeding | Firm capacity (continuous rating) | KI33Hours exceedingFirm capacity (continuous rating)
|  | KI33 | Hours exceeding | Firm capacity (short-term rating) | KI33Hours exceedingFirm capacity (short-term rating)
|  | KI33 | Regional diversity factor | Summer | KI33Regional diversity factorSummer | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791 | 0.791
|  | KI33 | Regional diversity factor | Winter | KI33Regional diversity factorWinter | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974 | 0.94974
|  | KI33 | Load transfer capacity (MVA) | 1 | KI33Load transfer capacity (MVA)1
|  | KI33 | Load transfer capacity (MVA) | 2 | KI33Load transfer capacity (MVA)2
|  | KI33 | Load transfer capacity (MVA) | 3 | KI33Load transfer capacity (MVA)3
|  | KI33 | Load transfer capacity (MVA) | 4 | KI33Load transfer capacity (MVA)4
|  | KI33 | Load transfer capacity (MVA) | 5 | KI33Load transfer capacity (MVA)5
|  | KI33 | Embedded generation capacity (MVA) | Units less than 100 kVA | KI33Embedded generation capacity (MVA)Units less than 100 kVA | 1.4112
|  | KI33 | Embedded generation capacity (MVA) | Units greater than 100 kVA | KI33Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | KR | Substation capacity (winter and summer) (MVA) | Total | KRSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50
|  | KR | Substation capacity (winter and summer) (MVA) | Firm delivery | KRSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25[1] | 25 | 25 | 25 | 25
|  | KR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | KRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 30 | 30 | 30 | 30 | 30
|  | KR | Maximum demand forecast(peak season) | Maximum demand (MW) | KRMaximum demand forecast(peak season)Maximum demand (MW) | 18.8029 | 18.3048 | 18.1489 | 18.0031 | 17.7155 | 17.6498 | 17.5552 | 17.5794 | 17.7119 | 17.8723 | 17.8176 | 17.763
|  | KR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.2714 | 3.1847 | 3.1576 | 3.1322 | 3.0822 | 3.0708 | 3.0543 | 3.0585 | 3.0816 | 3.1095 | 3.1 | 3.0905
|  | KR | Maximum demand forecast(peak season) | Maximum demand (MVA) | KRMaximum demand forecast(peak season)Maximum demand (MVA) | 19.0854 | 18.5798 | 18.4215 | 18.2735 | 17.9817 | 17.915 | 17.8189 | 17.8435 | 17.978 | 18.1408 | 18.0852 | 18.0298
|  | KR | Maximum demand forecast(peak season) | Power factor (coincident) | KRMaximum demand forecast(peak season)Power factor (coincident) | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852 | 0.9852
|  | KR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | KRMaximum demand forecast(non-peak season)Maximum demand (MW) | 15.1178 | 14.2116 | 14.2828 | 14.3294 | 14.2079 | 14.2977 | 14.4244 | 14.5365 | 14.8918 | 15.1537 | 15.23 | 15.3067 |  | Summer
|  | KR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | KRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.8335 | 4.5438 | 4.5666 | 4.5815 | 4.5426 | 4.5713 | 4.6118 | 4.6477 | 4.7613 | 4.845 | 4.8694 | 4.8939 |  | Summer
|  | KR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 15.8717 | 14.9203 | 14.995 | 15.044 | 14.9164 | 15.0107 | 15.1437 | 15.2614 | 15.6345 | 15.9094 | 15.9895 | 16.07 |  | Summer
|  | KR | Hours exceeding | 95% of maximum demand | KRHours exceeding95% of maximum demand | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
|  | KR | Hours exceeding | Firm capacity (continuous rating) | KRHours exceedingFirm capacity (continuous rating)
|  | KR | Hours exceeding | Firm capacity (short-term rating) | KRHours exceedingFirm capacity (short-term rating)
|  | KR | Regional diversity factor | Summer | KRRegional diversity factorSummer | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927 | 0.83927
|  | KR | Regional diversity factor | Winter | KRRegional diversity factorWinter | 1 | bar: 3 2019 to 13 2029
|  | KR | Load transfer capacity (MVA) | 1 | KRLoad transfer capacity (MVA)1 | 1.7 | [11 empty] | Electrona
|  | KR | Load transfer capacity (MVA) | 2 | KRLoad transfer capacity (MVA)2 | 3.4 | [11 empty] | Kermandie
|  | KR | Load transfer capacity (MVA) | 3 | KRLoad transfer capacity (MVA)3 | 1.7 | [11 empty] | Kingston
|  | KR | Load transfer capacity (MVA) | 4 | KRLoad transfer capacity (MVA)4
|  | KR | Load transfer capacity (MVA) | 5 | KRLoad transfer capacity (MVA)5
|  | KR | Embedded generation capacity (MVA) | Units less than 100 kVA | KREmbedded generation capacity (MVA)Units less than 100 kVA | 3.772
|  | KR | Embedded generation capacity (MVA) | Units greater than 100 kVA | KREmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | LF | Substation capacity (winter and summer) (MVA) | Total | LFSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 120[1] | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | LF | Substation capacity (winter and summer) (MVA) | Firm delivery | LFSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | LF | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | LFSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | LF | Maximum demand forecast(peak season) | Maximum demand (MW) | LFMaximum demand forecast(peak season)Maximum demand (MW) | 36.1027 | 38.1319 | 37.6364 | 37.1659 | 36.4129 | 36.1307 | 35.7973 | 35.7117 | 35.8455 | 36.0345 | 35.776 | 35.5193
|  | LF | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.4748 | 3.6702 | 3.6225 | 3.5772 | 3.5047 | 3.4775 | 3.4455 | 3.4372 | 3.4501 | 3.4683 | 3.4434 | 3.4187
|  | LF | Maximum demand forecast(peak season) | Maximum demand (MVA) | LFMaximum demand forecast(peak season)Maximum demand (MVA) | 36.2695 | 38.3081 | 37.8103 | 37.3376 | 36.5812 | 36.2976 | 35.9627 | 35.8768 | 36.0111 | 36.201 | 35.9413 | 35.6834
|  | LF | Maximum demand forecast(peak season) | Power factor (coincident) | LFMaximum demand forecast(peak season)Power factor (coincident) | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954
|  | LF | Maximum demand forecast(non-peak season) | Maximum demand (MW) | LFMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.9677 | 21.5582 | 21.3294 | 21.0611 | 20.5513 | 20.3586 | 20.2254 | 20.0757 | 20.2582 | 20.3053 | 20.3053 | 20.3053 |  | Summer
|  | LF | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | LFMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.0279 | 0.96484 | 0.95459 | 0.94259 | 0.91977 | 0.91115 | 0.90519 | 0.89849 | 0.90666 | 0.90876 | 0.90876 | 0.90876 |  | Summer
|  | LF | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.9907 | 21.5798 | 21.3507 | 21.0822 | 20.5719 | 20.3789 | 20.2456 | 20.0958 | 20.2785 | 20.3256 | 20.3256 | 20.3256 |  | Summer
|  | LF | Hours exceeding | 95% of maximum demand | LFHours exceeding95% of maximum demand | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  | LF | Hours exceeding | Firm capacity (continuous rating) | LFHours exceedingFirm capacity (continuous rating)
|  | LF | Hours exceeding | Firm capacity (short-term rating) | LFHours exceedingFirm capacity (short-term rating)
|  | LF | Regional diversity factor | Summer | LFRegional diversity factorSummer | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068 | 0.78068
|  | LF | Regional diversity factor | Winter | LFRegional diversity factorWinter | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481 | 0.97481
|  | LF | Load transfer capacity (MVA) | 1 | LFLoad transfer capacity (MVA)1
|  | LF | Load transfer capacity (MVA) | 2 | LFLoad transfer capacity (MVA)2
|  | LF | Load transfer capacity (MVA) | 3 | LFLoad transfer capacity (MVA)3
|  | LF | Load transfer capacity (MVA) | 4 | LFLoad transfer capacity (MVA)4
|  | LF | Load transfer capacity (MVA) | 5 | LFLoad transfer capacity (MVA)5
|  | LF | Embedded generation capacity (MVA) | Units less than 100 kVA | LFEmbedded generation capacity (MVA)Units less than 100 kVA | 3.7019
|  | LF | Embedded generation capacity (MVA) | Units greater than 100 kVA | LFEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.1
|  | MB | Substation capacity (winter and summer) (MVA) | Total | MBSubstation capacity (winter and summer) (MVA)Total | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | MB | Substation capacity (winter and summer) (MVA) | Firm delivery | MBSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MB | Maximum demand forecast(peak season) | Maximum demand (MW) | MBMaximum demand forecast(peak season)Maximum demand (MW) | 6.6929 | 8.249 | 8.4458 | 8.6159 | 8.6547 | 8.8753 | 9.1051 | 9.3139 | 9.6707 | 9.9608 | 10.1984 | 10.4416
|  | MB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.493 | 3.0727 | 3.146 | 3.2093 | 3.2238 | 3.306 | 3.3916 | 3.4694 | 3.6022 | 3.7103 | 3.7988 | 3.8894
|  | MB | Maximum demand forecast(peak season) | Maximum demand (MVA) | MBMaximum demand forecast(peak season)Maximum demand (MVA) | 7.1421 | 8.8027 | 9.0127 | 9.1942 | 9.2356 | 9.471 | 9.7163 | 9.9391 | 10.3198 | 10.6294 | 10.8829 | 11.1425
|  | MB | Maximum demand forecast(peak season) | Power factor (coincident) | MBMaximum demand forecast(peak season)Power factor (coincident) | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371 | 0.9371
|  | MB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MBMaximum demand forecast(non-peak season)Maximum demand (MW) | 5.9995 | 4.8423 | 4.8623 | 4.8664 | 4.815 | 4.8427 | 4.8622 | 4.9145 | 4.9976 | 5.0895 | 5.1222 | 5.1551 |  | Winter
|  | MB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.91374 | 0.73749 | 0.74054 | 0.74117 | 0.73334 | 0.73755 | 0.74052 | 0.74849 | 0.76115 | 0.77514 | 0.78012 | 0.78513 |  | Winter
|  | MB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 6.0687 | 4.8981 | 4.9184 | 4.9226 | 4.8705 | 4.8986 | 4.9182 | 4.9712 | 5.0553 | 5.1482 | 5.1812 | 5.2145 |  | Winter
|  | MB | Hours exceeding | 95% of maximum demand | MBHours exceeding95% of maximum demand | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  | MB | Hours exceeding | Firm capacity (continuous rating) | MBHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | MB | Hours exceeding | Firm capacity (short-term rating) | MBHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | MB | Regional diversity factor | Summer | MBRegional diversity factorSummer | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588 | 0.70588
|  | MB | Regional diversity factor | Winter | MBRegional diversity factorWinter | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194 | 0.4194
|  | MB | Load transfer capacity (MVA) | 1 | MBLoad transfer capacity (MVA)1 | 3.4 | [11 empty] | New Norfolk
|  | MB | Load transfer capacity (MVA) | 2 | MBLoad transfer capacity (MVA)2 | 4.9 | [11 empty] | Wayatinah
|  | MB | Load transfer capacity (MVA) | 3 | MBLoad transfer capacity (MVA)3
|  | MB | Load transfer capacity (MVA) | 4 | MBLoad transfer capacity (MVA)4
|  | MB | Load transfer capacity (MVA) | 5 | MBLoad transfer capacity (MVA)5
|  | MB | Embedded generation capacity (MVA) | Units less than 100 kVA | MBEmbedded generation capacity (MVA)Units less than 100 kVA | 0.391
|  | MB | Embedded generation capacity (MVA) | Units greater than 100 kVA | MBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.2
|  | MT | Substation capacity (winter and summer) (MVA) | Total | MTSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | MT | Substation capacity (winter and summer) (MVA) | Firm delivery | MTSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | MT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | MT | Maximum demand forecast(peak season) | Maximum demand (MW) | MTMaximum demand forecast(peak season)Maximum demand (MW) | 38.8648 | 41.3237 | 41.4522 | 41.449 | 40.9813 | 41.2007 | 41.3586 | 41.8028 | 42.5116 | 43.2982 | 43.5557 | 43.8147
|  | MT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.2131 | 3.4164 | 3.427 | 3.4267 | 3.388 | 3.4062 | 3.4192 | 3.456 | 3.5146 | 3.5796 | 3.6009 | 3.6223
|  | MT | Maximum demand forecast(peak season) | Maximum demand (MVA) | MTMaximum demand forecast(peak season)Maximum demand (MVA) | 38.9974 | 41.4647 | 41.5936 | 41.5904 | 41.1211 | 41.3412 | 41.4997 | 41.9454 | 42.6566 | 43.4459 | 43.7043 | 43.9642
|  | MT | Maximum demand forecast(peak season) | Power factor (coincident) | MTMaximum demand forecast(peak season)Power factor (coincident) | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966
|  | MT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MTMaximum demand forecast(non-peak season)Maximum demand (MW) | 27.7111 | 28.5275 | 28.5533 | 28.5266 | 28.1727 | 28.2617 | 28.4473 | 28.6182 | 29.272 | 29.741 | 29.8035 | 29.8662 |  | Summer
|  | MT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.87663 | 0.90246 | 0.90327 | 0.90243 | 0.89123 | 0.89405 | 0.89992 | 0.90533 | 0.92601 | 0.94084 | 0.94282 | 0.94481 |  | Summer
|  | MT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 27.725 | 28.5418 | 28.5676 | 28.5408 | 28.1868 | 28.2759 | 28.4615 | 28.6325 | 29.2867 | 29.7558 | 29.8184 | 29.8811 |  | Summer
|  | MT | Hours exceeding | 95% of maximum demand | MTHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  | MT | Hours exceeding | Firm capacity (continuous rating) | MTHours exceedingFirm capacity (continuous rating)
|  | MT | Hours exceeding | Firm capacity (short-term rating) | MTHours exceedingFirm capacity (short-term rating)
|  | MT | Regional diversity factor | Summer | MTRegional diversity factorSummer | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517 | 0.69517
|  | MT | Regional diversity factor | Winter | MTRegional diversity factorWinter | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035 | 0.95035
|  | MT | Load transfer capacity (MVA) | 1 | MTLoad transfer capacity (MVA)1
|  | MT | Load transfer capacity (MVA) | 2 | MTLoad transfer capacity (MVA)2
|  | MT | Load transfer capacity (MVA) | 3 | MTLoad transfer capacity (MVA)3
|  | MT | Load transfer capacity (MVA) | 4 | MTLoad transfer capacity (MVA)4
|  | MT | Load transfer capacity (MVA) | 5 | MTLoad transfer capacity (MVA)5
|  | MT | Embedded generation capacity (MVA) | Units less than 100 kVA | MTEmbedded generation capacity (MVA)Units less than 100 kVA | 4.5985
|  | MT | Embedded generation capacity (MVA) | Units greater than 100 kVA | MTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | MY | Substation capacity (winter and summer) (MVA) | Total | MYSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | MY | Substation capacity (winter and summer) (MVA) | Firm delivery | MYSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | MY | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | MYSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | MY | Maximum demand forecast(peak season) | Maximum demand (MW) | MYMaximum demand forecast(peak season)Maximum demand (MW) | 36.3895 | 40.7163 | 40.4915 | 40.1402 | 39.3496 | 39.2352 | 39.0693 | 39.1722 | 39.5169 | 39.9253 | 39.8298 | 39.7345
|  | MY | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 5.3665 | 6.0046 | 5.9714 | 5.9196 | 5.803 | 5.7862 | 5.7617 | 5.7769 | 5.8277 | 5.8879 | 5.8738 | 5.8598
|  | MY | Maximum demand forecast(peak season) | Maximum demand (MVA) | MYMaximum demand forecast(peak season)Maximum demand (MVA) | 36.7831 | 41.1566 | 40.9295 | 40.5744 | 39.7752 | 39.6595 | 39.4919 | 39.5959 | 39.9444 | 40.3571 | 40.2606 | 40.1643
|  | MY | Maximum demand forecast(peak season) | Power factor (coincident) | MYMaximum demand forecast(peak season)Power factor (coincident) | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893 | 0.9893
|  | MY | Maximum demand forecast(non-peak season) | Maximum demand (MW) | MYMaximum demand forecast(non-peak season)Maximum demand (MW) | 20.5933 | 21.8268 | 21.353 | 20.9842 | 20.4603 | 20.3409 | 20.3706 | 20.4706 | 20.9985 | 21.4777 | 21.6023 | 21.7276 |  | Summer
|  | MY | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | MYMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 5.4945 | 5.8236 | 5.6972 | 5.5988 | 5.459 | 5.4272 | 5.4351 | 5.4618 | 5.6027 | 5.7305 | 5.7637 | 5.7972 |  | Summer
|  | MY | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 21.3137 | 22.5903 | 22.1 | 21.7183 | 21.176 | 21.0525 | 21.0832 | 21.1868 | 21.7331 | 22.229 | 22.358 | 22.4876 |  | Summer
|  | MY | Hours exceeding | 95% of maximum demand | MYHours exceeding95% of maximum demand | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
|  | MY | Hours exceeding | Firm capacity (continuous rating) | MYHours exceedingFirm capacity (continuous rating)
|  | MY | Hours exceeding | Firm capacity (short-term rating) | MYHours exceedingFirm capacity (short-term rating)
|  | MY | Regional diversity factor | Summer | MYRegional diversity factorSummer | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445 | 0.84445
|  | MY | Regional diversity factor | Winter | MYRegional diversity factorWinter | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772 | 0.97772
|  | MY | Load transfer capacity (MVA) | 1 | MYLoad transfer capacity (MVA)1 | 6.3 | [11 empty] | Norwood
|  | MY | Load transfer capacity (MVA) | 2 | MYLoad transfer capacity (MVA)2 | 31.4 | [11 empty] | Trevallyn
|  | MY | Load transfer capacity (MVA) | 3 | MYLoad transfer capacity (MVA)3
|  | MY | Load transfer capacity (MVA) | 4 | MYLoad transfer capacity (MVA)4
|  | MY | Load transfer capacity (MVA) | 5 | MYLoad transfer capacity (MVA)5
|  | MY | Embedded generation capacity (MVA) | Units less than 100 kVA | MYEmbedded generation capacity (MVA)Units less than 100 kVA | 3.006
|  | MY | Embedded generation capacity (MVA) | Units greater than 100 kVA | MYEmbedded generation capacity (MVA)Units greater than 100 kVA | 2.2
|  | NH | Substation capacity (winter and summer) (MVA) | Total | NHSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | NH | Substation capacity (winter and summer) (MVA) | Firm delivery | NHSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  | NH | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NHSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | NH | Maximum demand forecast(peak season) | Maximum demand (MW) | NHMaximum demand forecast(peak season)Maximum demand (MW) | 35.1408 | 34.6096 | 35.0796 | 35.0401 | 34.6172 | 34.7916 | 34.9239 | 35.3041 | 35.908 | 36.5786 | 36.8272 | 37.0775
|  | NH | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 7.6698 | 7.5539 | 7.6564 | 7.6478 | 7.5555 | 7.5936 | 7.6225 | 7.7054 | 7.8372 | 7.9836 | 8.0379 | 8.0925
|  | NH | Maximum demand forecast(peak season) | Maximum demand (MVA) | NHMaximum demand forecast(peak season)Maximum demand (MVA) | 35.9681 | 35.4243 | 35.9054 | 35.865 | 35.4321 | 35.6106 | 35.746 | 36.1352 | 36.7533 | 37.4397 | 37.6942 | 37.9504
|  | NH | Maximum demand forecast(peak season) | Power factor (coincident) | NHMaximum demand forecast(peak season)Power factor (coincident) | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977 | 0.977
|  | NH | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NHMaximum demand forecast(non-peak season)Maximum demand (MW) | 22.6397 | 21.3639 | 21.8348 | 21.8421 | 21.5965 | 21.6851 | 21.8425 | 21.9855 | 22.4984 | 22.8693 | 22.8053 | 22.7415 |  | Summer
|  | NH | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NHMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 5.422 | 5.1164 | 5.2292 | 5.2309 | 5.1721 | 5.1933 | 5.231 | 5.2653 | 5.3881 | 5.477 | 5.4616 | 5.4463 |  | Summer
|  | NH | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 23.2799 | 21.9681 | 22.4522 | 22.4597 | 22.2072 | 22.2983 | 22.4601 | 22.6072 | 23.1346 | 23.516 | 23.4502 | 23.3846 |  | Summer
|  | NH | Hours exceeding | 95% of maximum demand | NHHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | NH | Hours exceeding | Firm capacity (continuous rating) | NHHours exceedingFirm capacity (continuous rating)
|  | NH | Hours exceeding | Firm capacity (short-term rating) | NHHours exceedingFirm capacity (short-term rating)
|  | NH | Regional diversity factor | Summer | NHRegional diversity factorSummer | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015 | 0.8015
|  | NH | Regional diversity factor | Winter | NHRegional diversity factorWinter | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736 | 0.98736
|  | NH | Load transfer capacity (MVA) | 1 | NHLoad transfer capacity (MVA)1 | 9.8 | [11 empty] | Chapel Street
|  | NH | Load transfer capacity (MVA) | 2 | NHLoad transfer capacity (MVA)2 | 14.6 | [11 empty] | East Hobart
|  | NH | Load transfer capacity (MVA) | 3 | NHLoad transfer capacity (MVA)3 | 9.8 | [11 empty] | New Town
|  | NH | Load transfer capacity (MVA) | 4 | NHLoad transfer capacity (MVA)4 | 14.6 | [11 empty] | West Hobart
|  | NH | Load transfer capacity (MVA) | 5 | NHLoad transfer capacity (MVA)5
|  | NH | Embedded generation capacity (MVA) | Units less than 100 kVA | NHEmbedded generation capacity (MVA)Units less than 100 kVA | 2.5519
|  | NH | Embedded generation capacity (MVA) | Units greater than 100 kVA | NHEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | NN | Substation capacity (winter and summer) (MVA) | Total | NNSubstation capacity (winter and summer) (MVA)Total | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | NN | Substation capacity (winter and summer) (MVA) | Firm delivery | NNSubstation capacity (winter and summer) (MVA)Firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | NN | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NNSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | NN | Maximum demand forecast(peak season) | Maximum demand (MW) | NNMaximum demand forecast(peak season)Maximum demand (MW) | 17.8945 | 16.7002 | 16.6312 | 16.5094 | 16.2026 | 16.1648 | 16.1004 | 16.145 | 16.2892 | 16.4595 | 16.432 | 16.4046
|  | NN | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.7856 | 2.5996 | 2.5889 | 2.5699 | 2.5222 | 2.5163 | 2.5063 | 2.5132 | 2.5357 | 2.5622 | 2.5579 | 2.5536
|  | NN | Maximum demand forecast(peak season) | Maximum demand (MVA) | NNMaximum demand forecast(peak season)Maximum demand (MVA) | 18.11 | 16.9013 | 16.8315 | 16.7082 | 16.3977 | 16.3595 | 16.2943 | 16.3394 | 16.4854 | 16.6578 | 16.6299 | 16.6021
|  | NN | Maximum demand forecast(peak season) | Power factor (coincident) | NNMaximum demand forecast(peak season)Power factor (coincident) | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881
|  | NN | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NNMaximum demand forecast(non-peak season)Maximum demand (MW) | 17.1816 | 12.4583 | 12.3555 | 12.2256 | 11.9296 | 11.9036 | 11.9017 | 11.8836 | 12.0602 | 12.1571 | 12.114 | 12.0711 |  | Summer
|  | NN | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NNMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.9712 | 3.6046 | 3.5749 | 3.5373 | 3.4516 | 3.4441 | 3.4436 | 3.4383 | 3.4894 | 3.5175 | 3.505 | 3.4926 |  | Summer
|  | NN | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 17.8863 | 12.9693 | 12.8623 | 12.727 | 12.4189 | 12.3918 | 12.3899 | 12.371 | 12.5549 | 12.6557 | 12.6109 | 12.5662 |  | Summer
|  | NN | Hours exceeding | 95% of maximum demand | NNHours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | NN | Hours exceeding | Firm capacity (continuous rating) | NNHours exceedingFirm capacity (continuous rating)
|  | NN | Hours exceeding | Firm capacity (short-term rating) | NNHours exceedingFirm capacity (short-term rating)
|  | NN | Regional diversity factor | Summer | NNRegional diversity factorSummer | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554 | 0.68554
|  | NN | Regional diversity factor | Winter | NNRegional diversity factorWinter | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838 | 0.85838
|  | NN | Load transfer capacity (MVA) | 1 | NNLoad transfer capacity (MVA)1 | 6.6 | [11 empty] | Meadowbank
|  | NN | Load transfer capacity (MVA) | 2 | NNLoad transfer capacity (MVA)2
|  | NN | Load transfer capacity (MVA) | 3 | NNLoad transfer capacity (MVA)3
|  | NN | Load transfer capacity (MVA) | 4 | NNLoad transfer capacity (MVA)4
|  | NN | Load transfer capacity (MVA) | 5 | NNLoad transfer capacity (MVA)5
|  | NN | Embedded generation capacity (MVA) | Units less than 100 kVA | NNEmbedded generation capacity (MVA)Units less than 100 kVA | 2.355
|  | NN | Embedded generation capacity (MVA) | Units greater than 100 kVA | NNEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.56
|  | NT | Substation capacity (winter and summer) (MVA) | Total | NTSubstation capacity (winter and summer) (MVA)Total | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
|  | NT | Substation capacity (winter and summer) (MVA) | Firm delivery | NTSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | NT | Maximum demand forecast(peak season) | Maximum demand (MW) | NTMaximum demand forecast(peak season)Maximum demand (MW) | 3.7823 | 3.65 | 3.6349 | 3.6083 | 3.5413 | 3.533 | 3.5189 | 3.5287 | 3.5602 | 3.5974 | 3.5914 | 3.5854
|  | NT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.14159 | 0.13664 | 0.13608 | 0.13508 | 0.13257 | 0.13226 | 0.13173 | 0.1321 | 0.13328 | 0.13467 | 0.13445 | 0.13422
|  | NT | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTMaximum demand forecast(peak season)Maximum demand (MVA) | 3.7849 | 3.6526 | 3.6375 | 3.6108 | 3.5437 | 3.5355 | 3.5214 | 3.5311 | 3.5627 | 3.5999 | 3.5939 | 3.5879
|  | NT | Maximum demand forecast(peak season) | Power factor (coincident) | NTMaximum demand forecast(peak season)Power factor (coincident) | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993 | 0.9993
|  | NT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NTMaximum demand forecast(non-peak season)Maximum demand (MW) | 3.3205 | 3.6663 | 3.6393 | 3.6042 | 3.5198 | 3.5142 | 3.5148 | 3.5102 | 3.5629 | 3.592 | 3.5812 | 3.5704 |  | Summer
|  | NT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.37149 | 0.41017 | 0.40715 | 0.40323 | 0.39378 | 0.39315 | 0.39323 | 0.39271 | 0.3986 | 0.40186 | 0.40065 | 0.39945 |  | Summer
|  | NT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 3.3412 | 3.6892 | 3.662 | 3.6267 | 3.5418 | 3.5361 | 3.5368 | 3.5321 | 3.5851 | 3.6144 | 3.6035 | 3.5927 |  | Summer
|  | NT | Hours exceeding | 95% of maximum demand | NTHours exceeding95% of maximum demand | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
|  | NT | Hours exceeding | Firm capacity (continuous rating) | NTHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | NT | Hours exceeding | Firm capacity (short-term rating) | NTHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | NT | Regional diversity factor | Summer | NTRegional diversity factorSummer | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884 | 0.79884
|  | NT | Regional diversity factor | Winter | NTRegional diversity factorWinter | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302 | 0.78302
|  | NT | Load transfer capacity (MVA) | 1 | NTLoad transfer capacity (MVA)1
|  | NT | Load transfer capacity (MVA) | 2 | NTLoad transfer capacity (MVA)2
|  | NT | Load transfer capacity (MVA) | 3 | NTLoad transfer capacity (MVA)3
|  | NT | Load transfer capacity (MVA) | 4 | NTLoad transfer capacity (MVA)4
|  | NT | Load transfer capacity (MVA) | 5 | NTLoad transfer capacity (MVA)5
|  | NT | Embedded generation capacity (MVA) | Units less than 100 kVA | NTEmbedded generation capacity (MVA)Units less than 100 kVA | 0
|  | NT | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | NW | Substation capacity (winter and summer) (MVA) | Total | NWSubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | NW | Substation capacity (winter and summer) (MVA) | Firm delivery | NWSubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | NW | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NWSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | NW | Maximum demand forecast(peak season) | Maximum demand (MW) | NWMaximum demand forecast(peak season)Maximum demand (MW) | 27.1312 | 27.6642 | 27.4973 | 27.245 | 26.6972 | 26.6105 | 26.4909 | 26.5605 | 26.7941 | 27.0708 | 26.9983 | 26.926
|  | NW | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.4372 | 1.4654 | 1.4566 | 1.4432 | 1.4142 | 1.4096 | 1.4032 | 1.4069 | 1.4193 | 1.434 | 1.4301 | 1.4263
|  | NW | Maximum demand forecast(peak season) | Maximum demand (MVA) | NWMaximum demand forecast(peak season)Maximum demand (MVA) | 27.1692 | 27.703 | 27.5359 | 27.2832 | 26.7346 | 26.6478 | 26.528 | 26.5977 | 26.8316 | 27.1088 | 27.0362 | 26.9638
|  | NW | Maximum demand forecast(peak season) | Power factor (coincident) | NWMaximum demand forecast(peak season)Power factor (coincident) | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986 | 0.9986
|  | NW | Maximum demand forecast(non-peak season) | Maximum demand (MW) | NWMaximum demand forecast(non-peak season)Maximum demand (MW) | 16.6774 | 17.3262 | 17.1746 | 16.9911 | 16.6172 | 16.5124 | 16.47 | 16.4222 | 16.6502 | 16.7688 | 16.6824 | 16.5964 |  | Summer
|  | NW | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | NWMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.1815 | 1.2275 | 1.2167 | 1.2037 | 1.1772 | 1.1698 | 1.1668 | 1.1634 | 1.1796 | 1.188 | 1.1818 | 1.1757 |  | Summer
|  | NW | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 16.7192 | 17.3697 | 17.2176 | 17.0337 | 16.6589 | 16.5538 | 16.5112 | 16.4634 | 16.692 | 16.8108 | 16.7242 | 16.638 |  | Summer
|  | NW | Hours exceeding | 95% of maximum demand | NWHours exceeding95% of maximum demand | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  | NW | Hours exceeding | Firm capacity (continuous rating) | NWHours exceedingFirm capacity (continuous rating)
|  | NW | Hours exceeding | Firm capacity (short-term rating) | NWHours exceedingFirm capacity (short-term rating)
|  | NW | Regional diversity factor | Summer | NWRegional diversity factorSummer | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347 | 0.81347
|  | NW | Regional diversity factor | Winter | NWRegional diversity factorWinter | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791 | 0.90791
|  | NW | Load transfer capacity (MVA) | 1 | NWLoad transfer capacity (MVA)1 | 16.2 | [11 empty] | Hadspen
|  | NW | Load transfer capacity (MVA) | 2 | NWLoad transfer capacity (MVA)2 | 10.8 | [11 empty] | Mowbray
|  | NW | Load transfer capacity (MVA) | 3 | NWLoad transfer capacity (MVA)3 | 27 | [11 empty] | St Leonards
|  | NW | Load transfer capacity (MVA) | 4 | NWLoad transfer capacity (MVA)4 | 16.2 | [11 empty] | Trevallyn
|  | NW | Load transfer capacity (MVA) | 5 | NWLoad transfer capacity (MVA)5
|  | NW | Embedded generation capacity (MVA) | Units less than 100 kVA | NWEmbedded generation capacity (MVA)Units less than 100 kVA | 3.7749
|  | NW | Embedded generation capacity (MVA) | Units greater than 100 kVA | NWEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.58708
|  | PL | Substation capacity (winter and summer) (MVA) | Total | PLSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | PL | Substation capacity (winter and summer) (MVA) | Firm delivery | PLSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25 | 25 | 25 | 25 | 25 | 25
|  | PL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | PL | Maximum demand forecast(peak season) | Maximum demand (MW) | PLMaximum demand forecast(peak season)Maximum demand (MW) | 6.5132 | 6.8742 | 6.8235 | 6.7578 | 6.5995 | 6.5889 | 6.5902 | 6.5815 | 6.6802 | 6.7348 | 6.7146 | 6.6945
|  | PL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.8235 | 2.9799 | 2.958 | 2.9295 | 2.8609 | 2.8563 | 2.8568 | 2.8531 | 2.8959 | 2.9195 | 2.9108 | 2.902
|  | PL | Maximum demand forecast(peak season) | Maximum demand (MVA) | PLMaximum demand forecast(peak season)Maximum demand (MVA) | 7.0988 | 7.4923 | 7.4371 | 7.3655 | 7.1929 | 7.1814 | 7.1828 | 7.1732 | 7.2809 | 7.3404 | 7.3184 | 7.2964
|  | PL | Maximum demand forecast(peak season) | Power factor (coincident) | PLMaximum demand forecast(peak season)Power factor (coincident) | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175 | 0.9175
|  | PL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PLMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.0952 | 4.1886 | 4.1713 | 4.1408 | 4.0638 | 4.0543 | 4.0382 | 4.0494 | 4.0855 | 4.1283 | 4.1214 | 4.1145 |  | Winter
|  | PL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.39845 | 0.40754 | 0.40585 | 0.40288 | 0.3954 | 0.39447 | 0.3929 | 0.39399 | 0.39751 | 0.40167 | 0.40099 | 0.40032 |  | Winter
|  | PL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.1146 | 4.2084 | 4.191 | 4.1603 | 4.083 | 4.0735 | 4.0572 | 4.0685 | 4.1048 | 4.1477 | 4.1408 | 4.1339 |  | Winter
|  | PL | Hours exceeding | 95% of maximum demand | PLHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | PL | Hours exceeding | Firm capacity (continuous rating) | PLHours exceedingFirm capacity (continuous rating)
|  | PL | Hours exceeding | Firm capacity (short-term rating) | PLHours exceedingFirm capacity (short-term rating)
|  | PL | Regional diversity factor | Summer | PLRegional diversity factorSummer | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614 | 0.70614
|  | PL | Regional diversity factor | Winter | PLRegional diversity factorWinter | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782 | 0.87782
|  | PL | Load transfer capacity (MVA) | 1 | PLLoad transfer capacity (MVA)1 | 3.9 | [11 empty] | Burnie
|  | PL | Load transfer capacity (MVA) | 2 | PLLoad transfer capacity (MVA)2 | 3.9 | [11 empty] | Smithton
|  | PL | Load transfer capacity (MVA) | 3 | PLLoad transfer capacity (MVA)3
|  | PL | Load transfer capacity (MVA) | 4 | PLLoad transfer capacity (MVA)4
|  | PL | Load transfer capacity (MVA) | 5 | PLLoad transfer capacity (MVA)5
|  | PL | Embedded generation capacity (MVA) | Units less than 100 kVA | PLEmbedded generation capacity (MVA)Units less than 100 kVA | 0.6376
|  | PL | Embedded generation capacity (MVA) | Units greater than 100 kVA | PLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.225
|  | PM | Substation capacity (winter and summer) (MVA) | Total | PMSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | PM | Substation capacity (winter and summer) (MVA) | Firm delivery | PMSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | PM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | PMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | PM | Maximum demand forecast(peak season) | Maximum demand (MW) | PMMaximum demand forecast(peak season)Maximum demand (MW) | 9.1387 | 8.7808 | 8.7162 | 8.6322 | 8.43 | 8.4165 | 8.4181 | 8.4069 | 8.5331 | 8.6029 | 8.577 | 8.5513
|  | PM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.5715 | 3.4316 | 3.4063 | 3.3735 | 3.2945 | 3.2892 | 3.2899 | 3.2855 | 3.3348 | 3.3621 | 3.352 | 3.3419
|  | PM | Maximum demand forecast(peak season) | Maximum demand (MVA) | PMMaximum demand forecast(peak season)Maximum demand (MVA) | 9.8118 | 9.4276 | 9.3581 | 9.268 | 9.0509 | 9.0364 | 9.0381 | 9.0261 | 9.1616 | 9.2365 | 9.2088 | 9.1811
|  | PM | Maximum demand forecast(peak season) | Power factor (coincident) | PMMaximum demand forecast(peak season)Power factor (coincident) | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314 | 0.9314
|  | PM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | PMMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.4967 | 3.98 | 3.9636 | 3.9346 | 3.8615 | 3.8525 | 3.8371 | 3.8477 | 3.8821 | 3.9227 | 3.9161 | 3.9096 |  | Winter
|  | PM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | PMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.42804 | 0.37886 | 0.37729 | 0.37453 | 0.36757 | 0.36672 | 0.36525 | 0.36626 | 0.36954 | 0.3734 | 0.37278 | 0.37215 |  | Winter
|  | PM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.517 | 3.998 | 3.9815 | 3.9524 | 3.8789 | 3.8699 | 3.8544 | 3.8651 | 3.8997 | 3.9404 | 3.9338 | 3.9273 |  | Winter
|  | PM | Hours exceeding | 95% of maximum demand | PMHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
|  | PM | Hours exceeding | Firm capacity (continuous rating) | PMHours exceedingFirm capacity (continuous rating)
|  | PM | Hours exceeding | Firm capacity (short-term rating) | PMHours exceedingFirm capacity (short-term rating)
|  | PM | Regional diversity factor | Summer | PMRegional diversity factorSummer | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314 | 0.70314
|  | PM | Regional diversity factor | Winter | PMRegional diversity factorWinter | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172 | 0.78172
|  | PM | Load transfer capacity (MVA) | 1 | PMLoad transfer capacity (MVA)1 | 1 | [11 empty] | Avoca
|  | PM | Load transfer capacity (MVA) | 2 | PMLoad transfer capacity (MVA)2 | 5 | [11 empty] | Hadspen
|  | PM | Load transfer capacity (MVA) | 3 | PMLoad transfer capacity (MVA)3 | 2 | [11 empty] | Norwood
|  | PM | Load transfer capacity (MVA) | 4 | PMLoad transfer capacity (MVA)4 | 1.5 | [11 empty] | Railton
|  | PM | Load transfer capacity (MVA) | 5 | PMLoad transfer capacity (MVA)5
|  | PM | Embedded generation capacity (MVA) | Units less than 100 kVA | PMEmbedded generation capacity (MVA)Units less than 100 kVA | 0.52636
|  | PM | Embedded generation capacity (MVA) | Units greater than 100 kVA | PMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | QT | Substation capacity (winter and summer) (MVA) | Total | QTSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | QT | Substation capacity (winter and summer) (MVA) | Firm delivery | QTSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | QT | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | QTSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | QT | Maximum demand forecast(peak season) | Maximum demand (MW) | QTMaximum demand forecast(peak season)Maximum demand (MW) | 5.6217 | 5.2777 | 5.2403 | 5.2056 | 5.1299 | 5.1182 | 5.0981 | 5.1125 | 5.1585 | 5.2127 | 5.2042 | 5.1958
|  | QT | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.225 | 0.21124 | 0.20974 | 0.20835 | 0.20532 | 0.20485 | 0.20405 | 0.20462 | 0.20646 | 0.20863 | 0.20829 | 0.20796
|  | QT | Maximum demand forecast(peak season) | Maximum demand (MVA) | QTMaximum demand forecast(peak season)Maximum demand (MVA) | 5.6262 | 5.2819 | 5.2445 | 5.2098 | 5.134 | 5.1223 | 5.1022 | 5.1166 | 5.1626 | 5.2169 | 5.2084 | 5.1999
|  | QT | Maximum demand forecast(peak season) | Power factor (coincident) | QTMaximum demand forecast(peak season)Power factor (coincident) | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992 | 0.9992
|  | QT | Maximum demand forecast(non-peak season) | Maximum demand (MW) | QTMaximum demand forecast(non-peak season)Maximum demand (MW) | 4.2567 | 4.0858 | 4.0895 | 4.0817 | 4.02 | 4.0103 | 4.002 | 3.9816 | 4.0196 | 4.0238 | 4.007 | 3.9903 |  | Summer
|  | QT | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | QTMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.42295 | 0.40597 | 0.40633 | 0.40556 | 0.39943 | 0.39847 | 0.39764 | 0.39561 | 0.39938 | 0.39981 | 0.39814 | 0.39648 |  | Summer
|  | QT | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 4.2777 | 4.1059 | 4.1096 | 4.1018 | 4.0398 | 4.0301 | 4.0217 | 4.0012 | 4.0393 | 4.0437 | 4.0267 | 4.0099 |  | Summer
|  | QT | Hours exceeding | 95% of maximum demand | QTHours exceeding95% of maximum demand | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
|  | QT | Hours exceeding | Firm capacity (continuous rating) | QTHours exceedingFirm capacity (continuous rating)
|  | QT | Hours exceeding | Firm capacity (short-term rating) | QTHours exceedingFirm capacity (short-term rating)
|  | QT | Regional diversity factor | Summer | QTRegional diversity factorSummer | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249 | 0.84249
|  | QT | Regional diversity factor | Winter | QTRegional diversity factorWinter | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865 | 0.91865
|  | QT | Load transfer capacity (MVA) | 1 | QTLoad transfer capacity (MVA)1
|  | QT | Load transfer capacity (MVA) | 2 | QTLoad transfer capacity (MVA)2
|  | QT | Load transfer capacity (MVA) | 3 | QTLoad transfer capacity (MVA)3
|  | QT | Load transfer capacity (MVA) | 4 | QTLoad transfer capacity (MVA)4
|  | QT | Load transfer capacity (MVA) | 5 | QTLoad transfer capacity (MVA)5
|  | QT | Embedded generation capacity (MVA) | Units less than 100 kVA | QTEmbedded generation capacity (MVA)Units less than 100 kVA | 0.47965
|  | QT | Embedded generation capacity (MVA) | Units greater than 100 kVA | QTEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RA | Substation capacity (winter and summer) (MVA) | Total | RASubstation capacity (winter and summer) (MVA)Total | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | RA | Substation capacity (winter and summer) (MVA) | Firm delivery | RASubstation capacity (winter and summer) (MVA)Firm delivery | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | RA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
|  | RA | Maximum demand forecast(peak season) | Maximum demand (MW) | RAMaximum demand forecast(peak season)Maximum demand (MW) | 46.976 | 50.1748 | 49.933 | 49.6945 | 49.0711 | 49.041 | 48.9015 | 49.0618 | 49.489 | 49.9586 | 49.9365 | 49.9145
|  | RA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 10.8826 | 11.6237 | 11.5676 | 11.5124 | 11.368 | 11.361 | 11.3287 | 11.3658 | 11.4648 | 11.5736 | 11.5685 | 11.5633
|  | RA | Maximum demand forecast(peak season) | Maximum demand (MVA) | RAMaximum demand forecast(peak season)Maximum demand (MVA) | 48.2201 | 51.5036 | 51.2553 | 51.0106 | 50.3706 | 50.3398 | 50.1966 | 50.3611 | 50.7996 | 51.2817 | 51.259 | 51.2364
|  | RA | Maximum demand forecast(peak season) | Power factor (coincident) | RAMaximum demand forecast(peak season)Power factor (coincident) | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742
|  | RA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RAMaximum demand forecast(non-peak season)Maximum demand (MW) | 44.6348 | 46.47 | 46.5034 | 46.445 | 45.8241 | 45.8509 | 45.958 | 45.9942 | 46.7827 | 47.2639 | 47.2316 | 47.1994 |  | Summer
|  | RA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 16.7278 | 17.4156 | 17.4281 | 17.4062 | 17.1735 | 17.1835 | 17.2237 | 17.2372 | 17.5327 | 17.7131 | 17.701 | 17.6889 |  | Summer
|  | RA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 47.6664 | 49.6263 | 49.6619 | 49.5995 | 48.9364 | 48.9651 | 49.0794 | 49.1181 | 49.9602 | 50.474 | 50.4396 | 50.4051 |  | Summer
|  | RA | Hours exceeding | 95% of maximum demand | RAHours exceeding95% of maximum demand | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
|  | RA | Hours exceeding | Firm capacity (continuous rating) | RAHours exceedingFirm capacity (continuous rating)
|  | RA | Hours exceeding | Firm capacity (short-term rating) | RAHours exceedingFirm capacity (short-term rating)
|  | RA | Regional diversity factor | Summer | RARegional diversity factorSummer | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511 | 0.98511
|  | RA | Regional diversity factor | Winter | RARegional diversity factorWinter | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514 | 0.9514
|  | RA | Load transfer capacity (MVA) | 1 | RALoad transfer capacity (MVA)1 | 8.7 | [11 empty] | Devonport
|  | RA | Load transfer capacity (MVA) | 2 | RALoad transfer capacity (MVA)2 | 4.4 | [11 empty] | Ulverstone
|  | RA | Load transfer capacity (MVA) | 3 | RALoad transfer capacity (MVA)3
|  | RA | Load transfer capacity (MVA) | 4 | RALoad transfer capacity (MVA)4
|  | RA | Load transfer capacity (MVA) | 5 | RALoad transfer capacity (MVA)5
|  | RA | Embedded generation capacity (MVA) | Units less than 100 kVA | RAEmbedded generation capacity (MVA)Units less than 100 kVA | 5.4357
|  | RA | Embedded generation capacity (MVA) | Units greater than 100 kVA | RAEmbedded generation capacity (MVA)Units greater than 100 kVA | 3.005
|  | RB22 | Substation capacity (winter and summer) (MVA) | Total | RB22Substation capacity (winter and summer) (MVA)Total | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | RB22 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB22Substation capacity (winter and summer) (MVA)Firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | RB22 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB22Substation capacity (winter and summer) (MVA)Short-term firm delivery | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | RB22 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB22Maximum demand forecast(peak season)Maximum demand (MW) | 2.5344 | 2.9295 | 2.9088 | 2.8895 | 2.8475 | 2.841 | 2.8298 | 2.8378 | 2.8634 | 2.8935 | 2.889 | 2.8845
|  | RB22 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.85085 | 0.98353 | 0.97655 | 0.9701 | 0.95597 | 0.9538 | 0.95005 | 0.95274 | 0.96131 | 0.97142 | 0.96992 | 0.96841
|  | RB22 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB22Maximum demand forecast(peak season)Maximum demand (MVA) | 2.6734 | 3.0902 | 3.0683 | 3.048 | 3.0037 | 2.9968 | 2.985 | 2.9935 | 3.0204 | 3.0522 | 3.0475 | 3.0427
|  | RB22 | Maximum demand forecast(peak season) | Power factor (coincident) | RB22Maximum demand forecast(peak season)Power factor (coincident) | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948 | 0.948
|  | RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB22Maximum demand forecast(non-peak season)Maximum demand (MW) | 1.5521 | 2.0073 | 1.9923 | 1.9751 | 1.9447 | 1.9419 | 1.9425 | 1.9401 | 1.9695 | 1.9858 | 1.9832 | 1.9805 |  | Summer
|  | RB22 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB22Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.8867 | 1.1467 | 1.1382 | 1.1283 | 1.1109 | 1.1093 | 1.1097 | 1.1084 | 1.1251 | 1.1345 | 1.1329 | 1.1314 |  | Summer
|  | RB22 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 1.7876 | 2.3117 | 2.2945 | 2.2747 | 2.2396 | 2.2364 | 2.2371 | 2.2344 | 2.2682 | 2.287 | 2.2839 | 2.2809 |  | Summer
|  | RB22 | Hours exceeding | 95% of maximum demand | RB22Hours exceeding95% of maximum demand | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
|  | RB22 | Hours exceeding | Firm capacity (continuous rating) | RB22Hours exceedingFirm capacity (continuous rating)
|  | RB22 | Hours exceeding | Firm capacity (short-term rating) | RB22Hours exceedingFirm capacity (short-term rating)
|  | RB22 | Regional diversity factor | Summer | RB22Regional diversity factorSummer | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031 | 0.66031
|  | RB22 | Regional diversity factor | Winter | RB22Regional diversity factorWinter | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738 | 0.94738
|  | RB22 | Load transfer capacity (MVA) | 1 | RB22Load transfer capacity (MVA)1
|  | RB22 | Load transfer capacity (MVA) | 2 | RB22Load transfer capacity (MVA)2
|  | RB22 | Load transfer capacity (MVA) | 3 | RB22Load transfer capacity (MVA)3
|  | RB22 | Load transfer capacity (MVA) | 4 | RB22Load transfer capacity (MVA)4
|  | RB22 | Load transfer capacity (MVA) | 5 | RB22Load transfer capacity (MVA)5
|  | RB22 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB22Embedded generation capacity (MVA)Units less than 100 kVA | 0
|  | RB22 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB22Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RB44 | Substation capacity (winter and summer) (MVA) | Total | RB44Substation capacity (winter and summer) (MVA)Total | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | RB44 | Substation capacity (winter and summer) (MVA) | Firm delivery | RB44Substation capacity (winter and summer) (MVA)Firm delivery | 36 | 60[2] | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | RB44 | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RB44Substation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
|  | RB44 | Maximum demand forecast(peak season) | Maximum demand (MW) | RB44Maximum demand forecast(peak season)Maximum demand (MW) | 14.2297 | 28.9029 | 28.7622 | 28.5998 | 28.3134 | 28.2869 | 28.2928 | 28.2708 | 28.5472 | 28.7009 | 28.6757 | 28.6506
|  | RB44 | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 8.6577 | 17.5854 | 17.4998 | 17.4009 | 17.2267 | 17.2106 | 17.2141 | 17.2007 | 17.3689 | 17.4624 | 17.4471 | 17.4318
|  | RB44 | Maximum demand forecast(peak season) | Maximum demand (MVA) | RB44Maximum demand forecast(peak season)Maximum demand (MVA) | 16.6565 | 33.8323 | 33.6676 | 33.4775 | 33.1422 | 33.1112 | 33.1181 | 33.0923 | 33.4159 | 33.5958 | 33.5663 | 33.5369
|  | RB44 | Maximum demand forecast(peak season) | Power factor (coincident) | RB44Maximum demand forecast(peak season)Power factor (coincident) | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543
|  | RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RB44Maximum demand forecast(non-peak season)Maximum demand (MW) | 15.1558 | 29.1809 | 29.0448 | 28.9189 | 28.6435 | 28.6012 | 28.528 | 28.5804 | 28.7476 | 28.9447 | 28.9153 | 28.886 |  | Winter
|  | RB44 | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RB44Maximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 5.9995 | 11.5514 | 11.4975 | 11.4477 | 11.3387 | 11.3219 | 11.2929 | 11.3137 | 11.3798 | 11.4579 | 11.4463 | 11.4346 |  | Winter
|  | RB44 | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 16.3001 | 31.3841 | 31.2377 | 31.1023 | 30.8061 | 30.7605 | 30.6819 | 30.7382 | 30.918 | 31.1301 | 31.0984 | 31.0669 |  | Winter
|  | RB44 | Hours exceeding | 95% of maximum demand | RB44Hours exceeding95% of maximum demand | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67
|  | RB44 | Hours exceeding | Firm capacity (continuous rating) | RB44Hours exceedingFirm capacity (continuous rating)
|  | RB44 | Hours exceeding | Firm capacity (short-term rating) | RB44Hours exceedingFirm capacity (short-term rating)
|  | RB44 | Regional diversity factor | Summer | RB44Regional diversity factorSummer | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367 | 0.88367
|  | RB44 | Regional diversity factor | Winter | RB44Regional diversity factorWinter | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888 | 0.98888
|  | RB44 | Load transfer capacity (MVA) | 1 | RB44Load transfer capacity (MVA)1
|  | RB44 | Load transfer capacity (MVA) | 2 | RB44Load transfer capacity (MVA)2
|  | RB44 | Load transfer capacity (MVA) | 3 | RB44Load transfer capacity (MVA)3
|  | RB44 | Load transfer capacity (MVA) | 4 | RB44Load transfer capacity (MVA)4
|  | RB44 | Load transfer capacity (MVA) | 5 | RB44Load transfer capacity (MVA)5
|  | RB44 | Embedded generation capacity (MVA) | Units less than 100 kVA | RB44Embedded generation capacity (MVA)Units less than 100 kVA | 0.28285
|  | RB44 | Embedded generation capacity (MVA) | Units greater than 100 kVA | RB44Embedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RI | Substation capacity (winter and summer) (MVA) | Total | RISubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
|  | RI | Substation capacity (winter and summer) (MVA) | Firm delivery | RISubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | RI | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RISubstation capacity (winter and summer) (MVA)Short-term firm delivery | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | RI | Maximum demand forecast(peak season) | Maximum demand (MW) | RIMaximum demand forecast(peak season)Maximum demand (MW) | 68.405 | 78.1605 | 78.8017 | 78.694 | 77.7093 | 78.0351 | 78.2481 | 79.0044 | 80.2594 | 81.6591 | 82.1067 | 82.5568
|  | RI | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 15.8469 | 18.1069 | 18.2555 | 18.2305 | 18.0024 | 18.0779 | 18.1272 | 18.3024 | 18.5932 | 18.9174 | 19.0211 | 19.1254
|  | RI | Maximum demand forecast(peak season) | Maximum demand (MVA) | RIMaximum demand forecast(peak season)Maximum demand (MVA) | 70.2166 | 80.2304 | 80.8887 | 80.7781 | 79.7673 | 80.1017 | 80.3203 | 81.0967 | 82.3849 | 83.8217 | 84.2812 | 84.7432
|  | RI | Maximum demand forecast(peak season) | Power factor (coincident) | RIMaximum demand forecast(peak season)Power factor (coincident) | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742
|  | RI | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RIMaximum demand forecast(non-peak season)Maximum demand (MW) | 45.4554 | 55.2401 | 55.8977 | 55.9514 | 55.341 | 55.5471 | 55.8885 | 56.1677 | 57.3805 | 58.2265 | 58.6109 | 58.9979 |  | Summer
|  | RI | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RIMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 14.8596 | 18.0583 | 18.2733 | 18.2909 | 18.0913 | 18.1587 | 18.2703 | 18.3616 | 18.7581 | 19.0346 | 19.1603 | 19.2868 |  | Summer
|  | RI | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 47.8226 | 58.1168 | 58.8087 | 58.8652 | 58.223 | 58.4399 | 58.799 | 59.0928 | 60.3687 | 61.2588 | 61.6633 | 62.0704 |  | Summer
|  | RI | Hours exceeding | 95% of maximum demand | RIHours exceeding95% of maximum demand | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
|  | RI | Hours exceeding | Firm capacity (continuous rating) | RIHours exceedingFirm capacity (continuous rating)
|  | RI | Hours exceeding | Firm capacity (short-term rating) | RIHours exceedingFirm capacity (short-term rating)
|  | RI | Regional diversity factor | Summer | RIRegional diversity factorSummer | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099 | 0.83099
|  | RI | Regional diversity factor | Winter | RIRegional diversity factorWinter | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845 | 0.94845
|  | RI | Load transfer capacity (MVA) | 1 | RILoad transfer capacity (MVA)1
|  | RI | Load transfer capacity (MVA) | 2 | RILoad transfer capacity (MVA)2
|  | RI | Load transfer capacity (MVA) | 3 | RILoad transfer capacity (MVA)3
|  | RI | Load transfer capacity (MVA) | 4 | RILoad transfer capacity (MVA)4
|  | RI | Load transfer capacity (MVA) | 5 | RILoad transfer capacity (MVA)5
|  | RI | Embedded generation capacity (MVA) | Units less than 100 kVA | RIEmbedded generation capacity (MVA)Units less than 100 kVA | 3.0945
|  | RI | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | RK | Substation capacity (winter and summer) (MVA) | Total | RKSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | RK | Substation capacity (winter and summer) (MVA) | Firm delivery | RKSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | RK | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RKSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | RK | Maximum demand forecast(peak season) | Maximum demand (MW) | RKMaximum demand forecast(peak season)Maximum demand (MW) | 21.802 | 19.6131 | 19.5321 | 19.3891 | 19.0287 | 18.9844 | 18.9087 | 18.9611 | 19.1305 | 19.3305 | 19.2982 | 19.2659
|  | RK | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.2729 | 1.1451 | 1.1404 | 1.132 | 1.111 | 1.1084 | 1.104 | 1.107 | 1.1169 | 1.1286 | 1.1267 | 1.1248
|  | RK | Maximum demand forecast(peak season) | Maximum demand (MVA) | RKMaximum demand forecast(peak season)Maximum demand (MVA) | 21.8391 | 19.6465 | 19.5653 | 19.4221 | 19.0611 | 19.0167 | 18.9409 | 18.9933 | 19.1631 | 19.3634 | 19.3311 | 19.2987
|  | RK | Maximum demand forecast(peak season) | Power factor (coincident) | RKMaximum demand forecast(peak season)Power factor (coincident) | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983
|  | RK | Maximum demand forecast(non-peak season) | Maximum demand (MW) | RKMaximum demand forecast(non-peak season)Maximum demand (MW) | 16.0374 | 11.0985 | 10.9636 | 10.858 | 10.6588 | 10.6208 | 10.6243 | 10.6115 | 10.7721 | 10.8615 | 10.7927 | 10.7244 |  | Summer
|  | RK | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | RKMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.81855 | 0.56647 | 0.55958 | 0.55419 | 0.54402 | 0.54208 | 0.54226 | 0.54161 | 0.54981 | 0.55437 | 0.55086 | 0.54737 |  | Summer
|  | RK | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 16.0583 | 11.113 | 10.9779 | 10.8721 | 10.6726 | 10.6346 | 10.6381 | 10.6254 | 10.7861 | 10.8756 | 10.8068 | 10.7384 |  | Summer
|  | RK | Hours exceeding | 95% of maximum demand | RKHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
|  | RK | Hours exceeding | Firm capacity (continuous rating) | RKHours exceedingFirm capacity (continuous rating)
|  | RK | Hours exceeding | Firm capacity (short-term rating) | RKHours exceedingFirm capacity (short-term rating)
|  | RK | Regional diversity factor | Summer | RKRegional diversity factorSummer | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309 | 0.64309
|  | RK | Regional diversity factor | Winter | RKRegional diversity factorWinter | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946 | 0.85946
|  | RK | Load transfer capacity (MVA) | 1 | RKLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Cambridge
|  | RK | Load transfer capacity (MVA) | 2 | RKLoad transfer capacity (MVA)2 | 5.8 | [11 empty] | Howrah
|  | RK | Load transfer capacity (MVA) | 3 | RKLoad transfer capacity (MVA)3
|  | RK | Load transfer capacity (MVA) | 4 | RKLoad transfer capacity (MVA)4
|  | RK | Load transfer capacity (MVA) | 5 | RKLoad transfer capacity (MVA)5
|  | RK | Embedded generation capacity (MVA) | Units less than 100 kVA | RKEmbedded generation capacity (MVA)Units less than 100 kVA | 3.3856
|  | RK | Embedded generation capacity (MVA) | Units greater than 100 kVA | RKEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SD | Substation capacity (winter and summer) (MVA) | Total | SDSubstation capacity (winter and summer) (MVA)Total | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
|  | SD | Substation capacity (winter and summer) (MVA) | Firm delivery | SDSubstation capacity (winter and summer) (MVA)Firm delivery | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5
|  | SD | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SDSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
|  | SD | Maximum demand forecast(peak season) | Maximum demand (MW) | SDMaximum demand forecast(peak season)Maximum demand (MW) | 11.2449 | 12.6787 | 12.4576 | 12.245 | 11.9384 | 11.7832 | 11.6093 | 11.5142 | 11.4887 | 11.4791 | 11.4791 | 11.4791
|  | SD | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.1058 | 1.2467 | 1.225 | 1.2041 | 1.1739 | 1.1587 | 1.1416 | 1.1322 | 1.1297 | 1.1288 | 1.1288 | 1.1288
|  | SD | Maximum demand forecast(peak season) | Maximum demand (MVA) | SDMaximum demand forecast(peak season)Maximum demand (MVA) | 11.2992 | 12.7398 | 12.5177 | 12.3041 | 11.996 | 11.84 | 11.6653 | 11.5698 | 11.5442 | 11.5345 | 11.5345 | 11.5345
|  | SD | Maximum demand forecast(peak season) | Power factor (coincident) | SDMaximum demand forecast(peak season)Power factor (coincident) | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952 | 0.9952
|  | SD | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SDMaximum demand forecast(non-peak season)Maximum demand (MW) | 9.9693 | 11.3446 | 11.2193 | 11.0699 | 10.7702 | 10.7127 | 10.6744 | 10.62 | 10.7386 | 10.7851 | 10.8807 | 10.9772 |  | Summer
|  | SD | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SDMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.794 | 3.1794 | 3.1443 | 3.1024 | 3.0184 | 3.0023 | 2.9916 | 2.9763 | 3.0096 | 3.0226 | 3.0494 | 3.0764 |  | Summer
|  | SD | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 10.3534 | 11.7817 | 11.6516 | 11.4964 | 11.1852 | 11.1254 | 11.0857 | 11.0292 | 11.1523 | 11.2007 | 11.3 | 11.4001 |  | Summer
|  | SD | Hours exceeding | 95% of maximum demand | SDHours exceeding95% of maximum demand | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
|  | SD | Hours exceeding | Firm capacity (continuous rating) | SDHours exceedingFirm capacity (continuous rating)
|  | SD | Hours exceeding | Firm capacity (short-term rating) | SDHours exceedingFirm capacity (short-term rating)
|  | SD | Regional diversity factor | Summer | SDRegional diversity factorSummer | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342 | 0.87342
|  | SD | Regional diversity factor | Winter | SDRegional diversity factorWinter | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449 | 0.96449
|  | SD | Load transfer capacity (MVA) | 1 | SDLoad transfer capacity (MVA)1 | 4.8 | [11 empty] | Derby
|  | SD | Load transfer capacity (MVA) | 2 | SDLoad transfer capacity (MVA)2 | 3.2 | [11 empty] | George Town
|  | SD | Load transfer capacity (MVA) | 3 | SDLoad transfer capacity (MVA)3 | 2.1 | [11 empty] | Trevallyn
|  | SD | Load transfer capacity (MVA) | 4 | SDLoad transfer capacity (MVA)4
|  | SD | Load transfer capacity (MVA) | 5 | SDLoad transfer capacity (MVA)5
|  | SD | Embedded generation capacity (MVA) | Units less than 100 kVA | SDEmbedded generation capacity (MVA)Units less than 100 kVA | 2.4685
|  | SD | Embedded generation capacity (MVA) | Units greater than 100 kVA | SDEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SL | Substation capacity (winter and summer) (MVA) | Total | SLSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | SL | Substation capacity (winter and summer) (MVA) | Firm delivery | SLSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SLSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
|  | SL | Maximum demand forecast(peak season) | Maximum demand (MW) | SLMaximum demand forecast(peak season)Maximum demand (MW) | 28.6564 | 27.6156 | 27.4612 | 27.2209 | 26.6831 | 26.6022 | 26.485 | 26.552 | 26.7829 | 27.0573 | 26.9899 | 26.9227
|  | SL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.904 | 1.8348 | 1.8246 | 1.8086 | 1.7729 | 1.7675 | 1.7597 | 1.7642 | 1.7795 | 1.7977 | 1.7933 | 1.7888
|  | SL | Maximum demand forecast(peak season) | Maximum demand (MVA) | SLMaximum demand forecast(peak season)Maximum demand (MVA) | 28.7196 | 27.6765 | 27.5217 | 27.2809 | 26.742 | 26.6608 | 26.5434 | 26.6105 | 26.842 | 27.1169 | 27.0494 | 26.982
|  | SL | Maximum demand forecast(peak season) | Power factor (coincident) | SLMaximum demand forecast(peak season)Power factor (coincident) | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978 | 0.9978
|  | SL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SLMaximum demand forecast(non-peak season)Maximum demand (MW) | 18.1086 | 14.1231 | 13.9603 | 13.7721 | 13.4329 | 13.3188 | 13.2623 | 13.206 | 13.3729 | 13.4518 | 13.3273 | 13.2039 |  | Summer
|  | SL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SLMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.7429 | 1.3593 | 1.3437 | 1.3256 | 1.2929 | 1.2819 | 1.2765 | 1.2711 | 1.2871 | 1.2947 | 1.2827 | 1.2709 |  | Summer
|  | SL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 18.1923 | 14.1884 | 14.0248 | 13.8358 | 13.495 | 13.3804 | 13.3236 | 13.267 | 13.4347 | 13.5139 | 13.3889 | 13.265 |  | Summer
|  | SL | Hours exceeding | 95% of maximum demand | SLHours exceeding95% of maximum demand | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
|  | SL | Hours exceeding | Firm capacity (continuous rating) | SLHours exceedingFirm capacity (continuous rating)
|  | SL | Hours exceeding | Firm capacity (short-term rating) | SLHours exceedingFirm capacity (short-term rating)
|  | SL | Regional diversity factor | Summer | SLRegional diversity factorSummer | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329 | 0.84329
|  | SL | Regional diversity factor | Winter | SLRegional diversity factorWinter | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408 | 0.95408
|  | SL | Load transfer capacity (MVA) | 1 | SLLoad transfer capacity (MVA)1 | 3 | [11 empty] | Mowbray
|  | SL | Load transfer capacity (MVA) | 2 | SLLoad transfer capacity (MVA)2 | 10 | [11 empty] | Norwood
|  | SL | Load transfer capacity (MVA) | 3 | SLLoad transfer capacity (MVA)3 | 3 | [11 empty] | Trevallyn
|  | SL | Load transfer capacity (MVA) | 4 | SLLoad transfer capacity (MVA)4
|  | SL | Load transfer capacity (MVA) | 5 | SLLoad transfer capacity (MVA)5
|  | SL | Embedded generation capacity (MVA) | Units less than 100 kVA | SLEmbedded generation capacity (MVA)Units less than 100 kVA | 2.8082
|  | SL | Embedded generation capacity (MVA) | Units greater than 100 kVA | SLEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SM | Substation capacity (winter and summer) (MVA) | Total | SMSubstation capacity (winter and summer) (MVA)Total | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 50 | 50
|  | SM | Substation capacity (winter and summer) (MVA) | Firm delivery | SMSubstation capacity (winter and summer) (MVA)Firm delivery | 10 | 10 | 10 | 10 | 10 | 10 | 25[1] | 25 | 25 | 25 | 25 | 25
|  | SM | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SMSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 30 | 30 | 30 | 30 | 30
|  | SM | Maximum demand forecast(peak season) | Maximum demand (MW) | SMMaximum demand forecast(peak season)Maximum demand (MW) | 15.4174 | 12.35 | 12.1754 | 11.9637 | 11.621 | 11.4738 | 11.3084 | 11.2198 | 11.1991 | 11.1939 | 11.1939 | 11.1939
|  | SM | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 2.2628 | 1.8126 | 1.787 | 1.7559 | 1.7056 | 1.684 | 1.6598 | 1.6468 | 1.6437 | 1.6429 | 1.6429 | 1.6429
|  | SM | Maximum demand forecast(peak season) | Maximum demand (MVA) | SMMaximum demand forecast(peak season)Maximum demand (MVA) | 15.5825 | 12.4823 | 12.3059 | 12.0918 | 11.7455 | 11.5967 | 11.4296 | 11.34 | 11.3191 | 11.3138 | 11.3138 | 11.3138
|  | SM | Maximum demand forecast(peak season) | Power factor (coincident) | SMMaximum demand forecast(peak season)Power factor (coincident) | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894 | 0.9894
|  | SM | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SMMaximum demand forecast(non-peak season)Maximum demand (MW) | 10.8563 | 9.847 | 9.7159 | 9.5647 | 9.2865 | 9.2234 | 9.183 | 9.1324 | 9.232 | 9.2697 | 9.195 | 9.1208 |  | Summer
|  | SM | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SMMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 1.319 | 1.1964 | 1.1805 | 1.1621 | 1.1283 | 1.1206 | 1.1157 | 1.1096 | 1.1217 | 1.1262 | 1.1172 | 1.1082 |  | Summer
|  | SM | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 10.9361 | 9.9194 | 9.7874 | 9.635 | 9.3548 | 9.2913 | 9.2506 | 9.1996 | 9.2998 | 9.3379 | 9.2626 | 9.1879 |  | Summer
|  | SM | Hours exceeding | 95% of maximum demand | SMHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | SM | Hours exceeding | Firm capacity (continuous rating) | SMHours exceedingFirm capacity (continuous rating)
|  | SM | Hours exceeding | Firm capacity (short-term rating) | SMHours exceedingFirm capacity (short-term rating)
|  | SM | Regional diversity factor | Summer | SMRegional diversity factorSummer | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022 | 0.93022
|  | SM | Regional diversity factor | Winter | SMRegional diversity factorWinter | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287 | 0.62287
|  | SM | Load transfer capacity (MVA) | 1 | SMLoad transfer capacity (MVA)1 | 2.8 | [11 empty] | Avoca
|  | SM | Load transfer capacity (MVA) | 2 | SMLoad transfer capacity (MVA)2 | 4 | [11 empty] | Derby
|  | SM | Load transfer capacity (MVA) | 3 | SMLoad transfer capacity (MVA)3 | 4.5 | [11 empty] | Triabunna
|  | SM | Load transfer capacity (MVA) | 4 | SMLoad transfer capacity (MVA)4
|  | SM | Load transfer capacity (MVA) | 5 | SMLoad transfer capacity (MVA)5
|  | SM | Embedded generation capacity (MVA) | Units less than 100 kVA | SMEmbedded generation capacity (MVA)Units less than 100 kVA | 2.8842
|  | SM | Embedded generation capacity (MVA) | Units greater than 100 kVA | SMEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SO | Substation capacity (winter and summer) (MVA) | Total | SOSubstation capacity (winter and summer) (MVA)Total | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
|  | SO | Substation capacity (winter and summer) (MVA) | Firm delivery | SOSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SO | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SOSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
|  | SO | Maximum demand forecast(peak season) | Maximum demand (MW) | SOMaximum demand forecast(peak season)Maximum demand (MW) | 33.284 | 31.0316 | 30.8114 | 30.6077 | 30.1622 | 30.0936 | 29.9753 | 30.06 | 30.3305 | 30.6494 | 30.5995 | 30.5497
|  | SO | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SO | Maximum demand forecast(peak season) | Maximum demand (MVA) | SOMaximum demand forecast(peak season)Maximum demand (MVA) | 33.284 | 31.0316 | 30.8114 | 30.6077 | 30.1622 | 30.0936 | 29.9753 | 30.06 | 30.3305 | 30.6494 | 30.5995 | 30.5497
|  | SO | Maximum demand forecast(peak season) | Power factor (coincident) | SOMaximum demand forecast(peak season)Power factor (coincident) | 1 | bar: 3 2019 to 13 2029
|  | SO | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SOMaximum demand forecast(non-peak season)Maximum demand (MW) | 25.6044 | 19.4891 | 19.3218 | 19.1175 | 18.6877 | 18.5322 | 18.4168 | 18.2776 | 18.4371 | 18.4721 | 18.4721 | 18.4721 |  | Summer
|  | SO | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SOMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.51216 | 0.38984 | 0.38649 | 0.38241 | 0.37381 | 0.3707 | 0.36839 | 0.36561 | 0.3688 | 0.3695 | 0.3695 | 0.3695 |  | Summer
|  | SO | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 25.6095 | 19.493 | 19.3257 | 19.1213 | 18.6915 | 18.5359 | 18.4205 | 18.2813 | 18.4408 | 18.4758 | 18.4758 | 18.4758 |  | Summer
|  | SO | Hours exceeding | 95% of maximum demand | SOHours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | SO | Hours exceeding | Firm capacity (continuous rating) | SOHours exceedingFirm capacity (continuous rating)
|  | SO | Hours exceeding | Firm capacity (short-term rating) | SOHours exceedingFirm capacity (short-term rating)
|  | SO | Regional diversity factor | Summer | SORegional diversity factorSummer | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597 | 0.79597
|  | SO | Regional diversity factor | Winter | SORegional diversity factorWinter | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334 | 0.87334
|  | SO | Load transfer capacity (MVA) | 1 | SOLoad transfer capacity (MVA)1 | 1.5 | [11 empty] | Avoca
|  | SO | Load transfer capacity (MVA) | 2 | SOLoad transfer capacity (MVA)2 | 1.5 | [11 empty] | Meadowbank
|  | SO | Load transfer capacity (MVA) | 3 | SOLoad transfer capacity (MVA)3 | 1.5 | [11 empty] | Triabunna
|  | SO | Load transfer capacity (MVA) | 4 | SOLoad transfer capacity (MVA)4
|  | SO | Load transfer capacity (MVA) | 5 | SOLoad transfer capacity (MVA)5
|  | SO | Embedded generation capacity (MVA) | Units less than 100 kVA | SOEmbedded generation capacity (MVA)Units less than 100 kVA | 6.178
|  | SO | Embedded generation capacity (MVA) | Units greater than 100 kVA | SOEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | SR | Substation capacity (winter and summer) (MVA) | Total | SRSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50
|  | SR | Substation capacity (winter and summer) (MVA) | Firm delivery | SRSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 25[2] | 25[2] | 25 | 25
|  | SR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30
|  | SR | Maximum demand forecast(peak season) | Maximum demand (MW) | SRMaximum demand forecast(peak season)Maximum demand (MW) | 1.2827 | 1.2506 | 1.2455 | 1.2363 | 1.2134 | 1.2105 | 1.2057 | 1.209 | 1.2199 | 1.2326 | 1.2305 | 1.2285
|  | SR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.018141 | 0.017688 | 0.017615 | 0.017486 | 0.017161 | 0.017121 | 0.017053 | 0.0171 | 0.017253 | 0.017433 | 0.017404 | 0.017375
|  | SR | Maximum demand forecast(peak season) | Maximum demand (MVA) | SRMaximum demand forecast(peak season)Maximum demand (MVA) | 1.2828 | 1.2508 | 1.2456 | 1.2365 | 1.2135 | 1.2107 | 1.2058 | 1.2092 | 1.22 | 1.2327 | 1.2307 | 1.2286
|  | SR | Maximum demand forecast(peak season) | Power factor (coincident) | SRMaximum demand forecast(peak season)Power factor (coincident) | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999
|  | SR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | SRMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.6949 | 0.70704 | 0.70613 | 0.70383 | 0.69304 | 0.69207 | 0.69231 | 0.69148 | 0.70195 | 0.70778 | 0.70589 | 0.704 |  | Summer
|  | SR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | SRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Summer
|  | SR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.6949 | 0.70704 | 0.70613 | 0.70383 | 0.69304 | 0.69207 | 0.69231 | 0.69148 | 0.70195 | 0.70778 | 0.70589 | 0.704 |  | Summer
|  | SR | Hours exceeding | 95% of maximum demand | SRHours exceeding95% of maximum demand | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | SR | Hours exceeding | Firm capacity (continuous rating) | SRHours exceedingFirm capacity (continuous rating)
|  | SR | Hours exceeding | Firm capacity (short-term rating) | SRHours exceedingFirm capacity (short-term rating)
|  | SR | Regional diversity factor | Summer | SRRegional diversity factorSummer | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872 | 0.76872
|  | SR | Regional diversity factor | Winter | SRRegional diversity factorWinter | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261 | 0.82261
|  | SR | Load transfer capacity (MVA) | 1 | SRLoad transfer capacity (MVA)1
|  | SR | Load transfer capacity (MVA) | 2 | SRLoad transfer capacity (MVA)2
|  | SR | Load transfer capacity (MVA) | 3 | SRLoad transfer capacity (MVA)3
|  | SR | Load transfer capacity (MVA) | 4 | SRLoad transfer capacity (MVA)4
|  | SR | Load transfer capacity (MVA) | 5 | SRLoad transfer capacity (MVA)5
|  | SR | Embedded generation capacity (MVA) | Units less than 100 kVA | SREmbedded generation capacity (MVA)Units less than 100 kVA | 0.10927
|  | SR | Embedded generation capacity (MVA) | Units greater than 100 kVA | SREmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | ST | Substation capacity (winter and summer) (MVA) | Total | STSubstation capacity (winter and summer) (MVA)Total | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
|  | ST | Substation capacity (winter and summer) (MVA) | Firm delivery | STSubstation capacity (winter and summer) (MVA)Firm delivery | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
|  | ST | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | STSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | ST | Maximum demand forecast(peak season) | Maximum demand (MW) | STMaximum demand forecast(peak season)Maximum demand (MW) | 19.5706 | 22.4476 | 21.7431 | 21.0285 | 20.1822 | 19.6367 | 19.1323 | 18.6026 | 18.371 | 18.0063 | 18.0063 | 18.0063
|  | ST | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 7.5924 | 8.7085 | 8.4352 | 8.158 | 7.8297 | 7.618 | 7.4224 | 7.2169 | 7.127 | 6.9855 | 6.9855 | 6.9855
|  | ST | Maximum demand forecast(peak season) | Maximum demand (MVA) | STMaximum demand forecast(peak season)Maximum demand (MVA) | 20.9918 | 24.0776 | 23.322 | 22.5555 | 21.6477 | 21.0626 | 20.5216 | 19.9534 | 19.7051 | 19.3138 | 19.3138 | 19.3138
|  | ST | Maximum demand forecast(peak season) | Power factor (coincident) | STMaximum demand forecast(peak season)Power factor (coincident) | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323 | 0.9323
|  | ST | Maximum demand forecast(non-peak season) | Maximum demand (MW) | STMaximum demand forecast(non-peak season)Maximum demand (MW) | 19.7507 | 24.1743 | 24.0585 | 23.8669 | 23.4108 | 23.3488 | 23.2513 | 23.3132 | 23.5191 | 23.7627 | 23.7471 | 23.7315 |  | Winter
|  | ST | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | STMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.7836 | 5.855 | 5.827 | 5.7806 | 5.6701 | 5.6551 | 5.6315 | 5.6465 | 5.6963 | 5.7553 | 5.7515 | 5.7478 |  | Winter
|  | ST | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 20.3218 | 24.8733 | 24.7541 | 24.557 | 24.0876 | 24.0239 | 23.9236 | 23.9873 | 24.199 | 24.4497 | 24.4337 | 24.4177 |  | Winter
|  | ST | Hours exceeding | 95% of maximum demand | STHours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | ST | Hours exceeding | Firm capacity (continuous rating) | STHours exceedingFirm capacity (continuous rating)
|  | ST | Hours exceeding | Firm capacity (short-term rating) | STHours exceedingFirm capacity (short-term rating)
|  | ST | Regional diversity factor | Summer | STRegional diversity factorSummer | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269 | 0.80269
|  | ST | Regional diversity factor | Winter | STRegional diversity factorWinter | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959 | 0.87959
|  | ST | Load transfer capacity (MVA) | 1 | STLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Port Latta
|  | ST | Load transfer capacity (MVA) | 2 | STLoad transfer capacity (MVA)2
|  | ST | Load transfer capacity (MVA) | 3 | STLoad transfer capacity (MVA)3
|  | ST | Load transfer capacity (MVA) | 4 | STLoad transfer capacity (MVA)4
|  | ST | Load transfer capacity (MVA) | 5 | STLoad transfer capacity (MVA)5
|  | ST | Embedded generation capacity (MVA) | Units less than 100 kVA | STEmbedded generation capacity (MVA)Units less than 100 kVA | 1.7015
|  | ST | Embedded generation capacity (MVA) | Units greater than 100 kVA | STEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.825
|  | TB | Substation capacity (winter and summer) (MVA) | Total | TBSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | TB | Substation capacity (winter and summer) (MVA) | Firm delivery | TBSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | TB | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TBSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  | TB | Maximum demand forecast(peak season) | Maximum demand (MW) | TBMaximum demand forecast(peak season)Maximum demand (MW) | 7.7374 | 5.6276 | 5.6874 | 5.7329 | 5.6971 | 5.7876 | 5.89 | 5.9841 | 6.1778 | 6.333 | 6.4272 | 6.5227
|  | TB | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 1.9051 | 1.3856 | 1.4003 | 1.4116 | 1.4027 | 1.425 | 1.4502 | 1.4734 | 1.5211 | 1.5593 | 1.5825 | 1.606
|  | TB | Maximum demand forecast(peak season) | Maximum demand (MVA) | TBMaximum demand forecast(peak season)Maximum demand (MVA) | 7.9684 | 5.7957 | 5.8573 | 5.9041 | 5.8672 | 5.9605 | 6.0659 | 6.1628 | 6.3623 | 6.5221 | 6.6191 | 6.7176
|  | TB | Maximum demand forecast(peak season) | Power factor (coincident) | TBMaximum demand forecast(peak season)Power factor (coincident) | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971 | 0.971
|  | TB | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TBMaximum demand forecast(non-peak season)Maximum demand (MW) | 6.8238 | 7.0313 | 7.0628 | 7.0712 | 6.9988 | 7.0414 | 7.0719 | 7.1503 | 7.2736 | 7.4095 | 7.4596 | 7.5099 |  | Winter
|  | TB | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TBMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.45339 | 0.46717 | 0.46927 | 0.46983 | 0.46502 | 0.46784 | 0.46987 | 0.47508 | 0.48327 | 0.49231 | 0.49563 | 0.49898 |  | Winter
|  | TB | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 6.8388 | 7.0468 | 7.0784 | 7.0868 | 7.0142 | 7.0569 | 7.0875 | 7.1661 | 7.2896 | 7.4259 | 7.476 | 7.5265 |  | Winter
|  | TB | Hours exceeding | 95% of maximum demand | TBHours exceeding95% of maximum demand | 1 | bar: 3 2019 to 13 2029
|  | TB | Hours exceeding | Firm capacity (continuous rating) | TBHours exceedingFirm capacity (continuous rating)
|  | TB | Hours exceeding | Firm capacity (short-term rating) | TBHours exceedingFirm capacity (short-term rating)
|  | TB | Regional diversity factor | Summer | TBRegional diversity factorSummer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | TB | Regional diversity factor | Winter | TBRegional diversity factorWinter | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273 | 0.79273
|  | TB | Load transfer capacity (MVA) | 1 | TBLoad transfer capacity (MVA)1 | 3 | [11 empty] | St Marys
|  | TB | Load transfer capacity (MVA) | 2 | TBLoad transfer capacity (MVA)2 | 1.8 | [11 empty] | Sorell
|  | TB | Load transfer capacity (MVA) | 3 | TBLoad transfer capacity (MVA)3
|  | TB | Load transfer capacity (MVA) | 4 | TBLoad transfer capacity (MVA)4
|  | TB | Load transfer capacity (MVA) | 5 | TBLoad transfer capacity (MVA)5
|  | TB | Embedded generation capacity (MVA) | Units less than 100 kVA | TBEmbedded generation capacity (MVA)Units less than 100 kVA | 1.2688
|  | TB | Embedded generation capacity (MVA) | Units greater than 100 kVA | TBEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | TR | Substation capacity (winter and summer) (MVA) | Total | TRSubstation capacity (winter and summer) (MVA)Total | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
|  | TR | Substation capacity (winter and summer) (MVA) | Firm delivery | TRSubstation capacity (winter and summer) (MVA)Firm delivery | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
|  | TR | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TRSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
|  | TR | Maximum demand forecast(peak season) | Maximum demand (MW) | TRMaximum demand forecast(peak season)Maximum demand (MW) | 65.5208 | 64.6656 | 64.0761 | 63.5257 | 62.4974 | 62.2941 | 62.0131 | 62.168 | 62.7066 | 63.3476 | 63.1725 | 62.9978
|  | TR | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.8254 | 3.7754 | 3.741 | 3.7089 | 3.6488 | 3.637 | 3.6206 | 3.6296 | 3.6611 | 3.6985 | 3.6883 | 3.6781
|  | TR | Maximum demand forecast(peak season) | Maximum demand (MVA) | TRMaximum demand forecast(peak season)Maximum demand (MVA) | 65.6323 | 64.7757 | 64.1852 | 63.6339 | 62.6038 | 62.4002 | 62.1187 | 62.2738 | 62.8134 | 63.4554 | 63.28 | 63.1051
|  | TR | Maximum demand forecast(peak season) | Power factor (coincident) | TRMaximum demand forecast(peak season)Power factor (coincident) | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983 | 0.9983
|  | TR | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TRMaximum demand forecast(non-peak season)Maximum demand (MW) | 38.3689 | 35.479 | 35.1713 | 34.7986 | 34.0354 | 33.8227 | 33.7368 | 33.6398 | 34.1073 | 34.3506 | 34.2195 | 34.0888 |  | Summer
|  | TR | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TRMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 2.1731 | 2.0094 | 1.992 | 1.9709 | 1.9276 | 1.9156 | 1.9107 | 1.9052 | 1.9317 | 1.9455 | 1.9381 | 1.9307 |  | Summer
|  | TR | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 38.4303 | 35.5358 | 35.2277 | 34.8544 | 34.09 | 33.8769 | 33.7909 | 33.6937 | 34.1619 | 34.4057 | 34.2743 | 34.1434 |  | Summer
|  | TR | Hours exceeding | 95% of maximum demand | TRHours exceeding95% of maximum demand | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | TR | Hours exceeding | Firm capacity (continuous rating) | TRHours exceedingFirm capacity (continuous rating)
|  | TR | Hours exceeding | Firm capacity (short-term rating) | TRHours exceedingFirm capacity (short-term rating)
|  | TR | Regional diversity factor | Summer | TRRegional diversity factorSummer | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742 | 0.78742
|  | TR | Regional diversity factor | Winter | TRRegional diversity factorWinter | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409 | 0.97409
|  | TR | Load transfer capacity (MVA) | 1 | TRLoad transfer capacity (MVA)1 | 3.6 | [11 empty] | George Town
|  | TR | Load transfer capacity (MVA) | 2 | TRLoad transfer capacity (MVA)2 | 14.4 | [11 empty] | Hadspen
|  | TR | Load transfer capacity (MVA) | 3 | TRLoad transfer capacity (MVA)3 | 36.1 | [11 empty] | Mowbray
|  | TR | Load transfer capacity (MVA) | 4 | TRLoad transfer capacity (MVA)4 | 21.7 | [11 empty] | Norwood
|  | TR | Load transfer capacity (MVA) | 5 | TRLoad transfer capacity (MVA)5 | 21.7 | [11 empty] | St Leonards
|  | TR | Embedded generation capacity (MVA) | Units less than 100 kVA | TREmbedded generation capacity (MVA)Units less than 100 kVA | 10.0376
|  | TR | Embedded generation capacity (MVA) | Units greater than 100 kVA | TREmbedded generation capacity (MVA)Units greater than 100 kVA | 2.5
|  | TU | Substation capacity (winter and summer) (MVA) | Total | TUSubstation capacity (winter and summer) (MVA)Total | 13[1] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | TU | Substation capacity (winter and summer) (MVA) | Firm delivery | TUSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | TU | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | TUSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | TU | Maximum demand forecast(peak season) | Maximum demand (MW) | TUMaximum demand forecast(peak season)Maximum demand (MW) | 0.88438 | 1.0768 | 1.0714 | 1.0666 | 1.0625 | 1.0591 | 1.0566 | 1.055 | 1.0544 | 1.0546 | 1.0515 | 1.0485
|  | TU | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.18864 | 0.22968 | 0.22853 | 0.2275 | 0.22662 | 0.22591 | 0.22538 | 0.22504 | 0.22489 | 0.22494 | 0.22429 | 0.22364
|  | TU | Maximum demand forecast(peak season) | Maximum demand (MVA) | TUMaximum demand forecast(peak season)Maximum demand (MVA) | 0.90427 | 1.101 | 1.0955 | 1.0906 | 1.0864 | 1.083 | 1.0804 | 1.0788 | 1.0781 | 1.0783 | 1.0752 | 1.0721
|  | TU | Maximum demand forecast(peak season) | Power factor (coincident) | TUMaximum demand forecast(peak season)Power factor (coincident) | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  | TU | Maximum demand forecast(non-peak season) | Maximum demand (MW) | TUMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.87866 | 0.7269 | 0.72953 | 0.73217 | 0.73493 | 0.738 | 0.7414 | 0.74499 | 0.74866 | 0.75234 | 0.75553 | 0.75874 |  | Summer
|  | TU | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | TUMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.20641 | 0.17076 | 0.17137 | 0.172 | 0.17264 | 0.17337 | 0.17416 | 0.17501 | 0.17587 | 0.17673 | 0.17748 | 0.17824 |  | Summer
|  | TU | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.90258 | 0.74669 | 0.74939 | 0.7521 | 0.75494 | 0.75809 | 0.76158 | 0.76527 | 0.76904 | 0.77282 | 0.7761 | 0.77939 |  | Summer
|  | TU | Hours exceeding | 95% of maximum demand | TUHours exceeding95% of maximum demand | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | TU | Hours exceeding | Firm capacity (continuous rating) | TUHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | TU | Hours exceeding | Firm capacity (short-term rating) | TUHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | TU | Regional diversity factor | Summer | TURegional diversity factorSummer | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749 | 0.49749
|  | TU | Regional diversity factor | Winter | TURegional diversity factorWinter | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929 | 0.3929
|  | TU | Load transfer capacity (MVA) | 1 | TULoad transfer capacity (MVA)1
|  | TU | Load transfer capacity (MVA) | 2 | TULoad transfer capacity (MVA)2
|  | TU | Load transfer capacity (MVA) | 3 | TULoad transfer capacity (MVA)3
|  | TU | Load transfer capacity (MVA) | 4 | TULoad transfer capacity (MVA)4
|  | TU | Load transfer capacity (MVA) | 5 | TULoad transfer capacity (MVA)5
|  | TU | Embedded generation capacity (MVA) | Units less than 100 kVA | TUEmbedded generation capacity (MVA)Units less than 100 kVA | 0.03491
|  | TU | Embedded generation capacity (MVA) | Units greater than 100 kVA | TUEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | UL | Substation capacity (winter and summer) (MVA) | Total | ULSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | UL | Substation capacity (winter and summer) (MVA) | Firm delivery | ULSubstation capacity (winter and summer) (MVA)Firm delivery | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
|  | UL | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | ULSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
|  | UL | Maximum demand forecast(peak season) | Maximum demand (MW) | ULMaximum demand forecast(peak season)Maximum demand (MW) | 32.3161 | 27.2395 | 26.6874 | 26.0556 | 25.1431 | 24.6573 | 24.1334 | 23.7734 | 23.5554 | 23.3665 | 23.3665 | 23.3665
|  | UL | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 3.0762 | 2.5929 | 2.5404 | 2.4802 | 2.3934 | 2.3471 | 2.2973 | 2.263 | 2.2422 | 2.2243 | 2.2243 | 2.2243
|  | UL | Maximum demand forecast(peak season) | Maximum demand (MVA) | ULMaximum demand forecast(peak season)Maximum demand (MVA) | 32.4622 | 27.3626 | 26.808 | 26.1734 | 25.2568 | 24.7687 | 24.2425 | 23.8809 | 23.6618 | 23.4722 | 23.4722 | 23.4722
|  | UL | Maximum demand forecast(peak season) | Power factor (coincident) | ULMaximum demand forecast(peak season)Power factor (coincident) | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955 | 0.9955
|  | UL | Maximum demand forecast(non-peak season) | Maximum demand (MW) | ULMaximum demand forecast(non-peak season)Maximum demand (MW) | 21.6248 | 20.4731 | 20.3017 | 20.0856 | 19.5951 | 19.5437 | 19.5275 | 19.4816 | 19.7538 | 19.8947 | 19.8148 | 19.7351 |  | Summer
|  | UL | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | ULMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 4.5908 | 4.3463 | 4.3099 | 4.264 | 4.1599 | 4.149 | 4.1455 | 4.1358 | 4.1936 | 4.2235 | 4.2065 | 4.1896 |  | Summer
|  | UL | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 22.1067 | 20.9293 | 20.7541 | 20.5333 | 20.0317 | 19.9793 | 19.9626 | 19.9158 | 20.194 | 20.3381 | 20.2564 | 20.1749 |  | Summer
|  | UL | Hours exceeding | 95% of maximum demand | ULHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | UL | Hours exceeding | Firm capacity (continuous rating) | ULHours exceedingFirm capacity (continuous rating)
|  | UL | Hours exceeding | Firm capacity (short-term rating) | ULHours exceedingFirm capacity (short-term rating)
|  | UL | Regional diversity factor | Summer | ULRegional diversity factorSummer | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321 | 0.95321
|  | UL | Regional diversity factor | Winter | ULRegional diversity factorWinter | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008 | 0.84008
|  | UL | Load transfer capacity (MVA) | 1 | ULLoad transfer capacity (MVA)1 | 6.8 | [11 empty] | Burnie
|  | UL | Load transfer capacity (MVA) | 2 | ULLoad transfer capacity (MVA)2 | 10.3 | [11 empty] | Devonport
|  | UL | Load transfer capacity (MVA) | 3 | ULLoad transfer capacity (MVA)3 | 3.4 | [11 empty] | Railton
|  | UL | Load transfer capacity (MVA) | 4 | ULLoad transfer capacity (MVA)4
|  | UL | Load transfer capacity (MVA) | 5 | ULLoad transfer capacity (MVA)5
|  | UL | Embedded generation capacity (MVA) | Units less than 100 kVA | ULEmbedded generation capacity (MVA)Units less than 100 kVA | 5.2517
|  | UL | Embedded generation capacity (MVA) | Units greater than 100 kVA | ULEmbedded generation capacity (MVA)Units greater than 100 kVA | 8.805
|  | WA | Substation capacity (winter and summer) (MVA) | Total | WASubstation capacity (winter and summer) (MVA)Total | 3.8[1] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | WA | Substation capacity (winter and summer) (MVA) | Firm delivery | WASubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WASubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Maximum demand forecast(peak season) | Maximum demand (MW) | WAMaximum demand forecast(peak season)Maximum demand (MW) | 0.72857 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132 | 0.58132
|  | WA | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.051614 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182 | 0.041182
|  | WA | Maximum demand forecast(peak season) | Maximum demand (MVA) | WAMaximum demand forecast(peak season)Maximum demand (MVA) | 0.73039 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277
|  | WA | Maximum demand forecast(peak season) | Power factor (coincident) | WAMaximum demand forecast(peak season)Power factor (coincident) | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975 | 0.9975
|  | WA | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WAMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.47194 | 0.34033 | 0.33961 | 0.33889 | 0.33824 | 0.33778 | 0.3375 | 0.33734 | 0.33722 | 0.33711 | 0.33665 | 0.33618 |  | Summer
|  | WA | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WAMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.072517 | 0.052294 | 0.052183 | 0.052072 | 0.051973 | 0.051901 | 0.051859 | 0.051834 | 0.051816 | 0.051799 | 0.051728 | 0.051657 |  | Summer
|  | WA | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.47748 | 0.34433 | 0.34359 | 0.34287 | 0.34221 | 0.34174 | 0.34146 | 0.3413 | 0.34118 | 0.34107 | 0.3406 | 0.34013 |  | Summer
|  | WA | Hours exceeding | 95% of maximum demand | WAHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | WA | Hours exceeding | Firm capacity (continuous rating) | WAHours exceedingFirm capacity (continuous rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | WA | Hours exceeding | Firm capacity (short-term rating) | WAHours exceedingFirm capacity (short-term rating) | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
|  | WA | Regional diversity factor | Summer | WARegional diversity factorSummer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | WA | Regional diversity factor | Winter | WARegional diversity factorWinter | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808 | 0.56808
|  | WA | Load transfer capacity (MVA) | 1 | WALoad transfer capacity (MVA)1 | 0.9 | [11 empty] | Arthurs Lake
|  | WA | Load transfer capacity (MVA) | 2 | WALoad transfer capacity (MVA)2
|  | WA | Load transfer capacity (MVA) | 3 | WALoad transfer capacity (MVA)3
|  | WA | Load transfer capacity (MVA) | 4 | WALoad transfer capacity (MVA)4
|  | WA | Load transfer capacity (MVA) | 5 | WALoad transfer capacity (MVA)5
|  | WA | Embedded generation capacity (MVA) | Units less than 100 kVA | WAEmbedded generation capacity (MVA)Units less than 100 kVA | 0.14125
|  | WA | Embedded generation capacity (MVA) | Units greater than 100 kVA | WAEmbedded generation capacity (MVA)Units greater than 100 kVA | 0
|  | WV | Substation capacity (winter and summer) (MVA) | Total | WVSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | WV | Substation capacity (winter and summer) (MVA) | Firm delivery | WVSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | WV | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WVSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
|  | WV | Maximum demand forecast(peak season) | Maximum demand (MW) | WVMaximum demand forecast(peak season)Maximum demand (MW) | 10.5233 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741 | 12.0741
|  | WV | Maximum demand forecast(peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(peak season)Reactive power (coincident) (MVAr) | 0.14883 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077 | 0.17077
|  | WV | Maximum demand forecast(peak season) | Maximum demand (MVA) | WVMaximum demand forecast(peak season)Maximum demand (MVA) | 10.5244 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753
|  | WV | Maximum demand forecast(peak season) | Power factor (coincident) | WVMaximum demand forecast(peak season)Power factor (coincident) | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999 | 0.9999
|  | WV | Maximum demand forecast(non-peak season) | Maximum demand (MW) | WVMaximum demand forecast(non-peak season)Maximum demand (MW) | 0.060654 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 |  | Summer
|  | WV | Maximum demand forecast(non-peak season) | Reactive power (coincident) (MVAr) | WVMaximum demand forecast(non-peak season)Reactive power (coincident) (MVAr) | 0.031693 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 | 4.1042 |  | Summer
|  | WV | Maximum demand forecast(non-peak season) | Maximum demand (MVA) |  | 0.068435 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 |  | Summer
|  | WV | Hours exceeding | 95% of maximum demand | WVHours exceeding95% of maximum demand | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
|  | WV | Hours exceeding | Firm capacity (continuous rating) | WVHours exceedingFirm capacity (continuous rating)
|  | WV | Hours exceeding | Firm capacity (short-term rating) | WVHours exceedingFirm capacity (short-term rating)
|  | WV | Regional diversity factor | Summer | WVRegional diversity factorSummer | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482 | 0.11482
|  | WV | Regional diversity factor | Winter | WVRegional diversity factorWinter | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585 | 0.95585
|  | WV | Load transfer capacity (MVA) | 1 | WVLoad transfer capacity (MVA)1
|  | WV | Load transfer capacity (MVA) | 2 | WVLoad transfer capacity (MVA)2
|  | WV | Load transfer capacity (MVA) | 3 | WVLoad transfer capacity (MVA)3
|  | WV | Load transfer capacity (MVA) | 4 | WVLoad transfer capacity (MVA)4
|  | WV | Load transfer capacity (MVA) | 5 | WVLoad transfer capacity (MVA)5
|  | WV | Embedded generation capacity (MVA) | Units less than 100 kVA | WVEmbedded generation capacity (MVA)Units less than 100 kVA | 1.9107
|  | WV | Embedded generation capacity (MVA) | Units greater than 100 kVA | WVEmbedded generation capacity (MVA)Units greater than 100 kVA | 0.265

## Zone subs & sub-trans lines
[5 empty] | Planning area |  |  |  | Greater Hobart | [5 empty] | Sub-transmission lines |  | Source substation
| Zone substation: |  |  |  | Supplying |  |  |  | Distribution lines | [5 empty] | 25305 | Bellerive1 | Lindisfarne
| Bellerive |  |  |  | Voltage |  |  |  | 33/11 kV | [5 empty] | 25310 | Bellerive2 | Lindisfarne
[5 empty] | Number of transformers |  |  |  | 2 | [6 empty] | Bellerive3
[5 empty] | Peaking season |  |  |  | Winter
Forecast | Parameter |  |  | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substation capacity (winter and summer) (MVA) | Total | Substation capacity (winter and summer) (MVA) | BEZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50
| Firm delivery | Substation capacity (winter and summer) (MVA) | BEZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9
| Short-term firm delivery | Substation capacity (winter and summer) (MVA) | BEZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
Sub-transmission line capacity (MVA) | Total (winter) | Sub-transmission lines capacity | BEZSub-transmission lines capacityTotal (winter) | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4
| Firm delivery (winter) | Sub-transmission lines capacity | BEZSub-transmission lines capacityFirm delivery (winter) | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4
| Total (summer) | Sub-transmission lines capacity | BEZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
| Firm delivery (summer) | Sub-transmission lines capacity | BEZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(peak season) | BEZMaximum demand forecast(peak season)Maximum demand (MVA) | 12.53 | 12.39 | 12.25 | 12.11 | 11.98 | 11.84 | 11.7 | 11.57 | 11.44 | 11.3 | 11.17 | 11.04
(Winter) | Power factor (coincident) | Maximum demand forecast(peak season) | BEZMaximum demand forecast(peak season)Power factor (coincident) | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954
Maximum demand forecast | Maximum demand (MVA) | Maximum demand forecast(non-peak season) | BEZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61
(Summer) | Power factor (coincident) | Maximum demand forecast(non-peak season) | BEZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
Hours exceeding | 95% of maximum demand | Hours exceeding | BEZHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Load transfer capacity (MVA) | Cambridge | Load transfer capacity (MVA)1 | BEZLoad transfer capacity (MVA)1 | 6.2
| Geilston Bay | Load transfer capacity (MVA)2 | BEZLoad transfer capacity (MVA)2 | 4.1
| Howrah | Load transfer capacity (MVA)3 | BEZLoad transfer capacity (MVA)3 | 3.1
| Rokeby | Load transfer capacity (MVA)4 | BEZLoad transfer capacity (MVA)4 | 3.1
Embedded generation capacity (MVA) | Units less than 100 kVA | Embedded generation capacity (MVA) | BEZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.876
| Units greater than 100 kVA | Embedded generation capacity (MVA) | BEZEmbedded generation capacity (MVA)Units greater than 100 kVA
| Notes |  |  | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Load reduction following transfer of load to new Rosny Park Zone Substation, as detailed in chapter 6 of this APR.
|  |  |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  |  | 2029
|  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50
|  |  |  | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  |  |  | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  |  |  | 12.53 | 12.39 | 12.25 | 12.11 | 11.98 | 11.84 | 11.7 | 11.57 | 11.44 | 11.3 | 11.17 | 11.04

## Zone data (hidden)
[6 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 14
[6 empty] | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | Load transfer point | Non-peaking season | Substation | Planning area | Supplying | Voltage | Number of transformers | Peaking season | Substation |  |  | Sub-transmission feeders | Source substation | Substation | Comment
Bellerive | BEZ | BEZ | Substation capacity (winter and summer) (MVA) | Total | BEZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 |  |  | Bellerive | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 1 | Bellerive1 | 25305 | Lindisfarne | Bellerive | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Load reduction following transfer of load to new Rosny Park Zone Substation, as detailed in chapter 6 of this APR.
Cambridge | CAZ | BEZ | Substation capacity (winter and summer) (MVA) | Firm delivery | BEZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9 |  |  | Cambridge | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 2 | Bellerive2 | 25310 | Lindisfarne | Claremont | [1] We propose to replace the supply transformers due to asset condition in 2020 with new units of standard size, as detailed in Section 6.9.3 of this APR.
Claremont | CLZ | BEZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | BEZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |  |  | Claremont | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Bellerive | 3 | Bellerive3 |  |  | Derwent Park | [1] We propose to replace the supply transformers due to asset condition in 2019 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard. [2] Currently in summer, and from 2024 in winter, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR.
Derwent Park | DPZ | BEZ | Sub-transmission lines capacity | Total (winter) | BEZSub-transmission lines capacityTotal (winter) | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 |  |  | Derwent Park | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Cambridge | 1 | Cambridge1 | 25309 | Lindisfarne | East Hobart | [1] From summer 2018, load is forecast to exceed the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR.
East Hobart | EHZ | BEZ | Sub-transmission lines capacity | Firm delivery (winter) | BEZSub-transmission lines capacityFirm delivery (winter) | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 | 19.4 |  |  | East Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Cambridge | 2 | Cambridge2 | 24402 | Mornington | Geilston Bay | [1] We propose to replace the supply transformers due to asset condition in 2025 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard.
Geilston Bay | GBZ | BEZ | Sub-transmission lines capacity | Total (summer) | BEZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  |  | Geilston Bay | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Cambridge | 3 | Cambridge3 |  |  | Howrah | [1] From this data, the load at Howrah Zone has currently exceeds the firm rating of the sub-transmission lines. However we believe the assigned rating of these lines are overly conservative and are currently investigating this. Therefore this has not been identified as a constraint in this APR.
Howrah | HOZ | BEZ | Sub-transmission lines capacity | Firm delivery (summer) | BEZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 |  |  | Howrah | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Claremont | 1 | Claremont1 | 10007 | Creek Road | New Town | [1] Currently in summer, and in winter from 2024, load exceeds the firm rating of the sub-transmission lines, as detailed in Section 6.9.2 of this APR. [1] We propose to replace the supply transformers due to asset condition in 2022 with new units of standard size, as detailed in Section 6.9.3 of this APR. Upon replacement of the transformers, the firm rating of the substation will be limited by the rating of the 11 kV switchboard.
New Town | NTZ | BEZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(peak season)Maximum demand (MVA) | 12.53 | 12.39 | 12.25 | 12.11 | 11.98 | 11.84 | 11.7 | 11.57 | 11.44 | 11.3 | 11.17 | 11.04 |  |  | New Town | Greater Hobart | Distribution lines | 33/11 kV | 2 | Winter | Claremont | 2 | Claremont2 | 10026 | Creek Road | Trial Harbour | [1] Load forecast step increase in 2018 from point load increase.
Rosny Park | RPZ | BEZ | Maximum demand forecast(peak season) | Power factor (coincident) | BEZMaximum demand forecast(peak season)Power factor (coincident) | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 |  |  | Rosny Park | Greater Hobart | Distribution lines | 33/11 kV | 1 | Winter | Claremont | 3 | Claremont3 |  |  | Gretna rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines.
Sandy Bay | SBZ | BEZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | BEZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 |  | Summer | Sandy Bay | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | Derwent Park | 1 | Derwent Park1 | 11021 | Risdon | New Norfolk rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] We propose to replace and rationalise the supply transformers due to asset condition in by 2019 with new 3 x 5 MVA units of standard size.
Summerleas | SUZ | BEZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | BEZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 |  | Summer | Summerleas | Kingston-South | Distribution lines | 33/11 kV | 1 | Winter | Derwent Park | 2 | Derwent Park2 | 11025 | Risdon | Richmond rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines. [2] We propose to replace the supply transformers due to asset condition in 2019 with new 2 x 5 MVA units of standard size. [3] Load currently exceeds the firm rating of the substation, however fast, remote load transfers exist to manage this. This has not been identified as a constraint in this APR.
Trial Harbour | THZ | BEZ | Hours exceeding | 95% of maximum demand | BEZHours exceeding95% of maximum demand | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 |  |  | Trial Harbour | West Coast | Distribution lines | 44/22 kV | 2 | Winter | Derwent Park | 3 | Derwent Park3 |  |  | Wayatinah rural | [1] Rural zone substations are supplied from within the distribution network, not by sub-transmission lines.
West Hobart | WHZ | BEZ | Load transfer capacity (MVA) | 1 | BEZLoad transfer capacity (MVA)1 | 6.2 | [11 empty] | Cambridge |  | West Hobart | Greater Hobart | Distribution lines | 33/11 kV | 3 | Winter | East Hobart | 1 | East Hobart1 | 11004 | Risdon
Gretna rural | GRZ | BEZ | Load transfer capacity (MVA) | 2 | BEZLoad transfer capacity (MVA)2 | 4.1 | [11 empty] | Geilston Bay |  | Gretna rural | Central | Distribution lines | 22/11 kV | 1 | Summer | East Hobart | 2 | East Hobart2 | 11005 | Risdon
New Norfolk rural | NNZ | BEZ | Load transfer capacity (MVA) | 3 | BEZLoad transfer capacity (MVA)3 | 3.1 | [11 empty] | Howrah |  | New Norfolk rural | Central | Distribution lines | 22/11 kV | 4 | Winter | East Hobart | 3 | East Hobart3 | 11006 | Risdon
Richmond rural | RIZ | BEZ | Load transfer capacity (MVA) | 4 | BEZLoad transfer capacity (MVA)4 | 3.1 | [11 empty] | Rokeby |  | Richmond rural | Eastern | Distribution lines | 22/11 kV | 2 | Winter | Geilston Bay | 1 | Geilston Bay1 | 25307 | Lindisfarne
Wayatinah rural | WYZ | BEZ | Embedded generation capacity (MVA) | Units less than 100 kVA | BEZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.876 | [13 empty] | Wayatinah rural | Central | Distribution lines | 11/22 kV | 1 | Winter | Geilston Bay | 2 | Geilston Bay2 | 25308 | Lindisfarne
|  | BEZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | BEZEmbedded generation capacity (MVA)Units greater than 100 kVA | [20 empty] | Geilston Bay | 3 | Geilston Bay3
|  | CAZ | Substation capacity (winter and summer) (MVA) | Total | CAZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | [8 empty] | Howrah | 1 | Howrah1 | 24401 | Mornington
|  | CAZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CAZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [8 empty] | Howrah | 2 | Howrah2 | 24406 | Mornington
|  | CAZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CAZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | [8 empty] | Howrah | 3 | Howrah3
|  | CAZ | Sub-transmission lines capacity | Total (winter) | CAZSub-transmission lines capacityTotal (winter) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | [8 empty] | New Town | 1 | New Town1 | 11023 | Risdon
|  | CAZ | Sub-transmission lines capacity | Firm delivery (winter) | CAZSub-transmission lines capacityFirm delivery (winter) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | [8 empty] | New Town | 2 | New Town2 | 11027 | Risdon
|  | CAZ | Sub-transmission lines capacity | Total (summer) | CAZSub-transmission lines capacityTotal (summer) | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | [8 empty] | New Town | 3 | New Town3
|  | CAZ | Sub-transmission lines capacity | Firm delivery (summer) | CAZSub-transmission lines capacityFirm delivery (summer) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | [8 empty] | Rosny Park | 1 | Rosny Park1 | 24405 | Mornington
|  | CAZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(peak season)Maximum demand (MVA) | 14.35 | 14.26 | 14.24 | 14.22 | 14.2 | 14.19 | 14.17 | 14.16 | 14.14 | 14.13 | 14.11 | 14.09 | [8 empty] | Rosny Park | 2 | Rosny Park2
|  | CAZ | Maximum demand forecast(peak season) | Power factor (coincident) | CAZMaximum demand forecast(peak season)Power factor (coincident) | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | 0.9906 | [8 empty] | Rosny Park | 3 | Rosny Park3
|  | CAZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CAZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 10.45 | 10.44 | 10.45 | 10.46 | 10.47 | 10.48 | 10.49 | 10.49 | 10.5 | 10.51 | 10.52 | 10.53 |  | Summer | [6 empty] | Sandy Bay | 1 | Sandy Bay1 | 10008 | Creek Road
|  | CAZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CAZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 | 0.9761 |  | Summer | [6 empty] | Sandy Bay | 2 | Sandy Bay2 | 10022 | Creek Road
|  | CAZ | Hours exceeding | 95% of maximum demand | CAZHours exceeding95% of maximum demand | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [8 empty] | Sandy Bay | 3 | Sandy Bay3 | 10024 | Creek Road
|  | CAZ | Load transfer capacity (MVA) | 1 | CAZLoad transfer capacity (MVA)1 | 7.4 | [11 empty] | Bellerive | [7 empty] | Summerleas | 1 | Summerleas1 | 36240 | Kingston
|  | CAZ | Load transfer capacity (MVA) | 2 | CAZLoad transfer capacity (MVA)2 | 7.4 | [11 empty] | Rokeby | [7 empty] | Summerleas | 2 | Summerleas2
|  | CAZ | Load transfer capacity (MVA) | 3 | CAZLoad transfer capacity (MVA)3 | [20 empty] | Summerleas | 3 | Summerleas3
|  | CAZ | Load transfer capacity (MVA) | 4 | CAZLoad transfer capacity (MVA)4 | [20 empty] | Trial Harbour | 1 | Trial Harbour1 | 97013 | 50[1]
|  | CAZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CAZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.794 | [19 empty] | Trial Harbour | 2 | Trial Harbour2
|  | CAZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CAZEmbedded generation capacity (MVA)Units greater than 100 kVA | [20 empty] | Trial Harbour | 3 | Trial Harbour3
|  | CLZ | Substation capacity (winter and summer) (MVA) | Total | CLZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [8 empty] | West Hobart | 1 | West Hobart1 | 10001 | Creek Road
|  | CLZ | Substation capacity (winter and summer) (MVA) | Firm delivery | CLZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 25[1] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [8 empty] | West Hobart | 2 | West Hobart2 | 10002 | Creek Road
|  | CLZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | CLZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | [8 empty] | West Hobart | 3 | West Hobart3 | 10003 | Creek Road
|  | CLZ | Sub-transmission lines capacity | Total (winter) | CLZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | [8 empty] | Gretna rural | 1 | Gretna rural1 | [1]
|  | CLZ | Sub-transmission lines capacity | Firm delivery (winter) | CLZSub-transmission lines capacityFirm delivery (winter) | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | [8 empty] | Gretna rural | 2 | Gretna rural2
|  | CLZ | Sub-transmission lines capacity | Total (summer) | CLZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | [8 empty] | Gretna rural | 3 | Gretna rural3
|  | CLZ | Sub-transmission lines capacity | Firm delivery (summer) | CLZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | [8 empty] | New Norfolk rural | 1 | New Norfolk rural1 | [1]
|  | CLZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(peak season)Maximum demand (MVA) | 19.99 | 20.1 | 20.21 | 20.33 | 20.44 | 20.55 | 20.67 | 20.79 | 20.9 | 21.02 | 21.14 | 21.26 | [8 empty] | New Norfolk rural | 2 | New Norfolk rural2
|  | CLZ | Maximum demand forecast(peak season) | Power factor (coincident) | CLZMaximum demand forecast(peak season)Power factor (coincident) | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | [8 empty] | New Norfolk rural | 3 | New Norfolk rural3
|  | CLZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | CLZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 12.42 | 12.53 | 12.64 | 12.76 | 12.87 | 12.98 | 13.1 | 13.21 | 13.33 | 13.44 | 13.56 | 13.68 |  | Summer | [6 empty] | Richmond rural | 1 | Richmond rural1 | [1]
|  | CLZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | CLZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 |  | Summer | [6 empty] | Richmond rural | 2 | Richmond rural2
|  | CLZ | Hours exceeding | 95% of maximum demand | CLZHours exceeding95% of maximum demand | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | [8 empty] | Richmond rural | 3 | Richmond rural3
|  | CLZ | Load transfer capacity (MVA) | 1 | CLZLoad transfer capacity (MVA)1 | 4.2 | [11 empty] | Bridgewater | [7 empty] | Wayatinah rural | 1 | Wayatinah rural1 | [1]
|  | CLZ | Load transfer capacity (MVA) | 2 | CLZLoad transfer capacity (MVA)2 | 5.9 | [11 empty] | Chapel Street | [7 empty] | Wayatinah rural | 2 | Wayatinah rural2
|  | CLZ | Load transfer capacity (MVA) | 3 | CLZLoad transfer capacity (MVA)3 | 0.8 | [11 empty] | New Norfolk | [7 empty] | Wayatinah rural | 3 | Wayatinah rural3
|  | CLZ | Load transfer capacity (MVA) | 4 | CLZLoad transfer capacity (MVA)4
|  | CLZ | Embedded generation capacity (MVA) | Units less than 100 kVA | CLZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.318
|  | CLZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | CLZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | DPZ | Substation capacity (winter and summer) (MVA) | Total | DPZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50
|  | DPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | DPZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | DPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | DPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | DPZ | Sub-transmission lines capacity | Total (winter) | DPZSub-transmission lines capacityTotal (winter) | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1
|  | DPZ | Sub-transmission lines capacity | Firm delivery (winter) | DPZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
|  | DPZ | Sub-transmission lines capacity | Total (summer) | DPZSub-transmission lines capacityTotal (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | DPZ | Sub-transmission lines capacity | Firm delivery (summer) | DPZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | DPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(peak season)Maximum demand (MVA) | 21.6 | 21.72 | 21.84 | 21.96 | 22.08 | 22.2 | 22.32 | 22.45 | 22.57 | 22.69 | 22.82 | 22.94
|  | DPZ | Maximum demand forecast(peak season) | Power factor (coincident) | DPZMaximum demand forecast(peak season)Power factor (coincident) | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742
|  | DPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | DPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 13.14 | 13.23 | 13.31 | 13.4 | 13.49 | 13.58 | 13.67 | 13.76 | 13.85 | 13.94 | 14.03 | 14.13 |  | Summer
|  | DPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | DPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 |  | Summer
|  | DPZ | Hours exceeding | 95% of maximum demand | DPZHours exceeding95% of maximum demand | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
|  | DPZ | Load transfer capacity (MVA) | 1 | DPZLoad transfer capacity (MVA)1 | 13.9 | [11 empty] | Chapel Street
|  | DPZ | Load transfer capacity (MVA) | 2 | DPZLoad transfer capacity (MVA)2 | 9.4 | [11 empty] | New Town
|  | DPZ | Load transfer capacity (MVA) | 3 | DPZLoad transfer capacity (MVA)3
|  | DPZ | Load transfer capacity (MVA) | 4 | DPZLoad transfer capacity (MVA)4
|  | DPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | DPZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.786 | 3 2019: 0.786
|  | DPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | DPZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | EHZ | Substation capacity (winter and summer) (MVA) | Total | EHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | EHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | EHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | EHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | EHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | EHZ | Sub-transmission lines capacity | Total (winter) | EHZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
|  | EHZ | Sub-transmission lines capacity | Firm delivery (winter) | EHZSub-transmission lines capacityFirm delivery (winter) | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2 | 47.2
|  | EHZ | Sub-transmission lines capacity | Total (summer) | EHZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
|  | EHZ | Sub-transmission lines capacity | Firm delivery (summer) | EHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | EHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(peak season)Maximum demand (MVA) | 25.12 | 32.65 | 33.16 | 33.31 | 33.46 | 33.61 | 33.76 | 33.91 | 34.07 | 34.22 | 34.38 | 34.53
|  | EHZ | Maximum demand forecast(peak season) | Power factor (coincident) | EHZMaximum demand forecast(peak season)Power factor (coincident) | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742
|  | EHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | EHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 20.35 | 28.06 | 28.57 | 28.72 | 28.86 | 29 | 29.15 | 29.29 | 29.44 | 29.59 | 29.74 | 29.89 |  | Summer
|  | EHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | EHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 |  | Summer
|  | EHZ | Hours exceeding | 95% of maximum demand | EHZHours exceeding95% of maximum demand | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5
|  | EHZ | Load transfer capacity (MVA) | 1 | EHZLoad transfer capacity (MVA)1 | 4.3 | [11 empty] | Geilston Bay
|  | EHZ | Load transfer capacity (MVA) | 2 | EHZLoad transfer capacity (MVA)2 | 9.9 | [11 empty] | North Hobart
|  | EHZ | Load transfer capacity (MVA) | 3 | EHZLoad transfer capacity (MVA)3 | 11.3 | [11 empty] | West Hobart
|  | EHZ | Load transfer capacity (MVA) | 4 | EHZLoad transfer capacity (MVA)4
|  | EHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | EHZEmbedded generation capacity (MVA)Units less than 100 kVA | 0.356
|  | EHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | EHZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | GBZ | Substation capacity (winter and summer) (MVA) | Total | GBZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50
|  | GBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GBZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[1] | 22.9 | 22.9 | 22.9 | 22.9
|  | GBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | GBZ | Sub-transmission lines capacity | Total (winter) | GBZSub-transmission lines capacityTotal (winter) | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 46.3
|  | GBZ | Sub-transmission lines capacity | Firm delivery (winter) | GBZSub-transmission lines capacityFirm delivery (winter) | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
|  | GBZ | Sub-transmission lines capacity | Total (summer) | GBZSub-transmission lines capacityTotal (summer) | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
|  | GBZ | Sub-transmission lines capacity | Firm delivery (summer) | GBZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | GBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(peak season)Maximum demand (MVA) | 16.94 | 16.76 | 16.59 | 16.41 | 16.24 | 16.07 | 15.9 | 15.73 | 15.56 | 15.4 | 15.23 | 15.07
|  | GBZ | Maximum demand forecast(peak season) | Power factor (coincident) | GBZMaximum demand forecast(peak season)Power factor (coincident) | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954 | 0.9954
|  | GBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 |  | Summer
|  | GBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 | 0.999 |  | Summer
|  | GBZ | Hours exceeding | 95% of maximum demand | GBZHours exceeding95% of maximum demand | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | GBZ | Load transfer capacity (MVA) | 1 | GBZLoad transfer capacity (MVA)1 | 5.1 | [11 empty] | Bellerive
|  | GBZ | Load transfer capacity (MVA) | 2 | GBZLoad transfer capacity (MVA)2 | 5.1 | [11 empty] | Derwent Park
|  | GBZ | Load transfer capacity (MVA) | 3 | GBZLoad transfer capacity (MVA)3 | 3.8 | [11 empty] | West Hobart
|  | GBZ | Load transfer capacity (MVA) | 4 | GBZLoad transfer capacity (MVA)4
|  | GBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GBZEmbedded generation capacity (MVA)Units less than 100 kVA | 1.491
|  | GBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GBZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | HOZ | Substation capacity (winter and summer) (MVA) | Total | HOZSubstation capacity (winter and summer) (MVA)Total | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | HOZ | Substation capacity (winter and summer) (MVA) | Firm delivery | HOZSubstation capacity (winter and summer) (MVA)Firm delivery | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | HOZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | HOZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5
|  | HOZ | Sub-transmission lines capacity | Total (winter) | HOZSub-transmission lines capacityTotal (winter) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
|  | HOZ | Sub-transmission lines capacity | Firm delivery (winter) | HOZSub-transmission lines capacityFirm delivery (winter) | 18.3[1] | 18.3[1] | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | HOZ | Sub-transmission lines capacity | Total (summer) | HOZSub-transmission lines capacityTotal (summer) | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
|  | HOZ | Sub-transmission lines capacity | Firm delivery (summer) | HOZSub-transmission lines capacityFirm delivery (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | HOZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(peak season)Maximum demand (MVA) | 17.42 | 17.52 | 17.63 | 17.73 | 17.84 | 17.94 | 18.05 | 18.15 | 18.26 | 18.37 | 18.48 | 18.59
|  | HOZ | Maximum demand forecast(peak season) | Power factor (coincident) | HOZMaximum demand forecast(peak season)Power factor (coincident) | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966
|  | HOZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | HOZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 9.93 | 9.95 | 9.97 | 9.99 | 10.01 | 10.03 | 10.05 | 10.07 | 10.1 | 10.12 | 10.14 | 10.16 |  | Summer
|  | HOZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | HOZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 |  | Summer
|  | HOZ | Hours exceeding | 95% of maximum demand | HOZHours exceeding95% of maximum demand | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | HOZ | Load transfer capacity (MVA) | 1 | HOZLoad transfer capacity (MVA)1 | 9.93: 2.4 | Bellerive
|  | HOZ | Load transfer capacity (MVA) | 2 | HOZLoad transfer capacity (MVA)2 | 9.93: 7.1 | Rokeby
|  | HOZ | Load transfer capacity (MVA) | 3 | HOZLoad transfer capacity (MVA)3
|  | HOZ | Load transfer capacity (MVA) | 4 | HOZLoad transfer capacity (MVA)4
|  | HOZ | Embedded generation capacity (MVA) | Units less than 100 kVA | HOZEmbedded generation capacity (MVA)Units less than 100 kVA | 9.93: 1.905
|  | HOZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | HOZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | NTZ | Substation capacity (winter and summer) (MVA) | Total | NTZSubstation capacity (winter and summer) (MVA)Total | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50
|  | NTZ | Substation capacity (winter and summer) (MVA) | Firm delivery | NTZSubstation capacity (winter and summer) (MVA)Firm delivery | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.9[2] | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | NTZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NTZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9
|  | NTZ | Sub-transmission lines capacity | Total (winter) | NTZSub-transmission lines capacityTotal (winter) | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9 | 42.9
|  | NTZ | Sub-transmission lines capacity | Firm delivery (winter) | NTZSub-transmission lines capacityFirm delivery (winter) | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
|  | NTZ | Sub-transmission lines capacity | Total (summer) | NTZSub-transmission lines capacityTotal (summer) | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
|  | NTZ | Sub-transmission lines capacity | Firm delivery (summer) | NTZSub-transmission lines capacityFirm delivery (summer) | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
|  | NTZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(peak season)Maximum demand (MVA) | 22.02 | 22.14 | 22.26 | 22.38 | 22.5 | 22.63 | 22.75 | 22.88 | 23 | 23.13 | 23.26 | 23.38
|  | NTZ | Maximum demand forecast(peak season) | Power factor (coincident) | NTZMaximum demand forecast(peak season)Power factor (coincident) | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742 | 0.9742
|  | NTZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | NTZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 14.47 | 14.56 | 14.66 | 14.76 | 14.85 | 14.95 | 15.05 | 15.15 | 15.25 | 15.35 | 15.45 | 15.55 |  | Summer
|  | NTZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | NTZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 | 0.9505 |  | Summer
|  | NTZ | Hours exceeding | 95% of maximum demand | NTZHours exceeding95% of maximum demand | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
|  | NTZ | Load transfer capacity (MVA) | 1 | NTZLoad transfer capacity (MVA)1 | 14.47: 3.9 | Chapel Street
|  | NTZ | Load transfer capacity (MVA) | 2 | NTZLoad transfer capacity (MVA)2 | 14.47: 4.8 | Derwent Park
|  | NTZ | Load transfer capacity (MVA) | 3 | NTZLoad transfer capacity (MVA)3 | 14.47: 3.9 | East Hobart
|  | NTZ | Load transfer capacity (MVA) | 4 | NTZLoad transfer capacity (MVA)4 | 14.47: 7.7 | North Hobart
|  | NTZ | Embedded generation capacity (MVA) | Units less than 100 kVA | NTZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 1.446
|  | NTZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | NTZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | RPZ | Substation capacity (winter and summer) (MVA) | Total | RPZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | RPZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RPZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RPZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Sub-transmission lines capacity | Total (winter) | RPZSub-transmission lines capacityTotal (winter) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | RPZ | Sub-transmission lines capacity | Firm delivery (winter) | RPZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Sub-transmission lines capacity | Total (summer) | RPZSub-transmission lines capacityTotal (summer) | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
|  | RPZ | Sub-transmission lines capacity | Firm delivery (summer) | RPZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | RPZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(peak season)Maximum demand (MVA) | 14.19 | 16.45 | 16.45 | 16.45 | 16.46 | 16.46 | 16.46 | 16.46 | 16.46 | 16.46 | 16.47 | 16.47
|  | RPZ | Maximum demand forecast(peak season) | Power factor (coincident) | RPZMaximum demand forecast(peak season)Power factor (coincident) | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966 | 0.9966
|  | RPZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RPZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 10.96 | 10.97 | 10.97 | 10.98 | 10.98 | 10.99 | 10.99 | 10.99 | 11 | 11 | 11.01 | 11.01 |  | Summer
|  | RPZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RPZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 | 0.9995 |  | Summer
|  | RPZ | Hours exceeding | 95% of maximum demand | RPZHours exceeding95% of maximum demand | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
|  | RPZ | Load transfer capacity (MVA) | 1 | RPZLoad transfer capacity (MVA)1
|  | RPZ | Load transfer capacity (MVA) | 2 | RPZLoad transfer capacity (MVA)2
|  | RPZ | Load transfer capacity (MVA) | 3 | RPZLoad transfer capacity (MVA)3
|  | RPZ | Load transfer capacity (MVA) | 4 | RPZLoad transfer capacity (MVA)4
|  | RPZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RPZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 1.342
|  | RPZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RPZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | SBZ | Substation capacity (winter and summer) (MVA) | Total | SBZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | SBZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SBZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SBZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SBZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | SBZ | Sub-transmission lines capacity | Total (winter) | SBZSub-transmission lines capacityTotal (winter) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
|  | SBZ | Sub-transmission lines capacity | Firm delivery (winter) | SBZSub-transmission lines capacityFirm delivery (winter) | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3
|  | SBZ | Sub-transmission lines capacity | Total (summer) | SBZSub-transmission lines capacityTotal (summer) | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
|  | SBZ | Sub-transmission lines capacity | Firm delivery (summer) | SBZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | SBZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(peak season)Maximum demand (MVA) | 37.56 | 37.77 | 37.98 | 38.19 | 38.41 | 38.62 | 38.84 | 39.05 | 39.27 | 39.49 | 39.71 | 39.94
|  | SBZ | Maximum demand forecast(peak season) | Power factor (coincident) | SBZMaximum demand forecast(peak season)Power factor (coincident) | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827
|  | SBZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SBZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 24.1 | 24.31 | 24.53 | 24.74 | 24.96 | 25.18 | 25.4 | 25.62 | 25.85 | 26.08 | 26.31 | 26.54 |  | Summer
|  | SBZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SBZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 |  | Summer
|  | SBZ | Hours exceeding | 95% of maximum demand | SBZHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | SBZ | Load transfer capacity (MVA) | 1 | SBZLoad transfer capacity (MVA)1 | 14.47: 1.7 | Kingston
|  | SBZ | Load transfer capacity (MVA) | 2 | SBZLoad transfer capacity (MVA)2 | 14.47: 13.2 | West Hobart
|  | SBZ | Load transfer capacity (MVA) | 3 | SBZLoad transfer capacity (MVA)3
|  | SBZ | Load transfer capacity (MVA) | 4 | SBZLoad transfer capacity (MVA)4
|  | SBZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SBZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 3.212; 14.56: 3.212
|  | SBZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SBZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | SUZ | Substation capacity (winter and summer) (MVA) | Total | SUZSubstation capacity (winter and summer) (MVA)Total | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | SUZ | Substation capacity (winter and summer) (MVA) | Firm delivery | SUZSubstation capacity (winter and summer) (MVA)Firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | SUZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Sub-transmission lines capacity | Total (winter) | SUZSub-transmission lines capacityTotal (winter) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3
|  | SUZ | Sub-transmission lines capacity | Firm delivery (winter) | SUZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Sub-transmission lines capacity | Total (summer) | SUZSub-transmission lines capacityTotal (summer) | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3 | 21.3
|  | SUZ | Sub-transmission lines capacity | Firm delivery (summer) | SUZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SUZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(peak season)Maximum demand (MVA) | 10.91 | 11.02 | 11.13 | 11.24 | 11.34 | 11.45 | 11.57 | 11.68 | 11.79 | 11.91 | 12.02 | 12.14
|  | SUZ | Maximum demand forecast(peak season) | Power factor (coincident) | SUZMaximum demand forecast(peak season)Power factor (coincident) | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965 | 0.9965
|  | SUZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | SUZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 7.07 | 7.03 | 6.98 | 6.93 | 6.89 | 6.84 | 6.79 | 6.75 | 6.7 | 6.66 | 6.61 | 6.57 |  | Summer
|  | SUZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | SUZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 | 0.9994 |  | Summer
|  | SUZ | Hours exceeding | 95% of maximum demand | SUZHours exceeding95% of maximum demand | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
|  | SUZ | Load transfer capacity (MVA) | 1 | SUZLoad transfer capacity (MVA)1 | 14.47: 4.9 | Kingston
|  | SUZ | Load transfer capacity (MVA) | 2 | SUZLoad transfer capacity (MVA)2
|  | SUZ | Load transfer capacity (MVA) | 3 | SUZLoad transfer capacity (MVA)3
|  | SUZ | Load transfer capacity (MVA) | 4 | SUZLoad transfer capacity (MVA)4
|  | SUZ | Embedded generation capacity (MVA) | Units less than 100 kVA | SUZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 1.311
|  | SUZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | SUZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | THZ | Substation capacity (winter and summer) (MVA) | Total | THZSubstation capacity (winter and summer) (MVA)Total | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  | THZ | Substation capacity (winter and summer) (MVA) | Firm delivery | THZSubstation capacity (winter and summer) (MVA)Firm delivery | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
|  | THZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | THZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | THZ | Sub-transmission lines capacity | Total (winter) | THZSub-transmission lines capacityTotal (winter) | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
|  | THZ | Sub-transmission lines capacity | Firm delivery (winter) | THZSub-transmission lines capacityFirm delivery (winter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | THZ | Sub-transmission lines capacity | Total (summer) | THZSub-transmission lines capacityTotal (summer) | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
|  | THZ | Sub-transmission lines capacity | Firm delivery (summer) | THZSub-transmission lines capacityFirm delivery (summer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | THZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | THZMaximum demand forecast(peak season)Maximum demand (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.09 | 2.09 | 2.09 | 2.09 | 2.08 | 2.08 | 2.08
|  | THZ | Maximum demand forecast(peak season) | Power factor (coincident) | THZMaximum demand forecast(peak season)Power factor (coincident) | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298 | 0.9298
|  | THZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | THZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.35 | 1.35 | 1.35 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.33 |  | Summer
|  | THZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | THZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 | 0.8543 |  | Summer
|  | THZ | Hours exceeding | 95% of maximum demand | THZHours exceeding95% of maximum demand | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | THZ | Load transfer capacity (MVA) | 1 | THZLoad transfer capacity (MVA)1
|  | THZ | Load transfer capacity (MVA) | 2 | THZLoad transfer capacity (MVA)2
|  | THZ | Load transfer capacity (MVA) | 3 | THZLoad transfer capacity (MVA)3
|  | THZ | Load transfer capacity (MVA) | 4 | THZLoad transfer capacity (MVA)4
|  | THZ | Embedded generation capacity (MVA) | Units less than 100 kVA | THZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 0.11
|  | THZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | THZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | WHZ | Substation capacity (winter and summer) (MVA) | Total | WHZSubstation capacity (winter and summer) (MVA)Total | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | WHZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WHZSubstation capacity (winter and summer) (MVA)Firm delivery | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | WHZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WHZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
|  | WHZ | Sub-transmission lines capacity | Total (winter) | WHZSub-transmission lines capacityTotal (winter) | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9 | 67.9
|  | WHZ | Sub-transmission lines capacity | Firm delivery (winter) | WHZSub-transmission lines capacityFirm delivery (winter) | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3 | 45.3
|  | WHZ | Sub-transmission lines capacity | Total (summer) | WHZSub-transmission lines capacityTotal (summer) | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
|  | WHZ | Sub-transmission lines capacity | Firm delivery (summer) | WHZSub-transmission lines capacityFirm delivery (summer) | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.9
|  | WHZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(peak season)Maximum demand (MVA) | 34.55 | 35.35 | 35.55 | 35.74 | 35.94 | 36.14 | 36.34 | 36.54 | 36.74 | 36.94 | 37.14 | 37.35
|  | WHZ | Maximum demand forecast(peak season) | Power factor (coincident) | WHZMaximum demand forecast(peak season)Power factor (coincident) | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827 | 0.9827
|  | WHZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WHZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 21.82 | 22.62 | 22.81 | 23.01 | 23.21 | 23.4 | 23.6 | 23.81 | 24.01 | 24.22 | 24.43 | 24.63 |  | Summer
|  | WHZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WHZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 | 0.9904 |  | Summer
|  | WHZ | Hours exceeding | 95% of maximum demand | WHZHours exceeding95% of maximum demand | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  | WHZ | Load transfer capacity (MVA) | 1 | WHZLoad transfer capacity (MVA)1 | 14.47: 8.5 | East Hobart
|  | WHZ | Load transfer capacity (MVA) | 2 | WHZLoad transfer capacity (MVA)2 | 14.47: 6.4 | North Hobart
|  | WHZ | Load transfer capacity (MVA) | 3 | WHZLoad transfer capacity (MVA)3 | 14.47: 8.5 | Sandy Bay
|  | WHZ | Load transfer capacity (MVA) | 4 | WHZLoad transfer capacity (MVA)4
|  | WHZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WHZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 1.957
|  | WHZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WHZEmbedded generation capacity (MVA)Units greater than 100 kVA | 14.47: 1.1
|  | GRZ | Substation capacity (winter and summer) (MVA) | Total | GRZSubstation capacity (winter and summer) (MVA)Total | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | GRZ | Substation capacity (winter and summer) (MVA) | Firm delivery | GRZSubstation capacity (winter and summer) (MVA)Firm delivery | bar: 14.47 to 15.55
|  | GRZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | GRZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
|  | GRZ | Sub-transmission lines capacity | Total (winter) | GRZSub-transmission lines capacityTotal (winter)
|  | GRZ | Sub-transmission lines capacity | Firm delivery (winter) | GRZSub-transmission lines capacityFirm delivery (winter)
|  | GRZ | Sub-transmission lines capacity | Total (summer) | GRZSub-transmission lines capacityTotal (summer)
|  | GRZ | Sub-transmission lines capacity | Firm delivery (summer) | GRZSub-transmission lines capacityFirm delivery (summer)
|  | GRZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(peak season)Maximum demand (MVA) | 1.46 | 1.45 | 1.45 | 1.44 | 1.44 | 1.43 | 1.43 | 1.42 | 1.42 | 1.41 | 1.41 | 1.4
|  | GRZ | Maximum demand forecast(peak season) | Power factor (coincident) | GRZMaximum demand forecast(peak season)Power factor (coincident) | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606
|  | GRZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | GRZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 0.55 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 |  | Winter
|  | GRZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | GRZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 |  | Winter
|  | GRZ | Hours exceeding | 95% of maximum demand | GRZHours exceeding95% of maximum demand | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | GRZ | Load transfer capacity (MVA) | 1 | GRZLoad transfer capacity (MVA)1
|  | GRZ | Load transfer capacity (MVA) | 2 | GRZLoad transfer capacity (MVA)2
|  | GRZ | Load transfer capacity (MVA) | 3 | GRZLoad transfer capacity (MVA)3
|  | GRZ | Load transfer capacity (MVA) | 4 | GRZLoad transfer capacity (MVA)4
|  | GRZ | Embedded generation capacity (MVA) | Units less than 100 kVA | GRZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 0.116
|  | GRZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | GRZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | NNZ | Substation capacity (winter and summer) (MVA) | Total | NNZSubstation capacity (winter and summer) (MVA)Total | 10 | 10 | 10 | 15[2] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | NNZ | Substation capacity (winter and summer) (MVA) | Firm delivery | NNZSubstation capacity (winter and summer) (MVA)Firm delivery | 7.5 | 7.5 | 7.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | NNZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | NNZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 10 | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
|  | NNZ | Sub-transmission lines capacity | Total (winter) | NNZSub-transmission lines capacityTotal (winter)
|  | NNZ | Sub-transmission lines capacity | Firm delivery (winter) | NNZSub-transmission lines capacityFirm delivery (winter)
|  | NNZ | Sub-transmission lines capacity | Total (summer) | NNZSub-transmission lines capacityTotal (summer)
|  | NNZ | Sub-transmission lines capacity | Firm delivery (summer) | NNZSub-transmission lines capacityFirm delivery (summer)
|  | NNZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | NNZMaximum demand forecast(peak season)Maximum demand (MVA) | 7.36 | 7.34 | 7.33 | 7.32 | 7.31 | 7.29 | 7.28 | 7.27 | 7.26 | 7.25 | 7.23 | 7.22
|  | NNZ | Maximum demand forecast(peak season) | Power factor (coincident) | NNZMaximum demand forecast(peak season)Power factor (coincident) | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881 | 0.9881
|  | NNZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | NNZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 5.37 | 5.35 | 5.33 | 5.32 | 5.3 | 5.28 | 5.26 | 5.24 | 5.22 | 5.2 | 5.19 | 5.17 |  | Summer
|  | NNZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | NNZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 | 0.9606 |  | Summer
|  | NNZ | Hours exceeding | 95% of maximum demand | NNZHours exceeding95% of maximum demand | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
|  | NNZ | Load transfer capacity (MVA) | 1 | NNZLoad transfer capacity (MVA)1
|  | NNZ | Load transfer capacity (MVA) | 2 | NNZLoad transfer capacity (MVA)2
|  | NNZ | Load transfer capacity (MVA) | 3 | NNZLoad transfer capacity (MVA)3
|  | NNZ | Load transfer capacity (MVA) | 4 | NNZLoad transfer capacity (MVA)4
|  | NNZ | Embedded generation capacity (MVA) | Units less than 100 kVA | NNZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 0.966
|  | NNZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | NNZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | RIZ | Substation capacity (winter and summer) (MVA) | Total | RIZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 10[2] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | RIZ | Substation capacity (winter and summer) (MVA) | Firm delivery | RIZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RIZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | RIZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
|  | RIZ | Sub-transmission lines capacity | Total (winter) | RIZSub-transmission lines capacityTotal (winter)
|  | RIZ | Sub-transmission lines capacity | Firm delivery (winter) | RIZSub-transmission lines capacityFirm delivery (winter)
|  | RIZ | Sub-transmission lines capacity | Total (summer) | RIZSub-transmission lines capacityTotal (summer)
|  | RIZ | Sub-transmission lines capacity | Firm delivery (summer) | RIZSub-transmission lines capacityFirm delivery (summer)
|  | RIZ | Maximum demand forecast(peak season)[3] | Maximum demand (MVA) | RIZMaximum demand forecast(peak season)[3]Maximum demand (MVA) | 3.36 | 3.36 | 3.35 | 3.35 | 3.34 | 3.34 | 3.33 | 3.33 | 3.32 | 3.32 | 3.31 | 3.31
|  | RIZ | Maximum demand forecast(peak season) | Power factor (coincident) | RIZMaximum demand forecast(peak season)Power factor (coincident) | bar: 14.47 to 15.55
|  | RIZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | RIZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 |  | Summer
|  | RIZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | RIZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998 |  | Summer
|  | RIZ | Hours exceeding | 95% of maximum demand | RIZHours exceeding95% of maximum demand | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | RIZ | Load transfer capacity (MVA) | 1 | RIZLoad transfer capacity (MVA)1
|  | RIZ | Load transfer capacity (MVA) | 2 | RIZLoad transfer capacity (MVA)2
|  | RIZ | Load transfer capacity (MVA) | 3 | RIZLoad transfer capacity (MVA)3
|  | RIZ | Load transfer capacity (MVA) | 4 | RIZLoad transfer capacity (MVA)4
|  | RIZ | Embedded generation capacity (MVA) | Units less than 100 kVA | RIZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 0.706
|  | RIZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | RIZEmbedded generation capacity (MVA)Units greater than 100 kVA
|  | WYZ | Substation capacity (winter and summer) (MVA) | Total | WYZSubstation capacity (winter and summer) (MVA)Total | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | WYZ | Substation capacity (winter and summer) (MVA) | Firm delivery | WYZSubstation capacity (winter and summer) (MVA)Firm delivery | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  | WYZ | Substation capacity (winter and summer) (MVA) | Short-term firm delivery | WYZSubstation capacity (winter and summer) (MVA)Short-term firm delivery | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | WYZ | Sub-transmission lines capacity | Total (winter) | WYZSub-transmission lines capacityTotal (winter)
|  | WYZ | Sub-transmission lines capacity | Firm delivery (winter) | WYZSub-transmission lines capacityFirm delivery (winter)
|  | WYZ | Sub-transmission lines capacity | Total (summer) | WYZSub-transmission lines capacityTotal (summer)
|  | WYZ | Sub-transmission lines capacity | Firm delivery (summer) | WYZSub-transmission lines capacityFirm delivery (summer)
|  | WYZ | Maximum demand forecast(peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(peak season)Maximum demand (MVA) | 1.3011 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837
|  | WYZ | Maximum demand forecast(peak season) | Power factor (coincident) | WYZMaximum demand forecast(peak season)Power factor (coincident) | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109 | 0.9109
|  | WYZ | Maximum demand forecast(non-peak season) | Maximum demand (MVA) | WYZMaximum demand forecast(non-peak season)Maximum demand (MVA) | 1.231 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 |  | Winter
|  | WYZ | Maximum demand forecast(non-peak season) | Power factor (coincident) | WYZMaximum demand forecast(non-peak season)Power factor (coincident) | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 | 0.9825 |  | Winter
|  | WYZ | Hours exceeding | 95% of maximum demand | WYZHours exceeding95% of maximum demand | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | WYZ | Load transfer capacity (MVA) | 1 | WYZLoad transfer capacity (MVA)1
|  | WYZ | Load transfer capacity (MVA) | 2 | WYZLoad transfer capacity (MVA)2
|  | WYZ | Load transfer capacity (MVA) | 3 | WYZLoad transfer capacity (MVA)3
|  | WYZ | Load transfer capacity (MVA) | 4 | WYZLoad transfer capacity (MVA)4
|  | WYZ | Embedded generation capacity (MVA) | Units less than 100 kVA | WYZEmbedded generation capacity (MVA)Units less than 100 kVA | 14.47: 0
|  | WYZ | Embedded generation capacity (MVA) | Units greater than 100 kVA | WYZEmbedded generation capacity (MVA)Units greater than 100 kVA

## Distribution feeder max. demand
Distribution feeder maximum demand, (Amps) 2019 50% POE forecast.
|  | Summer | [11 empty] | Winter
Station | Feeder | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Arthurs Lake | 49101 | 44.2339 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 46.8205 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485 | 4.485
Avoca | 56001 | 10.6678 | 10.6358 | 10.6039 | 10.5721 | 10.5403 | 10.5087 | 10.4772 | 10.4458 | 10.4144 | 10.3832 | 10.352 | 10.321 | 0 | 6.2158 | 6.2052 | 6.1947 | 6.1841 | 6.1736 | 6.1631 | 6.1526 | 6.1422 | 6.1317 | 6.1213 | 6.1109
Avoca | 56002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoca | 56003 | 37.4511 | 38.5031 | 38.3875 | 38.2724 | 38.1576 | 38.0431 | 37.929 | 37.8152 | 37.7017 | 37.5886 | 37.4759 | 37.3634 | 40.7844 | 42.5149 | 42.4426 | 42.3705 | 42.2984 | 42.2265 | 42.1547 | 42.0831 | 42.0115 | 41.9401 | 41.8688 | 41.7976
Avoca | 56004 | 166.9078 | 166.4071 | 165.9078 | 165.4101 | 164.9139 | 164.4191 | 163.9259 | 163.4341 | 162.9438 | 162.455 | 161.9676 | 161.4817 | 128.2833 | 129.2984 | 129.0786 | 128.8592 | 128.6401 | 128.4214 | 128.2031 | 127.9851 | 127.7676 | 127.5504 | 127.3335 | 127.1171
Bellerive | 27171 | 117.8722 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 119.8345 | 165.8611 | 174.9814 | 173.2044 | 171.4402 | 169.6887 | 167.9498 | 166.2234 | 164.5095 | 162.8079 | 161.1186 | 159.4414 | 157.7763
Bellerive | 27172 | 0 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 135.0743 | 0 | 33.3996 | 31.727 | 30.0666 | 28.418 | 26.7814 | 25.1565 | 23.5433 | 21.9418 | 20.3517 | 18.7732 | 17.2059
Bellerive | 27173 | 25.5333 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 25.6681 | 32.5611 | 35.3988 | 35.1439 | 34.8909 | 34.6397 | 34.3903 | 34.1427 | 33.8968 | 33.6528 | 33.4105 | 33.1699 | 32.9311
Bellerive | 27174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bellerive | 27175 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 61.4833 | 135.6722 | 134.5685 | 132.9234 | 131.2901 | 129.6686 | 128.0587 | 126.4604 | 124.8737 | 123.2983 | 121.7343 | 120.1816 | 118.6401
Bellerive | 27176 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 156.0778 | 228.5111 | 242.3728 | 240.4686 | 238.5781 | 236.7013 | 234.8379 | 232.9879 | 231.1513 | 229.3279 | 227.5176 | 225.7204 | 223.9361
Bellerive | 27178 | 129.0556 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 130.2301 | 115.7778 | 123.7404 | 122.8495 | 121.9649 | 121.0868 | 120.215 | 119.3494 | 118.4901 | 117.637 | 116.79 | 115.9491 | 115.1143
Bridgewater | 48180 | 123.7783 | 122.6515 | 121.3023 | 119.968 | 118.6483 | 117.3432 | 116.0524 | 114.7758 | 113.5133 | 112.2646 | 111.0297 | 109.8084 | 189.1799 | 197.7341 | 196.0533 | 194.3869 | 192.7346 | 191.0963 | 189.472 | 187.8615 | 186.2647 | 184.6814 | 183.1116 | 181.5552
Bridgewater | 48181 | 39.8238 | 39.3857 | 38.9525 | 38.524 | 38.1002 | 37.6811 | 37.2666 | 36.8567 | 36.4513 | 36.0503 | 35.6538 | 35.2616 | 39.4494 | 39.8268 | 39.4883 | 39.1527 | 38.8199 | 38.4899 | 38.1627 | 37.8383 | 37.5167 | 37.1978 | 36.8817 | 36.5682
Bridgewater | 48182 | 156.1569 | 190.393 | 188.6633 | 186.9526 | 185.2608 | 183.5876 | 181.9327 | 180.2961 | 178.6775 | 177.0767 | 175.4935 | 173.9277 | 252.8439 | 290.8177 | 288.6275 | 286.456 | 284.3029 | 282.1681 | 280.0514 | 277.9527 | 275.8719 | 273.8088 | 271.7632 | 269.7349
Bridgewater | 48183 | 111.9497 | 110.7183 | 109.5004 | 108.2958 | 107.1046 | 105.9264 | 104.7613 | 103.6089 | 102.4692 | 101.342 | 100.2273 | 99.1248 | 144.5489 | 148.1925 | 146.9329 | 145.684 | 144.4456 | 143.2179 | 142.0005 | 140.7935 | 139.5968 | 138.4102 | 137.2337 | 136.0672
Bridgewater | 48184 | 154.7595 | 153.0571 | 151.3735 | 149.7084 | 148.0616 | 146.4329 | 144.8222 | 143.2291 | 141.6536 | 140.0954 | 138.5544 | 137.0303 | 209.7242 | 221.1864 | 219.3063 | 217.4422 | 215.594 | 213.7614 | 211.9444 | 210.1429 | 208.3567 | 206.5857 | 204.8297 | 203.0886
Bridgewater | 48185 | 123.0211 | 122.1909 | 120.8468 | 119.5174 | 118.2027 | 116.9025 | 115.6166 | 114.3448 | 113.087 | 111.8431 | 110.6128 | 109.396 | 160.9969 | 169.2138 | 167.7755 | 166.3494 | 164.9355 | 163.5335 | 162.1435 | 160.7653 | 159.3988 | 158.0439 | 156.7005 | 155.3685
Bridgewater | 48186 | 197.1923 | 195.0232 | 192.878 | 190.7563 | 188.658 | 186.5828 | 184.5303 | 182.5005 | 180.493 | 178.5076 | 176.544 | 174.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bridgewater | 48188 | 178.0333 | 176.075 | 174.1381 | 172.2226 | 170.3282 | 168.4546 | 166.6016 | 164.7689 | 162.9565 | 161.164 | 159.3912 | 157.6379 | 240.7811 | 246.3711 | 244.277 | 242.2006 | 240.1419 | 238.1007 | 236.0769 | 234.0702 | 232.0806 | 230.1079 | 228.152 | 226.2127
Bridgewater | 48189 | 67.1143 | 66.3761 | 65.6459 | 64.9238 | 64.2097 | 63.5034 | 62.8048 | 62.114 | 61.4307 | 60.755 | 60.0867 | 59.4257 | 101.0911 | 103.5409 | 102.6608 | 101.7882 | 100.923 | 100.0651 | 99.2146 | 98.3713 | 97.5351 | 96.7061 | 95.8841 | 95.069
Bridgewater | 48190 | 130.4561 | 129.1426 | 127.8436 | 126.5588 | 125.2882 | 124.0316 | 122.7888 | 121.5597 | 120.3441 | 119.1418 | 117.9528 | 116.7769 | 119.7324 | 118.8086 | 117.8927 | 116.9845 | 116.0841 | 115.1913 | 114.3061 | 113.4284 | 112.5582 | 111.6954 | 110.8399 | 109.9917
Bridgewater | 48191 | 41.1431 | 40.6905 | 40.2429 | 39.8003 | 39.3625 | 38.9295 | 38.5013 | 38.0777 | 37.6589 | 37.2446 | 36.8349 | 36.4298 | 55.2248 | 56.2066 | 55.7288 | 55.2552 | 54.7855 | 54.3198 | 53.8581 | 53.4003 | 52.9464 | 52.4963 | 52.0501 | 51.6077
Bridgewater | 48192 | 140.5055 | 139.3786 | 137.8454 | 136.3291 | 134.8295 | 133.3464 | 131.8795 | 130.4289 | 128.9942 | 127.5752 | 126.1719 | 124.784 | 296.4674 | 311.0219 | 308.3782 | 305.757 | 303.158 | 300.5812 | 298.0263 | 295.493 | 292.9813 | 290.491 | 288.0218 | 285.5736
Burnie | 91001 | 119.8944 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 144.7564 | 143.0611 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207 | 171.1207
Burnie | 91002 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 87.9333 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833 | 40.9833
Burnie | 91003 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 148.95 | 162.0333 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665 | 166.7665
Burnie | 91004 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 188.1222 | 184.4667 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152 | 208.1152
Burnie | 91005 | 103.8278 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 104.1691 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556 | 94.1556
Burnie | 91006 | 173.9444 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 179.7451 | 257.0111 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123 | 289.0123
Burnie | 91007 | 57.8333 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 57.9965 | 92.6111 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508 | 97.3508
Burnie | 91008 | 145.6944 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 146.0658 | 255.3722 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024 | 266.1024
Burnie | 91009 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 199.0444 | 148.35 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702 | 156.1702
Burnie | 91010 | 73.1444 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 74.524 | 158.4389 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067 | 166.4067
Burnie | 91011 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 104.2333 | 86.9444 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021 | 91.6021
Burnie | 91012 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 99.0556 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833 | 60.3833
Cambridge | 29481 | 45.9711 | 46.8123 | 46.9106 | 47.0091 | 47.1078 | 47.2068 | 47.3059 | 47.4052 | 47.5048 | 47.6046 | 47.7045 | 47.8047 | 65.6911 | 70.0911 | 70.5046 | 70.9206 | 71.3391 | 71.76 | 72.1833 | 72.6092 | 73.0376 | 73.4685 | 73.902 | 74.338
Cambridge | 29482 | 36.985 | 37.0627 | 37.1405 | 37.2185 | 37.2966 | 37.375 | 37.4535 | 37.5321 | 37.6109 | 37.6899 | 37.7691 | 37.8484 | 38.1072 | 40.656 | 40.8959 | 41.1371 | 41.3798 | 41.624 | 41.8696 | 42.1166 | 42.3651 | 42.615 | 42.8665 | 43.1194
Cambridge | 29483 | 97.2167 | 99.1607 | 99.3689 | 99.5776 | 99.7867 | 99.9962 | 100.2062 | 100.4166 | 100.6275 | 100.8388 | 101.0506 | 101.2628 | 135.3711 | 148.8587 | 149.7369 | 150.6204 | 151.5091 | 152.403 | 153.3021 | 154.2066 | 155.1164 | 156.0316 | 156.9522 | 157.8782
Cambridge | 29485 | 83.2417 | 83.4165 | 83.5917 | 83.7672 | 83.9431 | 84.1194 | 84.296 | 84.4731 | 84.6505 | 84.8282 | 85.0064 | 85.1849 | 87.9511 | 93.5496 | 94.1016 | 94.6568 | 95.2152 | 95.777 | 96.3421 | 96.9105 | 97.4823 | 98.0574 | 98.636 | 99.2179
Cambridge | 29486 | 28.4567 | 29.0872 | 29.1483 | 29.2095 | 29.2708 | 29.3323 | 29.3939 | 29.4556 | 29.5175 | 29.5795 | 29.6416 | 29.7038 | 30.3967 | 32.3829 | 32.5739 | 32.7661 | 32.9594 | 33.1539 | 33.3495 | 33.5463 | 33.7442 | 33.9433 | 34.1435 | 34.345
Cambridge | 29488 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 177.3622 | 201.2839 | 207.4291 | 205.9356 | 204.4529 | 202.9808 | 201.5193 | 200.0684 | 198.6279 | 197.1978 | 195.778 | 194.3684 | 192.9689
Cambridge | 29489 | 88.7856 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 88.8546 | 105.8861 | 108.7293 | 107.9465 | 107.1692 | 106.3976 | 105.6316 | 104.871 | 104.1159 | 103.3663 | 102.6221 | 101.8832 | 101.1496
Cambridge | 29490 | 49.5506 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 50.3726 | 67.3522 | 72.382 | 71.8608 | 71.3434 | 70.8298 | 70.3198 | 69.8135 | 69.3108 | 68.8118 | 68.3163 | 67.8245 | 67.3361
Cambridge | 29491 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 65.5545 | 73.1945 | 77.1628 | 76.6072 | 76.0557 | 75.5081 | 74.9644 | 74.4247 | 73.8888 | 73.3568 | 72.8286 | 72.3043 | 71.7837
Cambridge | 29492 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7733 | 1.7117 | 1.7317 | 1.7193 | 1.7069 | 1.6946 | 1.6824 | 1.6703 | 1.6582 | 1.6463 | 1.6345 | 1.6227 | 1.611
Chapel Street | 20534 | 34.5705 | 35.04 | 35.2958 | 35.5534 | 35.813 | 36.0744 | 36.3378 | 36.603 | 36.8702 | 37.1394 | 37.4105 | 37.6836 | 175.8617 | 176.952 | 178.0491 | 179.1531 | 180.2638 | 181.3814 | 182.506 | 183.6375 | 184.7761 | 185.9217 | 187.0744 | 188.2343
Chapel Street | 20535 | 158.6737 | 162.0311 | 163.2139 | 164.4054 | 165.6055 | 166.8144 | 168.0322 | 169.2588 | 170.4944 | 171.739 | 172.9927 | 174.2556 | 247.6803 | 264.901 | 266.5434 | 268.196 | 269.8588 | 271.5319 | 273.2154 | 274.9093 | 276.6138 | 278.3288 | 280.0544 | 281.7908
Chapel Street | 20536 | 83.1462 | 84.3578 | 84.9736 | 85.5939 | 86.2187 | 86.8481 | 87.4821 | 88.1208 | 88.764 | 89.412 | 90.0647 | 90.7222 | 132.4771 | 143.209 | 144.0969 | 144.9903 | 145.8892 | 146.7937 | 147.7038 | 148.6196 | 149.541 | 150.4682 | 151.4011 | 152.3398
Chapel Street | 20537 | 77.6014 | 78.9559 | 79.5323 | 80.1129 | 80.6977 | 81.2868 | 81.8802 | 82.4779 | 83.08 | 83.6865 | 84.2974 | 84.9128 | 120.9772 | 129.9109 | 130.7163 | 131.5268 | 132.3422 | 133.1628 | 133.9884 | 134.8191 | 135.655 | 136.496 | 137.3423 | 138.1938
Chapel Street | 20538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapel Street | 20539 | 18.9885 | 19.1271 | 19.2667 | 19.4074 | 19.549 | 19.6917 | 19.8355 | 19.9803 | 20.1261 | 20.2731 | 20.4211 | 20.5701 | 34.1539 | 35.541 | 35.7613 | 35.983 | 36.2062 | 36.4306 | 36.6565 | 36.8838 | 37.1124 | 37.3425 | 37.5741 | 37.807
Chapel Street | 20540 | 120.9968 | 121.88 | 122.7698 | 123.666 | 124.5687 | 125.4781 | 126.3941 | 127.3168 | 128.2462 | 129.1824 | 130.1254 | 131.0753 | 128.5838 | 134.8553 | 135.6914 | 136.5327 | 137.3792 | 138.231 | 139.088 | 139.9503 | 140.818 | 141.6911 | 142.5696 | 143.4535
Chapel Street | 20541 | 134.8427 | 135.827 | 136.8186 | 137.8173 | 138.8234 | 139.8368 | 140.8576 | 141.8859 | 142.9216 | 143.965 | 145.0159 | 146.0745 | 221.64 | 235.9276 | 237.3903 | 238.8622 | 240.3431 | 241.8332 | 243.3326 | 244.8413 | 246.3593 | 247.8867 | 249.4236 | 250.97
Chapel Street | 20544 | 82.2478 | 83.1676 | 83.7747 | 84.3863 | 85.0023 | 85.6228 | 86.2478 | 86.8774 | 87.5117 | 88.1505 | 88.794 | 89.4422 | 133.8097 | 141.8258 | 142.7052 | 143.5899 | 144.4802 | 145.376 | 146.2773 | 147.1842 | 148.0968 | 149.015 | 149.9389 | 150.8685
Chapel Street | 20545 | 30.9029 | 31.4171 | 31.6464 | 31.8774 | 32.1101 | 32.3446 | 32.5807 | 32.8185 | 33.0581 | 33.2994 | 33.5425 | 33.7874 | 44.9832 | 49.8437 | 50.1527 | 50.4637 | 50.7765 | 51.0913 | 51.4081 | 51.7268 | 52.0476 | 52.3702 | 52.6949 | 53.0217
Chapel Street | 20547 | 79.8931 | 81.5293 | 82.1245 | 82.724 | 83.3279 | 83.9362 | 84.5489 | 85.1661 | 85.7878 | 86.4141 | 87.0449 | 87.6803 | 119.7446 | 128.3912 | 129.1873 | 129.9882 | 130.7941 | 131.6051 | 132.421 | 133.242 | 134.0681 | 134.8994 | 135.7357 | 136.5773
Chapel Street | 20548 | 181.3914 | 186.4272 | 187.7881 | 189.1589 | 190.5398 | 191.9307 | 193.3318 | 194.7432 | 196.1648 | 197.5968 | 199.0392 | 200.4922 | 270.5043 | 291.8724 | 293.682 | 295.5028 | 297.3349 | 299.1784 | 301.0333 | 302.8997 | 304.7777 | 306.6673 | 308.5687 | 310.4818
Chapel Street | 20549 | 99.3902 | 100.7494 | 101.4848 | 102.2257 | 102.9719 | 103.7236 | 104.4808 | 105.2435 | 106.0118 | 106.7857 | 107.5652 | 108.3504 | 150.9695 | 162.9119 | 163.922 | 164.9383 | 165.9609 | 166.9899 | 168.0252 | 169.067 | 170.1152 | 171.1699 | 172.2312 | 173.299
Chapel Street | 20551 | 56.8607 | 57.2758 | 57.6939 | 58.1151 | 58.5393 | 58.9667 | 59.3971 | 59.8307 | 60.2675 | 60.7074 | 61.1506 | 61.597 | 50.6409 | 50.9549 | 51.2708 | 51.5887 | 51.9085 | 52.2304 | 52.5542 | 52.88 | 53.2079 | 53.5378 | 53.8697 | 54.2037
Chapel Street | 20552 | 105.5731 | 107.5813 | 108.3666 | 109.1577 | 109.9546 | 110.7572 | 111.5657 | 112.3802 | 113.2006 | 114.0269 | 114.8593 | 115.6978 | 157.6971 | 170.6117 | 171.6695 | 172.7338 | 173.8048 | 174.8823 | 175.9666 | 177.0576 | 178.1554 | 179.2599 | 180.3713 | 181.4896
Chapel Street | 20553 | 102.2419 | 104.7646 | 105.5294 | 106.2998 | 107.0758 | 107.8574 | 108.6448 | 109.4379 | 110.2368 | 111.0415 | 111.8521 | 112.6686 | 139.2048 | 148.5024 | 149.4231 | 150.3496 | 151.2817 | 152.2197 | 153.1634 | 154.113 | 155.0685 | 156.03 | 156.9974 | 157.9707
Chapel Street | 20554 | 97.4869 | 98.1986 | 98.9154 | 99.6375 | 100.3649 | 101.0975 | 101.8356 | 102.579 | 103.3278 | 104.0821 | 104.8419 | 105.6072 | 135.841 | 146.4691 | 147.3772 | 148.291 | 149.2104 | 150.1355 | 151.0663 | 152.0029 | 152.9453 | 153.8936 | 154.8477 | 155.8078
Claremont | 21081 | 104.7111 | 105.6326 | 106.5621 | 107.4999 | 108.4459 | 109.4002 | 110.3629 | 111.3341 | 112.3139 | 113.3022 | 114.2993 | 115.3051 | 157.5889 | 164.5 | 165.4212 | 166.3475 | 167.2791 | 168.2158 | 169.1578 | 170.1051 | 171.0577 | 172.0156 | 172.9789 | 173.9476
Claremont | 21082 | 27.3167 | 27.5571 | 27.7996 | 28.0442 | 28.291 | 28.5399 | 28.7911 | 29.0445 | 29.3 | 29.5579 | 29.818 | 30.0804 | 39.35 | 43.8959 | 44.1417 | 44.3889 | 44.6375 | 44.8874 | 45.1388 | 45.3916 | 45.6458 | 45.9014 | 46.1584 | 46.4169
Claremont | 21083 | 138.6611 | 141.9761 | 143.2255 | 144.4859 | 145.7574 | 147.04 | 148.334 | 149.6393 | 150.9561 | 152.2846 | 153.6247 | 154.9766 | 151.9778 | 156.4324 | 157.3084 | 158.1893 | 159.0752 | 159.966 | 160.8618 | 161.7627 | 162.6685 | 163.5795 | 164.4955 | 165.4167
Claremont | 21084 | 121.95 | 125.2208 | 126.3228 | 127.4344 | 128.5559 | 129.6871 | 130.8284 | 131.9797 | 133.1411 | 134.3127 | 135.4947 | 136.687 | 127.7278 | 129.6681 | 130.3942 | 131.1244 | 131.8587 | 132.5971 | 133.3396 | 134.0863 | 134.8372 | 135.5923 | 136.3516 | 137.1152
Claremont | 21085 | 101.6556 | 102.9185 | 103.8242 | 104.7378 | 105.6595 | 106.5893 | 107.5273 | 108.4735 | 109.4281 | 110.3911 | 111.3625 | 112.3425 | 149.4556 | 161.2176 | 162.1204 | 163.0282 | 163.9412 | 164.8593 | 165.7825 | 166.7109 | 167.6445 | 168.5833 | 169.5273 | 170.4767
Claremont | 21086 | 72.5389 | 74.1711 | 74.8238 | 75.4823 | 76.1465 | 76.8166 | 77.4926 | 78.1745 | 78.8625 | 79.5565 | 80.2566 | 80.9628 | 133.3611 | 142.5244 | 143.3226 | 144.1252 | 144.9323 | 145.7439 | 146.5601 | 147.3808 | 148.2061 | 149.0361 | 149.8707 | 150.71
Claremont | 21087 | 57.5389 | 58.2801 | 58.793 | 59.3104 | 59.8323 | 60.3588 | 60.89 | 61.4258 | 61.9663 | 62.5117 | 63.0618 | 63.6167 | 89.1722 | 96.4092 | 96.9491 | 97.492 | 98.038 | 98.587 | 99.1391 | 99.6943 | 100.2526 | 100.814 | 101.3785 | 101.9463
Claremont | 21088 | 32.9167 | 33.3763 | 33.67 | 33.9663 | 34.2652 | 34.5667 | 34.8709 | 35.1778 | 35.4874 | 35.7996 | 36.1147 | 36.4325 | 51.2833 | 51.8166 | 52.1068 | 52.3986 | 52.692 | 52.9871 | 53.2838 | 53.5822 | 53.8823 | 54.184 | 54.4874 | 54.7926
Claremont | 21089 | 84.8333 | 86.202 | 86.9605 | 87.7258 | 88.4978 | 89.2766 | 90.0622 | 90.8547 | 91.6543 | 92.4608 | 93.2745 | 94.0953 | 124.2444 | 133.68 | 134.4286 | 135.1814 | 135.9385 | 136.6997 | 137.4652 | 138.235 | 139.0092 | 139.7876 | 140.5704 | 141.3576
Derby | 55001 | 120.2056 | 119.7608 | 119.3177 | 118.8762 | 118.4364 | 117.9981 | 117.5616 | 117.1266 | 116.6932 | 116.2614 | 115.8313 | 115.4027 | 44.9278 | 46.3456 | 46.2576 | 46.1697 | 46.082 | 45.9944 | 45.907 | 45.8198 | 45.7328 | 45.6459 | 45.5591 | 45.4726
Derby | 55002 | 45 | 44.8335 | 44.6676 | 44.5023 | 44.3377 | 44.1736 | 44.0102 | 43.8474 | 43.6851 | 43.5235 | 43.3625 | 43.202 | 31.6667 | 31.6065 | 31.5465 | 31.4865 | 31.4267 | 31.367 | 31.3074 | 31.2479 | 31.1885 | 31.1293 | 31.0701 | 31.0111
Derby | 55003 | 45.05 | 44.8833 | 44.7172 | 44.5518 | 44.3869 | 44.2227 | 44.0591 | 43.8961 | 43.7337 | 43.5718 | 43.4106 | 43.25 | 16.6667 | 17.0431 | 17.0107 | 16.9784 | 16.9462 | 16.914 | 16.8818 | 16.8498 | 16.8177 | 16.7858 | 16.7539 | 16.722
Derwent Bridge | 49621 | 7.0534 | 7.2592 | 7.2374 | 7.2157 | 7.1941 | 7.1725 | 7.151 | 7.1295 | 7.1081 | 7.0868 | 7.0655 | 7.0443 | 8.9599 | 9.8077 | 9.8087 | 9.8097 | 9.8107 | 9.8117 | 9.8126 | 9.8136 | 9.8146 | 9.8156 | 9.8166 | 9.8175
Derwent Park | 17100 | 110.0222 | 112.4133 | 113.1552 | 113.9021 | 114.6538 | 115.4105 | 116.1722 | 116.939 | 117.7108 | 118.4877 | 119.2697 | 120.0569 | 133.5889 | 139.0548 | 139.8196 | 140.5886 | 141.3618 | 142.1393 | 142.9211 | 143.7071 | 144.4975 | 145.2922 | 146.0914 | 146.8949
Derwent Park | 17101 | 77.35 | 77.8605 | 78.3744 | 78.8917 | 79.4124 | 79.9365 | 80.4641 | 80.9951 | 81.5297 | 82.0678 | 82.6094 | 83.1546 | 118.75 | 119.4031 | 120.0598 | 120.7202 | 121.3841 | 122.0517 | 122.723 | 123.398 | 124.0767 | 124.7591 | 125.4453 | 126.1352
Derwent Park | 17102 | 10.5556 | 10.6286 | 10.6987 | 10.7693 | 10.8404 | 10.9119 | 10.984 | 11.0565 | 11.1294 | 11.2029 | 11.2768 | 11.3513 | 13.5889 | 13.9852 | 14.0621 | 14.1395 | 14.2172 | 14.2954 | 14.374 | 14.4531 | 14.5326 | 14.6125 | 14.6929 | 14.7737
Derwent Park | 17103 | 82.6556 | 83.2011 | 83.7502 | 84.303 | 84.8594 | 85.4194 | 85.9832 | 86.5507 | 87.1219 | 87.6969 | 88.2757 | 88.8584 | 162.8667 | 177.9111 | 178.8896 | 179.8735 | 180.8628 | 181.8575 | 182.8578 | 183.8635 | 184.8747 | 185.8915 | 186.9139 | 187.942
Derwent Park | 17104 | 71.25 | 72.8015 | 73.282 | 73.7657 | 74.2525 | 74.7426 | 75.2359 | 75.7324 | 76.2323 | 76.7354 | 77.2419 | 77.7517 | 97.8778 | 102.9096 | 103.4756 | 104.0448 | 104.617 | 105.1924 | 105.771 | 106.3527 | 106.9376 | 107.5258 | 108.1172 | 108.7118
Derwent Park | 17105 | 138.4389 | 139.3526 | 140.2723 | 141.1981 | 142.13 | 143.0681 | 144.0123 | 144.9628 | 145.9196 | 146.8826 | 147.8521 | 148.8279 | 201.5778 | 212.0984 | 213.2649 | 214.4378 | 215.6173 | 216.8032 | 217.9956 | 219.1945 | 220.4001 | 221.6123 | 222.8312 | 224.0568
Derwent Park | 17106 | 154.1111 | 158.8563 | 159.9048 | 160.9601 | 162.0225 | 163.0918 | 164.1682 | 165.2517 | 166.3424 | 167.4403 | 168.5454 | 169.6578 | 176.1722 | 181.3612 | 182.3586 | 183.3616 | 184.3701 | 185.3841 | 186.4038 | 187.429 | 188.4598 | 189.4964 | 190.5386 | 191.5866
Derwent Park | 17107 | 83.1778 | 83.7267 | 84.2793 | 84.8356 | 85.3955 | 85.9591 | 86.5264 | 87.0975 | 87.6724 | 88.251 | 88.8335 | 89.4198 | 223.2722 | 261.5918 | 263.0306 | 264.4773 | 265.9319 | 267.3945 | 268.8652 | 270.3439 | 271.8308 | 273.3259 | 274.8292 | 276.3407
Derwent Park | 17108 | 18.7611 | 18.8849 | 19.0096 | 19.135 | 19.2613 | 19.3884 | 19.5164 | 19.6452 | 19.7749 | 19.9054 | 20.0368 | 20.169 | 37.2111 | 40.4118 | 40.6341 | 40.8576 | 41.0823 | 41.3082 | 41.5354 | 41.7639 | 41.9936 | 42.2245 | 42.4568 | 42.6903
Derwent Park | 17109 | 42.2389 | 42.5507 | 42.8315 | 43.1142 | 43.3988 | 43.6852 | 43.9735 | 44.2637 | 44.5559 | 44.8499 | 45.146 | 45.4439 | 69.7778 | 72.4163 | 72.8146 | 73.2151 | 73.6178 | 74.0227 | 74.4298 | 74.8392 | 75.2508 | 75.6647 | 76.0808 | 76.4993
Devonport | 80001 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 118.7793 | 187.1508 | 183.9957 | 180.8711 | 177.7769 | 174.7127 | 171.6782 | 168.6731 | 165.6972 | 162.7501 | 159.8317 | 156.9415 | 154.0794
Devonport | 80002 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 177.5212 | 186.3503 | 184.5427 | 182.7526 | 180.9799 | 179.2244 | 177.486 | 175.7643 | 174.0594 | 172.3711 | 170.6991 | 169.0433 | 167.4036
Devonport | 80003 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 159.7576 | 152.2707 | 150.7937 | 149.331 | 147.8825 | 146.448 | 145.0275 | 143.6207 | 142.2276 | 140.848 | 139.4817 | 138.1288 | 136.7889
Devonport | 80004 | 100.4121 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 119.7492 | 155.5386 | 181.21 | 179.6398 | 178.0849 | 176.545 | 175.0201 | 173.51 | 172.0145 | 170.5336 | 169.067 | 167.6146 | 166.1763
Devonport | 80005 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 108.8997 | 130.9219 | 132.1586 | 130.8766 | 129.6071 | 128.35 | 127.105 | 125.872 | 124.6511 | 123.442 | 122.2446 | 121.0588 | 119.8845
Devonport | 80006 | 115.9131 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 135.2502 | 105.0197 | 123.3381 | 122.3293 | 121.3303 | 120.3409 | 119.3612 | 118.391 | 117.4301 | 116.4786 | 115.5364 | 114.6032 | 113.6791
Devonport | 80007 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 105.0462 | 159.2538 | 163.7727 | 161.6482 | 159.5442 | 157.4608 | 155.3975 | 153.3542 | 151.3308 | 149.3269 | 147.3425 | 145.3774 | 143.4313
Devonport | 80008 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 73.2548 | 135.8572 | 139.2681 | 137.9172 | 136.5794 | 135.2546 | 133.9426 | 132.6434 | 131.3567 | 130.0826 | 128.8208 | 127.5712 | 126.3338
Devonport | 80009 | 87.051 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 100.8632 | 203.1097 | 233.2761 | 231.2009 | 229.1458 | 227.1106 | 225.0952 | 223.0994 | 221.1229 | 219.1656 | 217.2272 | 215.3077 | 213.4068
Devonport | 80010 | 79.0258 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 80.1659 | 171.0225 | 174.2106 | 172.5208 | 170.8473 | 169.1901 | 167.549 | 165.9237 | 164.3143 | 162.7204 | 161.142 | 159.579 | 158.031
Devonport | 80011 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 101.6846 | 145.7001 | 148.3568 | 146.3819 | 144.4261 | 142.4892 | 140.5712 | 138.6717 | 136.7907 | 134.9279 | 133.0832 | 131.2563 | 129.4472
East Hobart | 14060 | 0 | 84.2062 | 84.7619 | 85.3214 | 85.8845 | 86.4513 | 87.0219 | 87.5962 | 88.1744 | 88.7563 | 89.3421 | 89.9318 | 107.4389 | 108.0298 | 108.624 | 109.2214 | 109.8221 | 110.4261 | 111.0335 | 111.6442 | 112.2582 | 112.8756 | 113.4964 | 114.1207
East Hobart | 14061 | 69.0889 | 70.391 | 71.1765 | 71.9671 | 72.763 | 73.5641 | 74.3705 | 75.1823 | 75.9994 | 76.8218 | 77.6497 | 78.4831 | 78.5889 | 79.6473 | 80.5716 | 81.5009 | 82.4354 | 83.3749 | 84.3197 | 85.2696 | 86.2248 | 87.1852 | 88.1509 | 89.122
East Hobart | 14062 | 89.1056 | 89.6937 | 90.2856 | 90.8815 | 91.4813 | 92.0851 | 92.6929 | 93.3046 | 93.9205 | 94.5403 | 95.1643 | 95.7924 | 119.9278 | 130.5068 | 131.2246 | 131.9463 | 132.6721 | 133.4017 | 134.1355 | 134.8732 | 135.615 | 136.3609 | 137.1109 | 137.865
East Hobart | 14063 | 90.8056 | 91.4049 | 92.0081 | 92.6154 | 93.2267 | 93.842 | 94.4613 | 95.0848 | 95.7123 | 96.344 | 96.9799 | 97.62 | 124.8222 | 133.9545 | 134.6913 | 135.4321 | 136.177 | 136.9259 | 137.679 | 138.4363 | 139.1977 | 139.9632 | 140.733 | 141.5071
East Hobart | 14064 | 96.6722 | 130.4596 | 131.1018 | 131.7483 | 132.399 | 133.0541 | 133.7135 | 134.3772 | 135.0453 | 135.7178 | 136.3948 | 137.0762 | 107.05 | 140.7881 | 141.3801 | 141.9754 | 142.5739 | 143.1757 | 143.7809 | 144.3894 | 145.0012 | 145.6164 | 146.2349 | 146.8569
East Hobart | 14065 | 166.6333 | 206.4073 | 207.5143 | 208.6287 | 209.7504 | 210.8795 | 212.016 | 213.1601 | 214.3117 | 215.4709 | 216.6378 | 217.8123 | 216.23 | 259.73 | 260.95 | 262.17 | 263.4 | 264.63 | 265.88 | 267.13 | 268.38 | 269.65 | 270.92 | 272.19
East Hobart | 14066 | 92.9833 | 93.597 | 94.2148 | 94.8366 | 95.4625 | 96.0926 | 96.7268 | 97.3652 | 98.0078 | 98.6546 | 99.3057 | 99.9612 | 105.6444 | 110.8646 | 111.4743 | 112.0874 | 112.7039 | 113.3238 | 113.9471 | 114.5738 | 115.2039 | 115.8375 | 116.4747 | 117.1153
East Hobart | 14067 | 84.9333 | 124.1681 | 124.7323 | 125.3003 | 125.8721 | 126.4476 | 127.0269 | 127.61 | 128.197 | 128.7878 | 129.3826 | 129.9812 | 108.9333 | 155.4928 | 156.1353 | 156.7813 | 157.4309 | 158.0841 | 158.7408 | 159.4012 | 160.0652 | 160.7328 | 161.4041 | 162.0792
East Hobart | 14068 | 135.9444 | 136.8417 | 137.7448 | 138.6539 | 139.5691 | 140.4902 | 141.4175 | 142.3508 | 143.2903 | 144.236 | 145.188 | 146.1462 | 189.7278 | 191.8697 | 192.925 | 193.986 | 195.053 | 196.1258 | 197.2045 | 198.2891 | 199.3797 | 200.4763 | 201.5789 | 202.6876
East Hobart | 14069 | 92.2222 | 125.9802 | 126.5929 | 127.2096 | 127.8304 | 128.4553 | 129.0843 | 129.7175 | 130.3548 | 130.9964 | 131.6422 | 132.2922 | 99.0055 | 132.6994 | 133.2469 | 133.7974 | 134.351 | 134.9076 | 135.4673 | 136.03 | 136.5959 | 137.1648 | 137.7369 | 138.3122
East Hobart | 14070 | 164.2556 | 165.3396 | 166.4309 | 167.5293 | 168.635 | 169.748 | 170.8683 | 171.9961 | 173.1313 | 174.2739 | 175.4241 | 176.5819 | 200.5944 | 211.3965 | 212.5592 | 213.7283 | 214.9038 | 216.0857 | 217.2742 | 218.4692 | 219.6708 | 220.879 | 222.0938 | 223.3153
East Hobart | 14071 | 0 | 138.1221 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 0 | 138.1221 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592 | 157.4592
Electrona | 33271 | 108.0522 | 109.1289 | 109.118 | 109.1071 | 109.0962 | 109.0853 | 109.0743 | 109.0634 | 109.0525 | 109.0416 | 109.0307 | 109.0198 | 125.7674 | 130.1518 | 129.9436 | 129.7356 | 129.5281 | 129.3208 | 129.1139 | 128.9073 | 128.7011 | 128.4952 | 128.2896 | 128.0843
Electrona | 33272 | 161.1994 | 164.4876 | 164.4711 | 164.4547 | 164.4382 | 164.4218 | 164.4053 | 164.3889 | 164.3725 | 164.356 | 164.3396 | 164.3231 | 220.5155 | 229.7763 | 229.4087 | 229.0416 | 228.6751 | 228.3093 | 227.944 | 227.5793 | 227.2151 | 226.8516 | 226.4886 | 226.1262
Electrona | 33273 | 19.0725 | 19.0707 | 19.0687 | 19.0668 | 19.0649 | 19.063 | 19.0611 | 19.0592 | 19.0573 | 19.0554 | 19.0535 | 19.0516 | 18.2566 | 18.9338 | 18.9035 | 18.8733 | 18.8431 | 18.8129 | 18.7828 | 18.7528 | 18.7228 | 18.6928 | 18.6629 | 18.6331
Electrona | 33274 | 129.1755 | 130.4148 | 130.4017 | 130.3887 | 130.3757 | 130.3626 | 130.3496 | 130.3365 | 130.3235 | 130.3105 | 130.2974 | 130.2844 | 234.2663 | 242.5327 | 242.1446 | 241.7572 | 241.3704 | 240.9842 | 240.5986 | 240.2136 | 239.8293 | 239.4456 | 239.0625 | 238.68
Electrona | 33275 | 3.3943 | 3.4017 | 3.4014 | 3.401 | 3.4007 | 3.4003 | 3.4 | 3.3997 | 3.3993 | 3.399 | 3.3986 | 3.3983 | 7.8789 | 8.5304 | 8.5168 | 8.5032 | 8.4896 | 8.476 | 8.4624 | 8.4489 | 8.4354 | 8.4219 | 8.4084 | 8.3949
Electrona | 33276 | 136.2054 | 138.5964 | 138.5826 | 138.5687 | 138.5549 | 138.541 | 138.5272 | 138.5133 | 138.4994 | 138.4856 | 138.4717 | 138.4579 | 198.0491 | 204.6572 | 204.3297 | 204.0028 | 203.6764 | 203.3505 | 203.0251 | 202.7003 | 202.376 | 202.0522 | 201.7289 | 201.4061
Electrona | 33277 | 0 | 12.6639 | 12.6626 | 12.6613 | 12.6601 | 12.6588 | 12.6576 | 12.6563 | 12.655 | 12.6538 | 12.6525 | 12.6512 | 6.5458 | 7.5125 | 7.5005 | 7.4885 | 7.4765 | 7.4645 | 7.4526 | 7.4407 | 7.4288 | 7.4169 | 7.405 | 7.3932
Emu Bay | 90019 | 67.17 | 66.8207 | 66.4732 | 66.1276 | 65.7837 | 65.4416 | 65.1013 | 64.7628 | 64.4261 | 64.091 | 63.7578 | 63.4262 | 53.0917 | 52.9749 | 52.8583 | 52.742 | 52.626 | 52.5102 | 52.3947 | 52.2794 | 52.1644 | 52.0496 | 51.9352 | 51.8209
Emu Bay | 90020 | 84.725 | 84.2844 | 83.8461 | 83.4102 | 82.9764 | 82.5449 | 82.1157 | 81.6887 | 81.2639 | 80.8414 | 80.421 | 80.0028 | 96.2183 | 102.0806 | 101.856 | 101.6319 | 101.4083 | 101.1852 | 100.9626 | 100.7405 | 100.5189 | 100.2977 | 100.0771 | 99.8569
Emu Bay | 90021 | 87.1 | 86.6471 | 86.1965 | 85.7483 | 85.3024 | 84.8588 | 84.4176 | 83.9786 | 83.5419 | 83.1075 | 82.6753 | 82.2454 | 100.9833 | 104.9793 | 104.7483 | 104.5179 | 104.2879 | 104.0585 | 103.8296 | 103.6011 | 103.3732 | 103.1458 | 102.9189 | 102.6924
Emu Bay | 90023 | 107.5933 | 107.0338 | 106.4773 | 105.9236 | 105.3728 | 104.8249 | 104.2798 | 103.7375 | 103.1981 | 102.6614 | 102.1276 | 101.5965 | 124.9313 | 128.7681 | 128.4848 | 128.2022 | 127.9201 | 127.6387 | 127.3579 | 127.0777 | 126.7981 | 126.5192 | 126.2408 | 125.9631
Emu Bay | 90024 | 102.25 | 101.7183 | 101.1894 | 100.6632 | 100.1397 | 99.619 | 99.101 | 98.5857 | 98.073 | 97.563 | 97.0557 | 96.551 | 131.4933 | 136.9936 | 136.6922 | 136.3915 | 136.0914 | 135.792 | 135.4933 | 135.1952 | 134.8978 | 134.601 | 134.3049 | 134.0094
Geilston Bay | 26161 | 82.9667 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 83.2982 | 111.0667 | 118.4616 | 117.6086 | 116.7619 | 115.9212 | 115.0865 | 114.2579 | 113.4353 | 112.6185 | 111.8077 | 111.0027 | 110.2034
Geilston Bay | 26162 | 104.6 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 105.4569 | 156.3444 | 165.4995 | 164.3079 | 163.1249 | 161.9504 | 160.7843 | 159.6267 | 158.4774 | 157.3363 | 156.2035 | 155.0788 | 153.9623
Geilston Bay | 26163 | 39.3778 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 39.6774 | 50.9611 | 54.1145 | 53.7249 | 53.338 | 52.954 | 52.5727 | 52.1942 | 51.8184 | 51.4453 | 51.0749 | 50.7072 | 50.3421
Geilston Bay | 26164 | 129.4611 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 130.9238 | 187.3333 | 195.9697 | 194.5587 | 193.1579 | 191.7671 | 190.3864 | 189.0156 | 187.6547 | 186.3036 | 184.9622 | 183.6305 | 182.3083
Geilston Bay | 26165 | 93.9444 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 96.9333 | 56.2556 | 55.8505 | 55.4484 | 55.0492 | 54.6528 | 54.2593 | 53.8686 | 53.4808 | 53.0957 | 52.7134 | 52.3339 | 51.9571
Geilston Bay | 26166 | 59.6611 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 60.7373 | 83.7444 | 87.7587 | 85.5755 | 83.4079 | 81.256 | 79.1196 | 76.9985 | 74.8928 | 72.8021 | 70.7266 | 68.6659 | 66.6202
Geilston Bay | 26167 | 131.8556 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 133.3517 | 181.7389 | 196.1934 | 194.7808 | 193.3784 | 191.9861 | 190.6038 | 189.2314 | 187.869 | 186.5163 | 185.1734 | 183.8402 | 182.5165
Geilston Bay | 26169 | 0 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 131.9817 | 0 | 39.4874 | 37.7711 | 36.0671 | 34.3753 | 32.6958 | 31.0283 | 29.3729 | 27.7293 | 26.0976 | 24.4777 | 22.8694
George Town | 53001 | 80.6486 | 80.9044 | 80.686 | 80.4681 | 80.2508 | 80.0342 | 79.8181 | 79.6026 | 79.3876 | 79.1733 | 78.9595 | 78.7463 | 105.5208 | 105.352 | 105.1834 | 105.0151 | 104.8471 | 104.6794 | 104.5119 | 104.3447 | 104.1777 | 104.011 | 103.8446 | 103.6785
George Town | 53002 | 41.8434 | 44.7252 | 44.6045 | 44.484 | 44.3639 | 44.2441 | 44.1247 | 44.0055 | 43.8867 | 43.7682 | 43.6501 | 43.5322 | 36.9596 | 36.9004 | 36.8414 | 36.7824 | 36.7236 | 36.6648 | 36.6062 | 36.5476 | 36.4891 | 36.4307 | 36.3724 | 36.3143
George Town | 53003 | 77.7053 | 77.6399 | 77.4303 | 77.2212 | 77.0127 | 76.8048 | 76.5974 | 76.3906 | 76.1844 | 75.9787 | 75.7735 | 75.5689 | 138.18 | 141.9223 | 141.6952 | 141.4685 | 141.2422 | 141.0162 | 140.7906 | 140.5653 | 140.3404 | 140.1158 | 139.8917 | 139.6678
George Town | 53004 | 35.3589 | 35.2634 | 35.1682 | 35.0733 | 34.9786 | 34.8841 | 34.7899 | 34.696 | 34.6023 | 34.5089 | 34.4157 | 34.3228 | 49.5622 | 50.0198 | 49.9398 | 49.8599 | 49.7801 | 49.7005 | 49.621 | 49.5416 | 49.4623 | 49.3832 | 49.3041 | 49.2253
George Town | 53006 | 6.172 | 6.2837 | 6.2668 | 6.2499 | 6.233 | 6.2161 | 6.1994 | 6.1826 | 6.1659 | 6.1493 | 6.1327 | 6.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
George Town | 53007 | 4.1156 | 4.1044 | 4.0934 | 4.0823 | 4.0713 | 4.0603 | 4.0493 | 4.0384 | 4.0275 | 4.0166 | 4.0058 | 3.995 | 0 | 2.2367 | 2.2331 | 2.2295 | 2.226 | 2.2224 | 2.2188 | 2.2153 | 2.2117 | 2.2082 | 2.2047 | 2.2011
George Town | 53008 | 48.0867 | 47.9568 | 47.8274 | 47.6982 | 47.5694 | 47.441 | 47.3129 | 47.1852 | 47.0578 | 46.9307 | 46.804 | 46.6776 | 59.8303 | 62.5637 | 62.4635 | 62.3636 | 62.2638 | 62.1642 | 62.0647 | 61.9654 | 61.8663 | 61.7673 | 61.6685 | 61.5698
George Town | 53009 | 74.53 | 75.598 | 75.3939 | 75.1903 | 74.9873 | 74.7849 | 74.5829 | 74.3816 | 74.1807 | 73.9805 | 73.7807 | 73.5815 | 84.3433 | 87.8598 | 87.7193 | 87.5789 | 87.4388 | 87.2989 | 87.1592 | 87.0198 | 86.8805 | 86.7415 | 86.6027 | 86.4642
George Town | 53010 | 81.5218 | 82.4552 | 82.2326 | 82.0105 | 81.7891 | 81.5683 | 81.348 | 81.1284 | 80.9094 | 80.6909 | 80.473 | 80.2558 | 72.7208 | 77.2359 | 77.1123 | 76.9889 | 76.8658 | 76.7428 | 76.62 | 76.4974 | 76.375 | 76.2528 | 76.1308 | 76.009
Gordon | 49801 | 7.3808 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 7.6446 | 10.6375 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047 | 11.1047
Gretna | 37001 | 25.8778 | 25.8362 | 25.7458 | 25.6557 | 25.5659 | 25.4764 | 25.3873 | 25.2984 | 25.2099 | 25.1216 | 25.0337 | 24.9461 | 13.8167 | 13.9311 | 13.9074 | 13.8837 | 13.8601 | 13.8366 | 13.813 | 13.7896 | 13.7661 | 13.7427 | 13.7194 | 13.696
Gretna | 37002 | 57.2111 | 57.0109 | 56.8113 | 56.6125 | 56.4143 | 56.2169 | 56.0201 | 55.8241 | 55.6287 | 55.434 | 55.24 | 55.0466 | 19.6056 | 20.6849 | 20.6497 | 20.6146 | 20.5795 | 20.5446 | 20.5096 | 20.4748 | 20.44 | 20.4052 | 20.3705 | 20.3359
Hadspen | 67081 | 65.1456 | 65.5276 | 65.6849 | 65.8426 | 66.0006 | 66.159 | 66.3178 | 66.4769 | 66.6365 | 66.7964 | 66.9567 | 67.1174 | 114.4619 | 117.0565 | 116.8107 | 116.5654 | 116.3206 | 116.0763 | 115.8325 | 115.5893 | 115.3466 | 115.1043 | 114.8626 | 114.6214
Hadspen | 67082 | 125.2992 | 125.5999 | 125.9013 | 126.2035 | 126.5064 | 126.81 | 127.1143 | 127.4194 | 127.7252 | 128.0318 | 128.339 | 128.647 | 105.0164 | 110.1727 | 109.9413 | 109.7104 | 109.48 | 109.2501 | 109.0207 | 108.7918 | 108.5633 | 108.3353 | 108.1078 | 107.8808
Hadspen | 67083 | 109.1111 | 109.373 | 109.6355 | 109.8986 | 110.1624 | 110.4267 | 110.6918 | 110.9574 | 111.2237 | 111.4907 | 111.7582 | 112.0265 | 112.1942 | 112.0594 | 111.8241 | 111.5893 | 111.3549 | 111.1211 | 110.8877 | 110.6549 | 110.4225 | 110.1906 | 109.9592 | 109.7283
Hadspen | 67084 | 128.0311 | 183.5872 | 183.8952 | 184.204 | 184.5135 | 184.8237 | 185.1347 | 185.4464 | 185.7589 | 186.0721 | 186.3861 | 186.7008 | 106.5822 | 163.4986 | 163.2712 | 163.0444 | 162.818 | 162.5921 | 162.3667 | 162.1418 | 161.9173 | 161.6933 | 161.4697 | 161.2467
Hadspen | 67085 | 74.9833 | 75.1633 | 75.3437 | 75.5245 | 75.7058 | 75.8875 | 76.0696 | 76.2522 | 76.4352 | 76.6186 | 76.8025 | 76.9868 | 111.3028 | 111.4506 | 111.2166 | 110.983 | 110.75 | 110.5174 | 110.2853 | 110.0537 | 109.8226 | 109.592 | 109.3618 | 109.1322
Hadspen | 67086 | 116.0619 | 116.7924 | 117.0727 | 117.3537 | 117.6353 | 117.9176 | 118.2006 | 118.4843 | 118.7687 | 119.0537 | 119.3395 | 119.6259 | 161.945 | 169.4073 | 169.0516 | 168.6966 | 168.3423 | 167.9888 | 167.636 | 167.284 | 166.9327 | 166.5821 | 166.2323 | 165.8832
Hadspen | 67087 | 160.1019 | 160.4862 | 160.8714 | 161.2574 | 161.6445 | 162.0324 | 162.4213 | 162.8111 | 163.2018 | 163.5935 | 163.9862 | 164.3797 | 173.7028 | 176.6576 | 176.2866 | 175.9164 | 175.547 | 175.1783 | 174.8105 | 174.4434 | 174.077 | 173.7115 | 173.3467 | 172.9827
Hadspen | 67088 | 48.5444 | 48.6609 | 48.7777 | 48.8948 | 49.0121 | 49.1298 | 49.2477 | 49.3659 | 49.4844 | 49.6031 | 49.7222 | 49.8415 | 74.9606 | 76.1229 | 75.963 | 75.8035 | 75.6443 | 75.4855 | 75.3269 | 75.1688 | 75.0109 | 74.8534 | 74.6962 | 74.5393
Hadspen | 67089 | 57.0567 | 57.2645 | 57.4019 | 57.5397 | 57.6778 | 57.8162 | 57.955 | 58.0941 | 58.2335 | 58.3732 | 58.5133 | 58.6538 | 94.2503 | 98.6559 | 98.4487 | 98.242 | 98.0357 | 97.8298 | 97.6244 | 97.4193 | 97.2148 | 97.0106 | 96.8069 | 96.6036
Hadspen | 67090 | 148.7928 | 150.9273 | 151.2895 | 151.6526 | 152.0166 | 152.3814 | 152.7471 | 153.1137 | 153.4812 | 153.8495 | 154.2188 | 154.5889 | 220.2361 | 233.5334 | 233.043 | 232.5536 | 232.0653 | 231.5779 | 231.0916 | 230.6063 | 230.1221 | 229.6388 | 229.1566 | 228.6753
Hadspen | 67091 | 69.8467 | 70.641 | 70.8106 | 70.9805 | 71.1509 | 71.3216 | 71.4928 | 71.6644 | 71.8364 | 72.0088 | 72.1816 | 72.3548 | 124.3511 | 124.8082 | 124.5461 | 124.2845 | 124.0235 | 123.7631 | 123.5032 | 123.2438 | 122.985 | 122.7267 | 122.469 | 122.2118
Howrah | 22323 | 70.605 | 71.4915 | 71.6416 | 71.792 | 71.9428 | 72.0939 | 72.2453 | 72.397 | 72.549 | 72.7014 | 72.8541 | 73.007 | 94.9822 | 97.019 | 97.5914 | 98.1672 | 98.7464 | 99.329 | 99.915 | 100.5045 | 101.0975 | 101.694 | 102.294 | 102.8975
Howrah | 22324 | 48.3794 | 48.5406 | 48.6425 | 48.7446 | 48.847 | 48.9496 | 49.0524 | 49.1554 | 49.2586 | 49.3621 | 49.4657 | 49.5696 | 81.3567 | 87.0832 | 87.597 | 88.1138 | 88.6337 | 89.1566 | 89.6827 | 90.2118 | 90.744 | 91.2794 | 91.818 | 92.3597
Howrah | 22325 | 106.5156 | 107.9419 | 108.1686 | 108.3958 | 108.6234 | 108.8515 | 109.0801 | 109.3092 | 109.5387 | 109.7687 | 109.9993 | 110.2303 | 144.7272 | 156.3265 | 157.2488 | 158.1766 | 159.1098 | 160.0486 | 160.9928 | 161.9427 | 162.8982 | 163.8593 | 164.826 | 165.7985
Howrah | 22326 | 35.9222 | 36.5141 | 36.5907 | 36.6676 | 36.7446 | 36.8218 | 36.8991 | 36.9766 | 37.0542 | 37.132 | 37.21 | 37.2882 | 46.2639 | 50.4756 | 50.7734 | 51.073 | 51.3743 | 51.6774 | 51.9823 | 52.289 | 52.5975 | 52.9079 | 53.22 | 53.534
Howrah | 22328 | 93.7383 | 94.9705 | 95.17 | 95.3698 | 95.5701 | 95.7708 | 95.9719 | 96.1734 | 96.3754 | 96.5778 | 96.7806 | 96.9839 | 146.3233 | 156.7068 | 157.6314 | 158.5614 | 159.4969 | 160.438 | 161.3846 | 162.3367 | 163.2945 | 164.2579 | 165.2271 | 166.2019
Howrah | 22329 | 129.5056 | 131.4296 | 131.7056 | 131.9821 | 132.2593 | 132.5371 | 132.8154 | 133.0943 | 133.3738 | 133.6539 | 133.9345 | 134.2158 | 172.2722 | 190.4205 | 191.544 | 192.6741 | 193.8109 | 194.9544 | 196.1046 | 197.2616 | 198.4254 | 199.5962 | 200.7738 | 201.9583
Howrah | 22330 | 9.1067 | 9.2551 | 9.2746 | 9.294 | 9.3136 | 9.3331 | 9.3527 | 9.3724 | 9.392 | 9.4118 | 9.4315 | 9.4513 | 11.5194 | 12.0802 | 12.1515 | 12.2232 | 12.2953 | 12.3678 | 12.4408 | 12.5142 | 12.588 | 12.6623 | 12.737 | 12.8122
Howrah | 22331 | 121.2328 | 122.6053 | 122.8628 | 123.1208 | 123.3793 | 123.6384 | 123.8981 | 124.1583 | 124.419 | 124.6803 | 124.9421 | 125.2045 | 173.6261 | 188.0848 | 189.1945 | 190.3108 | 191.4336 | 192.5631 | 193.6992 | 194.842 | 195.9916 | 197.1479 | 198.3111 | 199.4811
Huon River | 38422 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.608 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832 | 0.832
Huon River | 38423 | 82.432 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 89.5779 | 88.528 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137 | 88.7137
Kermandie | 31002 | 26.3619 | 26.8164 | 26.744 | 26.6718 | 26.5998 | 26.528 | 26.4563 | 26.3849 | 26.3137 | 26.2426 | 26.1717 | 26.1011 | 36.2629 | 37.3472 | 37.2837 | 37.2203 | 37.157 | 37.0938 | 37.0308 | 36.9678 | 36.905 | 36.8422 | 36.7796 | 36.7171
Kermandie | 31007 | 82.3069 | 83.1575 | 82.933 | 82.7091 | 82.4858 | 82.2631 | 82.0409 | 81.8194 | 81.5985 | 81.3782 | 81.1585 | 80.9394 | 114.6008 | 117.9266 | 117.7262 | 117.526 | 117.3262 | 117.1268 | 116.9277 | 116.7289 | 116.5304 | 116.3323 | 116.1346 | 115.9371
Kermandie | 31008 | 114.7844 | 153.1487 | 152.8396 | 152.5314 | 152.2239 | 151.9174 | 151.6116 | 151.3067 | 151.0026 | 150.6993 | 150.3968 | 150.0952 | 144.9199 | 186.7611 | 186.5093 | 186.258 | 186.0071 | 185.7567 | 185.5066 | 185.257 | 185.0078 | 184.759 | 184.5107 | 184.2628
Kermandie | 31010 | 47.9797 | 114.4823 | 114.3522 | 114.2225 | 114.0931 | 113.964 | 113.8353 | 113.707 | 113.579 | 113.4513 | 113.324 | 113.197 | 72.0177 | 139.2012 | 139.0773 | 138.9536 | 138.8301 | 138.7068 | 138.5837 | 138.4608 | 138.3381 | 138.2156 | 138.0934 | 137.9713
Kingston | 34251 | 126.9113 | 167.2113 | 166.1188 | 165.0355 | 163.9614 | 162.8965 | 161.8406 | 160.7937 | 159.7557 | 158.7265 | 157.706 | 156.6943 | 116.6557 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904 | 164.8904
Kingston | 34252 | 168.4601 | 170.26 | 168.8127 | 167.3778 | 165.9551 | 164.5445 | 163.1459 | 161.7591 | 160.3842 | 159.0209 | 157.6692 | 156.3291 | 248.0597 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856 | 265.7856
Kingston | 34253 | 83.4488 | 84.2759 | 83.5596 | 82.8493 | 82.1451 | 81.4469 | 80.7546 | 80.0681 | 79.3876 | 78.7128 | 78.0437 | 77.3803 | 120.5129 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209 | 129.9209
Kingston | 34254 | 9.0844 | 9.0104 | 8.9339 | 8.8579 | 8.7826 | 8.708 | 8.634 | 8.5606 | 8.4878 | 8.4157 | 8.3441 | 8.2732 | 13.4972 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339 | 13.9339
Kingston | 34255 | 2.052 | 2.0346 | 2.0173 | 2.0001 | 1.9831 | 1.9663 | 1.9495 | 1.933 | 1.9165 | 1.9003 | 1.8841 | 1.8681 | 0 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699 | 119.7699
Kingston | 34256 | 97.4577 | 98.8239 | 97.9839 | 97.151 | 96.3252 | 95.5065 | 94.6947 | 93.8898 | 93.0917 | 92.3004 | 91.5159 | 90.738 | 140.1546 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877 | 147.0877
Kingston | 34257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston | 34258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kingston | 34259 | 170.7877 | 172.5588 | 171.0921 | 169.6378 | 168.1959 | 166.7662 | 165.3487 | 163.9432 | 162.5497 | 161.168 | 159.7981 | 158.4398 | 239.7722 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683 | 258.6683
Kingston | 34260 | 38.5963 | 38.8145 | 38.4845 | 38.1574 | 37.8331 | 37.5115 | 37.1927 | 36.8765 | 36.5631 | 36.2523 | 35.9441 | 35.6386 | 69.158 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913 | 70.913
Kingston | 34261 | 27.1571 | 26.9263 | 26.6974 | 26.4705 | 26.2455 | 26.0224 | 25.8012 | 25.5819 | 25.3644 | 25.1488 | 24.9351 | 24.7231 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637 | 26.4637
Kingston | 34262 | 82.0731 | 82.3767 | 81.6765 | 80.9823 | 80.2939 | 79.6114 | 78.9347 | 78.2638 | 77.5985 | 76.939 | 76.285 | 75.6365 | 139.4909 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242 | 140.2242
Kingston | 34263 | 83.5161 | 84.3451 | 83.6282 | 82.9173 | 82.2125 | 81.5137 | 80.8209 | 80.1339 | 79.4528 | 78.7774 | 78.1078 | 77.4439 | 125.9413 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686 | 134.686
Kingston | 34264 | 87.8796 | 90.524 | 89.7545 | 88.9916 | 88.2352 | 87.4852 | 86.7415 | 86.0042 | 85.2732 | 84.5484 | 83.8297 | 83.1172 | 145.1785 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395 | 146.0395
Knights Road | 30603 | 182.7033 | 183.4787 | 184.258 | 185.0412 | 185.8283 | 186.6193 | 187.4142 | 188.2132 | 189.0161 | 189.8231 | 190.6341 | 191.4491 | 181.02 | 184.474 | 183.9021 | 183.332 | 182.7637 | 182.1971 | 181.6323 | 181.0693 | 180.508 | 179.9484 | 179.3905 | 178.8344
Knights Road | 30604 | 249.3833 | 250.6303 | 251.8834 | 253.1428 | 254.4085 | 255.6806 | 256.959 | 258.2438 | 259.535 | 260.8327 | 262.1368 | 263.4475 | 249.75 | 253.8446 | 253.0577 | 252.2732 | 251.4911 | 250.7115 | 249.9343 | 249.1595 | 248.3871 | 247.6171 | 246.8495 | 246.0843
Knights Road | 30605 | 83.7017 | 85.046 | 85.4712 | 85.8986 | 86.3281 | 86.7597 | 87.1935 | 87.6295 | 88.0676 | 88.5079 | 88.9505 | 89.3952 | 135.4 | 141.9303 | 141.4903 | 141.0517 | 140.6144 | 140.1785 | 139.7439 | 139.3107 | 138.8789 | 138.4484 | 138.0192 | 137.5913
Knights Road | 30606 | 99.7233 | 101.1236 | 101.6292 | 102.1373 | 102.648 | 103.1613 | 103.6771 | 104.1955 | 104.7164 | 105.24 | 105.7662 | 106.2951 | 152.1533 | 157.4489 | 156.9608 | 156.4742 | 155.9891 | 155.5056 | 155.0235 | 154.5429 | 154.0638 | 153.5862 | 153.1101 | 152.6355
Knights Road | 30607 | 90.95 | 91.7597 | 92.2185 | 92.6796 | 93.1429 | 93.6087 | 94.0767 | 94.5471 | 95.0198 | 95.4949 | 95.9724 | 96.4523 | 134.6783 | 137.1889 | 136.7636 | 136.3396 | 135.917 | 135.4956 | 135.0756 | 134.6568 | 134.2394 | 133.8233 | 133.4084 | 132.9948
Knights Road | 30608 | 193.5767 | 194.3236 | 195.0742 | 195.8286 | 196.5867 | 197.3486 | 198.1144 | 198.884 | 199.6574 | 200.4347 | 201.2159 | 202.0009 | 223.6833 | 230.3861 | 229.8089 | 229.2335 | 228.6599 | 228.088 | 227.518 | 226.9497 | 226.3832 | 225.8184 | 225.2554 | 224.6941
Meadowbank | 45001 | 67.7822 | 68.742 | 69.7247 | 70.7309 | 71.7612 | 72.816 | 73.8961 | 75.002 | 76.1343 | 77.2937 | 78.4808 | 79.6963 | 24.83 | 26.0085 | 26.0865 | 26.1651 | 26.2442 | 26.3237 | 26.4038 | 26.4844 | 26.5655 | 26.6471 | 26.7292 | 26.8119
Meadowbank | 45002 | 61.7544 | 62.6362 | 63.539 | 64.4634 | 65.4098 | 66.3789 | 67.3712 | 68.3872 | 69.4274 | 70.4925 | 71.5831 | 72.6997 | 52.0756 | 52.2497 | 52.425 | 52.6014 | 52.7789 | 52.9576 | 53.1374 | 53.3184 | 53.5005 | 53.6838 | 53.8683 | 54.0539
Meadowbank | 45003 | 92.0653 | 94.2656 | 96.5186 | 98.8254 | 101.1873 | 103.6057 | 106.0819 | 108.6172 | 111.2132 | 113.8712 | 116.5927 | 119.3792 | 53.9283 | 55.4544 | 55.8093 | 56.1664 | 56.5259 | 56.8877 | 57.2518 | 57.6182 | 57.9869 | 58.358 | 58.7315 | 59.1074
Mowbray | 62004 | 102.3357 | 143.3387 | 144.106 | 144.8777 | 145.6539 | 146.4346 | 147.2198 | 148.0096 | 148.804 | 149.603 | 150.4066 | 151.2148 | 198.4966 | 249.1978 | 248.5599 | 247.9236 | 247.2888 | 246.6555 | 246.0238 | 245.3936 | 244.7648 | 244.1376 | 243.5119 | 242.8877
Mowbray | 62005 | 81.8104 | 82.2849 | 82.7621 | 83.2421 | 83.7249 | 84.2105 | 84.699 | 85.1902 | 85.6843 | 86.1813 | 86.6811 | 87.1839 | 131.6352 | 135.2441 | 134.9195 | 134.5957 | 134.2727 | 133.9504 | 133.629 | 133.3083 | 132.9883 | 132.6691 | 132.3507 | 132.0331
Mowbray | 62006 | 91.034 | 104.1775 | 104.6055 | 105.036 | 105.4689 | 105.9044 | 106.3424 | 106.7829 | 107.226 | 107.6717 | 108.12 | 108.5708 | 110.5495 | 138.2916 | 138.0525 | 137.814 | 137.576 | 137.3387 | 137.1019 | 136.8657 | 136.63 | 136.3949 | 136.1604 | 135.9264
Mowbray | 62008 | 95.9553 | 96.4478 | 96.9431 | 97.4412 | 97.9423 | 98.4463 | 98.9532 | 99.463 | 99.9758 | 100.4916 | 101.0104 | 101.5321 | 242.8167 | 248.6778 | 248.1075 | 247.5386 | 246.971 | 246.4048 | 245.8399 | 245.2764 | 244.7143 | 244.1535 | 243.5941 | 243.036
Mowbray | 62009 | 90.3979 | 90.9222 | 91.4496 | 91.98 | 92.5134 | 93.05 | 93.5897 | 94.1325 | 94.6785 | 95.2276 | 95.7799 | 96.3355 | 127.7657 | 133.446 | 133.1257 | 132.8062 | 132.4875 | 132.1695 | 131.8523 | 131.5359 | 131.2202 | 130.9052 | 130.5911 | 130.2777
Mowbray | 62010 | 92.9532 | 93.4923 | 94.0346 | 94.58 | 95.1286 | 95.6803 | 96.2352 | 96.7934 | 97.3548 | 97.9195 | 98.4874 | 99.0586 | 112.7151 | 118.3169 | 118.033 | 117.7497 | 117.4671 | 117.1852 | 116.9039 | 116.6234 | 116.3435 | 116.0642 | 115.7857 | 115.5078
Mowbray | 62011 | 40.2177 | 55.2498 | 55.2498 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 55.2499 | 62.0486 | 111.7186 | 111.7156 | 111.7127 | 111.7098 | 111.7069 | 111.704 | 111.7011 | 111.6982 | 111.6953 | 111.6924 | 111.6896
Mowbray | 62013 | 96.0228 | 96.5798 | 97.1399 | 97.7033 | 98.27 | 98.84 | 99.4132 | 99.9898 | 100.5698 | 101.1531 | 101.7398 | 102.3299 | 117.6017 | 120.0487 | 119.7606 | 119.4732 | 119.1865 | 118.9004 | 118.615 | 118.3304 | 118.0464 | 117.7631 | 117.4804 | 117.1985
New Norfolk Terminal | 39563 | 126.5772 | 126.1342 | 125.6927 | 125.2528 | 124.8144 | 124.3775 | 123.9422 | 123.5084 | 123.0761 | 122.6454 | 122.2161 | 121.7884 | 179.3886 | 188.94 | 188.6188 | 188.2981 | 187.978 | 187.6584 | 187.3394 | 187.0209 | 186.703 | 186.3856 | 186.0688 | 185.7524
New Norfolk Terminal | 39565 | 200.7118 | 200.0093 | 199.3093 | 198.6117 | 197.9165 | 197.2238 | 196.5335 | 195.8457 | 195.1602 | 194.4772 | 193.7965 | 193.1182 | 133.2278 | 136.7375 | 136.505 | 136.273 | 136.0413 | 135.81 | 135.5792 | 135.3487 | 135.1186 | 134.8889 | 134.6596 | 134.4307
New Norfolk Terminal | 39568 | 20.312 | 20.3477 | 20.2765 | 20.2055 | 20.1348 | 20.0643 | 19.9941 | 19.9241 | 19.8544 | 19.7849 | 19.7156 | 19.6466 | 22.2458 | 22.6024 | 22.564 | 22.5256 | 22.4873 | 22.4491 | 22.4109 | 22.3728 | 22.3348 | 22.2968 | 22.2589 | 22.2211
New Norfolk Terminal | 39569 | 0.062 | 0.061783 | 0.061567 | 0.061351 | 0.061137 | 0.060923 | 0.060709 | 0.060497 | 0.060285 | 0.060074 | 0.059864 | 0.059654 | 0.098667 | 0.10855 | 0.10837 | 0.10818 | 0.108 | 0.10782 | 0.10763 | 0.10745 | 0.10727 | 0.10708 | 0.1069 | 0.10672
New Norfolk Terminal | 39570 | 133.2537 | 132.7873 | 132.3226 | 131.8595 | 131.3979 | 130.9381 | 130.4798 | 130.0231 | 129.568 | 129.1145 | 128.6626 | 128.2123 | 95.294 | 97.7373 | 97.5711 | 97.4052 | 97.2397 | 97.0744 | 96.9093 | 96.7446 | 96.5801 | 96.4159 | 96.252 | 96.0884
New Norfolk Terminal | 39571 | 92.6572 | 92.3329 | 92.0098 | 91.6877 | 91.3668 | 91.047 | 90.7284 | 90.4108 | 90.0944 | 89.779 | 89.4648 | 89.1517 | 56.7522 | 62.466 | 62.3598 | 62.2537 | 62.1479 | 62.0423 | 61.9368 | 61.8315 | 61.7264 | 61.6215 | 61.5167 | 61.4121
New Norfolk Zone | 35010 | 90.5039 | 90.282 | 89.966 | 89.6512 | 89.3374 | 89.0247 | 88.7131 | 88.4026 | 88.0932 | 87.7849 | 87.4776 | 87.1715 | 136.1456 | 140.5285 | 140.2896 | 140.0511 | 139.8131 | 139.5754 | 139.3381 | 139.1012 | 138.8647 | 138.6287 | 138.393 | 138.1577
New Norfolk Zone | 35011 | 106.4644 | 106.5837 | 106.2107 | 105.839 | 105.4685 | 105.0994 | 104.7315 | 104.365 | 103.9997 | 103.6357 | 103.273 | 102.9115 | 140.1794 | 146.6242 | 146.3749 | 146.1261 | 145.8777 | 145.6297 | 145.3821 | 145.1349 | 144.8882 | 144.6419 | 144.396 | 144.1505
New Norfolk Zone | 35012 | 80.0672 | 79.787 | 79.5077 | 79.2295 | 78.9522 | 78.6758 | 78.4005 | 78.1261 | 77.8526 | 77.5801 | 77.3086 | 77.038 | 121.6344 | 126.3085 | 126.0938 | 125.8794 | 125.6654 | 125.4518 | 125.2385 | 125.0256 | 124.8131 | 124.6009 | 124.3891 | 124.1776
New Town | 16091 | 106.0389 | 107.1977 | 107.9052 | 108.6174 | 109.3343 | 110.0559 | 110.7823 | 111.5134 | 112.2494 | 112.9902 | 113.736 | 114.4866 | 264.1778 | 275.6087 | 277.1246 | 278.6488 | 280.1813 | 281.7223 | 283.2718 | 284.8298 | 286.3964 | 287.9715 | 289.5554 | 291.1479
New Town | 16092 | 82.0778 | 82.9159 | 83.4632 | 84.014 | 84.5685 | 85.1267 | 85.6885 | 86.2541 | 86.8233 | 87.3964 | 87.9732 | 88.5538 | 113.3667 | 114.3569 | 114.9859 | 115.6183 | 116.2542 | 116.8936 | 117.5365 | 118.183 | 118.833 | 119.4866 | 120.1438 | 120.8045
New Town | 16093 | 91.4444 | 92.048 | 92.6555 | 93.267 | 93.8826 | 94.5022 | 95.1259 | 95.7537 | 96.3857 | 97.0219 | 97.6622 | 98.3068 | 150.1114 | 162.1677 | 163.0596 | 163.9565 | 164.8582 | 165.7649 | 166.6767 | 167.5934 | 168.5151 | 169.442 | 170.3739 | 171.311
New Town | 16094 | 170.9278 | 174.362 | 175.5128 | 176.6712 | 177.8372 | 179.0109 | 180.1924 | 181.3817 | 182.5788 | 183.7838 | 184.9968 | 186.2178 | 221.25 | 223.11 | 224.3371 | 225.5709 | 226.8116 | 228.059 | 229.3133 | 230.5746 | 231.8427 | 233.1179 | 234.4 | 235.6892
New Town | 16095 | 63.4722 | 63.8911 | 64.3128 | 64.7373 | 65.1646 | 65.5946 | 66.0276 | 66.4633 | 66.902 | 67.3436 | 67.788 | 68.2354 | 77.4278 | 78.0488 | 78.478 | 78.9097 | 79.3437 | 79.7801 | 80.2189 | 80.66 | 81.1037 | 81.5498 | 81.9983 | 82.4493
New Town | 16096 | 103.3111 | 106.0382 | 106.738 | 107.4425 | 108.1516 | 108.8654 | 109.5839 | 110.3072 | 111.0352 | 111.768 | 112.5057 | 113.2482 | 195.5611 | 207.149 | 208.2884 | 209.4339 | 210.5858 | 211.7441 | 212.9086 | 214.0796 | 215.2571 | 216.441 | 217.6314 | 218.8284
New Town | 16097 | 47.8276 | 48.1433 | 48.461 | 48.7809 | 49.1028 | 49.4269 | 49.7531 | 50.0815 | 50.412 | 50.7448 | 51.0797 | 51.4168 | 57.3722 | 58.1894 | 58.5095 | 58.8313 | 59.1548 | 59.4802 | 59.8073 | 60.1363 | 60.467 | 60.7996 | 61.134 | 61.4702
New Town | 16098 | 170.9889 | 176.0045 | 177.1661 | 178.3354 | 179.5124 | 180.6972 | 181.8898 | 183.0903 | 184.2987 | 185.5151 | 186.7395 | 187.9719 | 253.0944 | 263.2729 | 264.7209 | 266.1769 | 267.6408 | 269.1129 | 270.593 | 272.0812 | 273.5777 | 275.0824 | 276.5953 | 278.1166
Newton | 96202 | 85.8544 | 85.5969 | 85.3401 | 85.0841 | 84.8288 | 84.5743 | 84.3206 | 84.0677 | 83.8154 | 83.564 | 83.3133 | 83.0634 | 95.8206 | 96.0043 | 95.8411 | 95.6782 | 95.5155 | 95.3531 | 95.191 | 95.0292 | 94.8677 | 94.7064 | 94.5454 | 94.3847
North Hobart | 18131A | 159.8703 | 159.4227 | 158.9763 | 158.5312 | 158.0873 | 157.6447 | 157.2032 | 156.7631 | 156.3241 | 155.8864 | 155.45 | 155.0147 | 157.1429 | 171.3733 | 172.5386 | 173.7119 | 174.8931 | 176.0824 | 177.2797 | 178.4852 | 179.6989 | 180.9209 | 182.1511 | 183.3898
North Hobart | 18131B | 135.9733 | 135.5926 | 135.213 | 134.8344 | 134.4568 | 134.0803 | 133.7049 | 133.3305 | 132.9572 | 132.5849 | 132.2137 | 131.8435 | 187.5724 | 193.2926 | 194.607 | 195.9303 | 197.2626 | 198.604 | 199.9545 | 201.3142 | 202.6832 | 204.0614 | 205.449 | 206.8461
North Hobart | 18132A | 10.4831 | 10.4538 | 10.4245 | 10.3953 | 10.3662 | 10.3372 | 10.3082 | 10.2794 | 10.2506 | 10.2219 | 10.1933 | 10.1647 | 20.1238 | 21.2593 | 21.4039 | 21.5494 | 21.696 | 21.8435 | 21.992 | 22.1416 | 22.2921 | 22.4437 | 22.5964 | 22.75
North Hobart | 18132B | 111.108 | 110.7969 | 110.4867 | 110.1773 | 109.8688 | 109.5612 | 109.2544 | 108.9485 | 108.6434 | 108.3392 | 108.0359 | 107.7334 | 137.2298 | 140.0814 | 141.0339 | 141.993 | 142.9585 | 143.9306 | 144.9094 | 145.8947 | 146.8868 | 147.8857 | 148.8913 | 149.9037
North Hobart | 18133A | 100.9112 | 100.3966 | 99.8835 | 99.3718 | 115.4361 | 114.9273 | 114.4198 | 113.9138 | 113.4092 | 112.906 | 112.4043 | 111.9039 | 124.896 | 128.0508 | 129.4851 | 130.9291 | 148.9576 | 150.4213 | 151.895 | 153.3788 | 154.8726 | 156.3765 | 157.8907 | 159.4152
North Hobart | 18133B | 27.0683 | 26.9925 | 26.917 | 26.8416 | 26.7664 | 26.6915 | 26.6168 | 26.5422 | 26.4679 | 26.3938 | 26.3199 | 26.2462 | 41.0647 | 44.2081 | 44.5087 | 44.8114 | 45.1161 | 45.4229 | 45.7318 | 46.0428 | 46.3559 | 46.6711 | 46.9884 | 47.308
North Hobart | 18134A | 49.3191 | 49.465 | 49.3265 | 49.1884 | 49.0507 | 48.9133 | 48.7764 | 48.6398 | 48.5036 | 48.3678 | 48.2324 | 48.0973 | 77.2893 | 83.631 | 84.1997 | 84.7722 | 85.3487 | 85.929 | 86.5134 | 87.1017 | 87.6939 | 88.2903 | 88.8906 | 89.4951
North Hobart | 18134B | 26.5671 | 26.9374 | 26.862 | 26.7868 | 26.7117 | 26.6369 | 26.5624 | 26.488 | 26.4138 | 26.3399 | 26.2661 | 26.1926 | 42.8298 | 45.8955 | 46.2076 | 46.5218 | 46.8382 | 47.1567 | 47.4774 | 47.8002 | 48.1252 | 48.4525 | 48.782 | 49.1137
North Hobart | 18135A | 63.8157 | 63.6452 | 63.467 | 63.2893 | 63.1121 | 62.9353 | 62.7591 | 62.5834 | 62.4082 | 62.2334 | 62.0592 | 61.8854 | 12.8691 | 14.6184 | 14.7179 | 14.8179 | 14.9187 | 15.0201 | 15.1223 | 15.2251 | 15.3286 | 15.4329 | 15.5378 | 15.6435
North Hobart | 18135B | 68.7174 | 68.525 | 68.3331 | 68.1418 | 67.951 | 67.7607 | 67.571 | 67.3818 | 67.1931 | 67.005 | 66.8174 | 66.6303 | 99.9669 | 105.265 | 105.9808 | 106.7015 | 107.4271 | 108.1576 | 108.893 | 109.6335 | 110.379 | 111.1296 | 111.8853 | 112.6461
North Hobart | 18136A | 54.0416 | 56.257 | 56.0994 | 55.9424 | 55.7857 | 55.6295 | 55.4738 | 55.3184 | 55.1635 | 55.0091 | 54.8551 | 54.7015 | 104.1713 | 106.8027 | 107.5289 | 108.2601 | 108.9963 | 109.7375 | 110.4837 | 111.235 | 111.9914 | 112.7529 | 113.5196 | 114.2916
North Hobart | 18136B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18141B | 111.9447 | 111.6312 | 111.3187 | 111.007 | 110.6961 | 110.3862 | 110.0771 | 109.7689 | 109.4615 | 109.1551 | 108.8494 | 108.5446 | 164.3296 | 166.0434 | 167.1725 | 168.3092 | 169.4537 | 170.606 | 171.7661 | 172.9341 | 174.1101 | 175.294 | 176.486 | 177.6862
North Hobart | 18142A | 69.8027 | 69.6072 | 69.4123 | 69.218 | 69.0242 | 68.8309 | 68.6382 | 68.446 | 68.2543 | 68.0632 | 67.8726 | 67.6826 | 29.5757 | 29.926 | 30.1295 | 30.3344 | 30.5406 | 30.7483 | 30.9574 | 31.1679 | 31.3799 | 31.5932 | 31.8081 | 32.0244
North Hobart | 18142B | 34.9077 | 34.8099 | 34.7125 | 34.6153 | 34.5183 | 34.4217 | 34.3253 | 34.2292 | 34.1334 | 34.0378 | 33.9425 | 33.8474 | 42.2707 | 45.6983 | 46.0091 | 46.3219 | 46.6369 | 46.9541 | 47.2733 | 47.5948 | 47.9184 | 48.2443 | 48.5723 | 48.9026
North Hobart | 18143A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8529 | 27.0355 | 27.2193 | 27.4044 | 27.5907 | 27.7784 | 27.9673 | 28.1574 | 28.3489 | 28.5417 | 28.7358
North Hobart | 18143B | 160.1729 | 162.8166 | 162.3607 | 161.9061 | 161.4527 | 161.0007 | 160.5499 | 160.1003 | 159.6521 | 159.205 | 158.7593 | 158.3147 | 235.5676 | 252.1014 | 253.8156 | 255.5416 | 257.2793 | 259.0288 | 260.7902 | 262.5635 | 264.349 | 266.1465 | 267.9563 | 269.7784
North Hobart | 18144A | 54.171 | 54.7317 | 54.5784 | 54.4256 | 54.2732 | 54.1212 | 53.9697 | 53.8186 | 53.6679 | 53.5176 | 53.3678 | 53.2183 | 101.1334 | 121.7392 | 122.567 | 123.4005 | 124.2396 | 125.0844 | 125.935 | 126.7914 | 127.6535 | 128.5216 | 129.3955 | 130.2754
North Hobart | 18144B | 95.0231 | 95.2067 | 94.9401 | 94.6743 | 94.4092 | 94.1448 | 93.8812 | 93.6184 | 93.3562 | 93.0948 | 92.8342 | 92.5742 | 136.6773 | 140.2954 | 141.2494 | 142.2099 | 143.1769 | 144.1505 | 145.1307 | 146.1176 | 147.1112 | 148.1116 | 149.1187 | 150.1327
North Hobart | 18145A | 43.7308 | 44.303 | 44.1789 | 44.0552 | 43.9319 | 43.8089 | 43.6862 | 43.5639 | 43.4419 | 43.3203 | 43.199 | 43.078 | 0 | 67.8658 | 68.3272 | 68.7919 | 69.2596 | 69.7306 | 70.2048 | 70.6822 | 71.1628 | 71.6467 | 72.1339 | 72.6244
North Hobart | 18145B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North Hobart | 18146A | 107.5796 | 108.1954 | 107.8925 | 107.5904 | 107.2891 | 106.9887 | 106.6892 | 106.3904 | 106.0925 | 105.7955 | 105.4993 | 105.2039 | 386.1578 | 408.2311 | 411.0071 | 413.8019 | 416.6158 | 419.4488 | 422.301 | 425.1727 | 428.0638 | 430.9747 | 433.9053 | 436.8559
North Hobart | 18146B | 150.3142 | 152.5804 | 152.1532 | 151.7271 | 151.3023 | 150.8787 | 150.4562 | 150.0349 | 149.6148 | 149.1959 | 148.7782 | 148.3616 | 222.5834 | 241.062 | 242.7012 | 244.3516 | 246.0132 | 247.6861 | 249.3703 | 251.066 | 252.7733 | 254.4921 | 256.2227 | 257.965
Norwood | 65060 | 104.172 | 103.6303 | 103.0915 | 102.5554 | 102.0221 | 101.4916 | 100.9638 | 100.4388 | 99.9165 | 99.397 | 98.8801 | 98.3659 | 45.2719 | 46.2677 | 46.1427 | 46.0181 | 45.8939 | 45.77 | 45.6464 | 45.5232 | 45.4002 | 45.2777 | 45.1554 | 45.0335
Norwood | 65061 | 57.4918 | 57.1928 | 56.8954 | 56.5996 | 56.3052 | 56.0125 | 55.7212 | 55.4314 | 55.1432 | 54.8565 | 54.5712 | 54.2874 | 91.3695 | 94.0295 | 93.7756 | 93.5224 | 93.2699 | 93.0181 | 92.7669 | 92.5165 | 92.2667 | 92.0176 | 91.7691 | 91.5213
Norwood | 65062 | 81.2623 | 80.8398 | 80.4194 | 80.0012 | 79.5852 | 79.1714 | 78.7597 | 78.3501 | 77.9427 | 77.5374 | 77.1342 | 76.7331 | 129.5058 | 129.7734 | 129.423 | 129.0735 | 128.725 | 128.3775 | 128.0309 | 127.6852 | 127.3404 | 126.9966 | 126.6537 | 126.3118
Norwood | 65063 | 44.315 | 44.8694 | 44.6361 | 44.404 | 44.1731 | 43.9434 | 43.7149 | 43.4876 | 43.2614 | 43.0365 | 42.8127 | 42.59 | 53.5488 | 58.1837 | 58.0266 | 57.8699 | 57.7137 | 57.5579 | 57.4025 | 57.2475 | 57.0929 | 56.9387 | 56.785 | 56.6317
Norwood | 65064 | 54.8884 | 54.603 | 54.3191 | 54.0366 | 53.7556 | 53.4761 | 53.198 | 52.9214 | 52.6462 | 52.3725 | 52.1001 | 51.8292 | 92.0138 | 95.7213 | 95.4629 | 95.2051 | 94.948 | 94.6917 | 94.436 | 94.181 | 93.9268 | 93.6732 | 93.4202 | 93.168
Norwood | 65065 | 102.808 | 101.9861 | 101.1685 | 100.3551 | 99.546 | 98.741 | 97.9403 | 97.1437 | 96.3513 | 95.563 | 94.7787 | 93.9986 | 167.3823 | 173.256 | 172.639 | 172.0238 | 171.4101 | 170.7981 | 170.1878 | 169.5791 | 168.9721 | 168.3667 | 167.7629 | 167.1608
Norwood | 65066 | 63.53 | 69.14 | 68.81 | 68.48 | 68.15 | 67.83 | 67.5 | 67.18 | 66.86 | 66.54 | 66.22 | 65.91 | 105.9416 | 116.0169 | 115.7186 | 115.4211 | 115.1244 | 114.8285 | 114.5333 | 114.239 | 113.9455 | 113.6527 | 113.3608 | 113.0696
Norwood | 65067 | 43.135 | 42.9107 | 42.6876 | 42.4656 | 42.2448 | 42.0251 | 41.8066 | 41.5892 | 41.3729 | 41.1578 | 40.9438 | 40.7308 | 52.3575 | 53.7438 | 53.5987 | 53.454 | 53.3097 | 53.1657 | 53.0222 | 52.879 | 52.7363 | 52.5939 | 52.4519 | 52.3103
Palmerston | 51001 | 8.9097 | 11.957 | 11.9211 | 11.8854 | 11.8497 | 11.8142 | 11.7787 | 11.7434 | 11.7081 | 11.673 | 11.638 | 11.6031 | 10.0182 | 10.0012 | 9.9842 | 9.9672 | 9.9503 | 9.9334 | 9.9165 | 9.8996 | 9.8828 | 9.866 | 9.8492 | 9.8325
Palmerston | 51002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Palmerston | 51003 | 179.1116 | 178.5743 | 178.0386 | 177.5045 | 176.9719 | 176.441 | 175.9117 | 175.384 | 174.8578 | 174.3332 | 173.8102 | 173.2888 | 67.2411 | 69.8866 | 69.7678 | 69.6492 | 69.5307 | 69.4125 | 69.2945 | 69.1767 | 69.0591 | 68.9417 | 68.8245 | 68.7075
Palmerston | 51004 | 80.422 | 80.1808 | 79.9402 | 79.7004 | 79.4613 | 79.2229 | 78.9852 | 78.7483 | 78.5121 | 78.2765 | 78.0417 | 77.8076 | 35.4621 | 36.3206 | 36.2589 | 36.1972 | 36.1357 | 36.0743 | 36.0129 | 35.9517 | 35.8906 | 35.8296 | 35.7687 | 35.7079
Port Latta | 94001 | 117.5736 | 119.7122 | 119.3531 | 118.995 | 118.638 | 118.2821 | 117.9273 | 117.5735 | 117.2207 | 116.8691 | 116.5185 | 116.1689 | 53.9078 | 54.9744 | 54.8809 | 54.7876 | 54.6945 | 54.6015 | 54.5087 | 54.416 | 54.3235 | 54.2311 | 54.139 | 54.0469
Port Latta | 94002 | 78.6926 | 78.4565 | 78.2212 | 77.9865 | 77.7525 | 77.5193 | 77.2867 | 77.0549 | 76.8237 | 76.5932 | 76.3635 | 76.1343 | 54.6049 | 55.6831 | 55.5884 | 55.4939 | 55.3995 | 55.3054 | 55.2114 | 55.1175 | 55.0238 | 54.9303 | 54.8369 | 54.7437
Queenstown | 98001 | 51.3357 | 51.7971 | 51.5796 | 51.3629 | 51.1472 | 50.9324 | 50.7185 | 50.5055 | 50.2933 | 50.0821 | 49.8717 | 49.6623 | 50.8878 | 53.0896 | 53.0046 | 52.9198 | 52.8352 | 52.7506 | 52.6662 | 52.582 | 52.4978 | 52.4138 | 52.33 | 52.2462
Queenstown | 98002 | 41.8147 | 42.9779 | 42.7974 | 42.6177 | 42.4387 | 42.2604 | 42.0829 | 41.9062 | 41.7302 | 41.5549 | 41.3804 | 41.2066 | 60.3255 | 59.2565 | 59.1617 | 59.067 | 58.9725 | 58.8781 | 58.7839 | 58.6899 | 58.596 | 58.5022 | 58.4086 | 58.3152
Queenstown | 98003 | 20.408 | 21.0151 | 20.9268 | 20.8389 | 20.7514 | 20.6642 | 20.5775 | 20.491 | 20.405 | 20.3193 | 20.2339 | 20.1489 | 34.282 | 33.7874 | 33.7334 | 33.6794 | 33.6255 | 33.5717 | 33.518 | 33.4644 | 33.4108 | 33.3574 | 33.304 | 33.2507
Railton | 85001 | 114.7303 | 114.65 | 114.5697 | 114.4895 | 114.4094 | 114.3293 | 114.2493 | 114.1693 | 114.0894 | 114.0095 | 113.9297 | 113.85 | 156.5532 | 161.3393 | 161.2747 | 161.2102 | 161.1457 | 161.0813 | 161.0168 | 160.9524 | 160.8881 | 160.8237 | 160.7594 | 160.6951
Railton | 85002 | 167.7156 | 167.5982 | 167.4809 | 167.3636 | 167.2465 | 167.1294 | 167.0124 | 166.8955 | 166.7787 | 166.6619 | 166.5453 | 166.4287 | 196.3434 | 200.8504 | 200.77 | 200.6897 | 200.6094 | 200.5292 | 200.449 | 200.3688 | 200.2886 | 200.2085 | 200.1285 | 200.0484
Railton | 85003 | 100.5377 | 100.4673 | 100.397 | 100.3267 | 100.2565 | 100.1863 | 100.1162 | 100.0461 | 99.9761 | 99.9061 | 99.8362 | 99.7663 | 85.2588 | 87.5564 | 87.5214 | 87.4864 | 87.4514 | 87.4164 | 87.3815 | 87.3465 | 87.3116 | 87.2766 | 87.2417 | 87.2068
Railton | 85004 | 119.1873 | 119.1039 | 119.0205 | 118.9372 | 118.8539 | 118.7707 | 118.6876 | 118.6045 | 118.5215 | 118.4385 | 118.3556 | 118.2728 | 63.0703 | 66.0223 | 65.9959 | 65.9695 | 65.9431 | 65.9167 | 65.8904 | 65.864 | 65.8377 | 65.8113 | 65.785 | 65.7587
Railton | 85005 | 285.9602 | 285.76 | 285.56 | 285.3601 | 285.1604 | 284.9607 | 284.7613 | 284.5619 | 284.3627 | 284.1637 | 283.9648 | 283.766 | 285.0666 | 295.7881 | 295.6698 | 295.5515 | 295.4333 | 295.3151 | 295.197 | 295.0789 | 294.9609 | 294.8429 | 294.725 | 294.6071
Railton | 85006 | 213.6329 | 213.4834 | 213.3339 | 213.1846 | 213.0354 | 212.8862 | 212.7372 | 212.5883 | 212.4395 | 212.2908 | 212.1422 | 211.9937 | 138.8794 | 144.2554 | 144.1977 | 144.1401 | 144.0824 | 144.0248 | 143.9672 | 143.9096 | 143.852 | 143.7945 | 143.7369 | 143.6795
Railton | 85007 | 327.9646 | 337.0802 | 336.8443 | 336.6085 | 336.3729 | 336.1374 | 335.9021 | 335.667 | 335.432 | 335.1972 | 334.9626 | 334.7281 | 327.3966 | 330.8515 | 330.7191 | 330.5868 | 330.4546 | 330.3224 | 330.1903 | 330.0582 | 329.9262 | 329.7942 | 329.6623 | 329.5304
Railton | 85008 | 102.217 | 102.1454 | 102.0739 | 102.0025 | 101.9311 | 101.8597 | 101.7884 | 101.7172 | 101.646 | 101.5748 | 101.5037 | 101.4327 | 145.3088 | 157.971 | 157.9079 | 157.8447 | 157.7815 | 157.7184 | 157.6553 | 157.5923 | 157.5293 | 157.4662 | 157.4033 | 157.3403
Richmond | 40001 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 88.18 | 101.2778 | 105.2809 | 105.1125 | 104.9443 | 104.7764 | 104.6088 | 104.4414 | 104.2743 | 104.1074 | 103.9409 | 103.7746 | 103.6085
Richmond | 40002 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 27.1128 | 32.78 | 34.4126 | 34.3576 | 34.3026 | 34.2477 | 34.1929 | 34.1382 | 34.0836 | 34.029 | 33.9746 | 33.9202 | 33.866
Richmond | 40003 | 50.5939 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 52.1675 | 37.6461 | 38.8732 | 38.811 | 38.7489 | 38.6869 | 38.625 | 38.5632 | 38.5015 | 38.4399 | 38.3784 | 38.317 | 38.2557
Rokeby | 28221 | 78.9448 | 79.4903 | 78.9895 | 78.4919 | 77.9974 | 77.506 | 77.0178 | 76.5325 | 76.0504 | 75.5713 | 75.0952 | 74.6221 | 110.351 | 116.7691 | 116.5706 | 116.3724 | 116.1746 | 115.9771 | 115.7799 | 115.5831 | 115.3866 | 115.1904 | 114.9946 | 114.7991
Rokeby | 28222 | 106.687 | 108.0085 | 107.3281 | 106.6519 | 105.98 | 105.3123 | 104.6489 | 103.9896 | 103.3344 | 102.6834 | 102.0365 | 101.3937 | 140.0543 | 144.9259 | 144.6795 | 144.4335 | 144.188 | 143.9429 | 143.6982 | 143.4539 | 143.21 | 142.9666 | 142.7235 | 142.4809
Rokeby | 28223 | 165.6956 | 166.9939 | 165.9418 | 164.8964 | 163.8576 | 162.8253 | 161.7995 | 160.7801 | 159.7672 | 158.7607 | 157.7605 | 156.7666 | 226.7469 | 236.4402 | 236.0382 | 235.637 | 235.2364 | 234.8365 | 234.4373 | 234.0387 | 233.6409 | 233.2437 | 232.8472 | 232.4513
Rokeby | 28224 | 76.6216 | 76.8223 | 76.3384 | 75.8574 | 75.3795 | 74.9046 | 74.4327 | 73.9638 | 73.4978 | 73.0348 | 72.5747 | 72.1175 | 109.8861 | 116.4952 | 116.2972 | 116.0995 | 115.9021 | 115.7051 | 115.5084 | 115.312 | 115.116 | 114.9203 | 114.7249 | 114.5299
Rokeby | 28225 | 4.4546 | 4.4278 | 4.3999 | 4.3722 | 4.3447 | 4.3173 | 4.2901 | 4.2631 | 4.2362 | 4.2095 | 4.183 | 4.1567 | 5.3782 | 5.4557 | 5.4465 | 5.4372 | 5.428 | 5.4187 | 5.4095 | 5.4003 | 5.3911 | 5.382 | 5.3728 | 5.3637
Rokeby | 28228 | 64.1012 | 64.6528 | 64.2455 | 63.8407 | 63.4385 | 63.0388 | 62.6417 | 62.2471 | 61.8549 | 61.4652 | 61.078 | 60.6932 | 98.7789 | 104.6089 | 104.431 | 104.2535 | 104.0763 | 103.8993 | 103.7227 | 103.5464 | 103.3704 | 103.1946 | 103.0192 | 102.8441
Rokeby | 28229 | 7.5703 | 7.5583 | 7.5107 | 7.4634 | 7.4164 | 7.3697 | 7.3232 | 7.2771 | 7.2312 | 7.1857 | 7.1404 | 7.0954 | 10.9299 | 11.8057 | 11.7856 | 11.7656 | 11.7456 | 11.7256 | 11.7057 | 11.6858 | 11.6659 | 11.6461 | 11.6263 | 11.6065
Rokeby | 28230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rokeby | 28231 | 146.3483 | 146.622 | 145.6983 | 144.7804 | 143.8683 | 142.9619 | 142.0612 | 141.1663 | 140.2769 | 139.3932 | 138.515 | 137.6423 | 201.1483 | 204.2728 | 203.9255 | 203.5789 | 203.2328 | 202.8873 | 202.5424 | 202.1981 | 201.8543 | 201.5112 | 201.1686 | 200.8266
Rokeby | 28232 | 120.9933 | 121.9294 | 121.1613 | 120.3979 | 119.6394 | 118.8857 | 118.1367 | 117.3925 | 116.6529 | 115.918 | 115.1877 | 114.462 | 174.448 | 187.1113 | 186.7932 | 186.4757 | 186.1587 | 185.8422 | 185.5263 | 185.2109 | 184.896 | 184.5817 | 184.2679 | 183.9546
Rosebery | 97001 | 25.1364 | 25.501 | 25.4679 | 25.4348 | 25.4017 | 25.3687 | 25.3357 | 25.3028 | 25.2699 | 25.237 | 25.2042 | 25.1715 | 27.5137 | 27.136 | 27.0953 | 27.0546 | 27.0141 | 26.9735 | 26.9331 | 26.8927 | 26.8523 | 26.8121 | 26.7718 | 26.7317
Rosebery | 97002 | 35.8567 | 36.7595 | 36.7118 | 36.664 | 36.6164 | 36.5688 | 36.5212 | 36.4738 | 36.4263 | 36.379 | 36.3317 | 36.2845 | 32.7617 | 35.7699 | 35.7163 | 35.6627 | 35.6092 | 35.5558 | 35.5024 | 35.4492 | 35.396 | 35.3429 | 35.2899 | 35.237
Rosebery | 97013 | 10.137 | 10.2839 | 10.2746 | 10.2654 | 10.2562 | 10.2469 | 10.2377 | 10.2285 | 10.2193 | 10.2101 | 10.2009 | 10.1917 | 16.0494 | 17.2216 | 17.2044 | 17.1871 | 17.17 | 17.1528 | 17.1356 | 17.1185 | 17.1014 | 17.0843 | 17.0672 | 17.0501
Rosebery | 97014 | 216.2996 | 217.2204 | 217.0249 | 216.8296 | 216.6345 | 216.4395 | 216.2447 | 216.0501 | 215.8556 | 215.6614 | 215.4673 | 215.2733 | 229.6687 | 229.4391 | 229.2096 | 228.9804 | 228.7515 | 228.5227 | 228.2942 | 228.0659 | 227.8378 | 227.61 | 227.3824 | 227.155
Rosny Park | 23341 | 170.9239 | 172.3122 | 172.4443 | 172.5767 | 172.7094 | 172.8424 | 172.9756 | 173.1091 | 173.2429 | 173.377 | 173.5114 | 173.646 | 117.0867 | 200.6688 | 200.6793 | 200.6898 | 200.7004 | 200.711 | 200.7217 | 200.7325 | 200.7434 | 200.7543 | 200.7652 | 200.7763
Rosny Park | 23342 | 112.41 | 113.689 | 113.7363 | 113.7837 | 113.8312 | 113.8789 | 113.9266 | 113.9744 | 114.0223 | 114.0703 | 114.1184 | 114.1666 | 173.2172 | 175.7168 | 175.7756 | 175.8348 | 175.8943 | 175.9542 | 176.0144 | 176.075 | 176.136 | 176.1973 | 176.2589 | 176.3209
Rosny Park | 23343 | 115.2261 | 115.2767 | 115.3273 | 115.378 | 115.4289 | 115.4799 | 115.5309 | 115.5821 | 115.6334 | 115.6848 | 115.7363 | 115.7879 | 175.7722 | 176.9159 | 176.9818 | 177.0481 | 177.1148 | 177.1818 | 177.2493 | 177.3172 | 177.3854 | 177.4541 | 177.5232 | 177.5927
Rosny Park | 23347 | 109.8439 | 111.2954 | 111.3632 | 111.4312 | 111.4993 | 111.5675 | 111.6359 | 111.7044 | 111.7731 | 111.8419 | 111.9108 | 111.9799 | 162.9483 | 175.2307 | 175.417 | 175.6045 | 175.793 | 175.9827 | 176.1735 | 176.3654 | 176.5584 | 176.7526 | 176.9479 | 177.1444
Rosny Park | 23348 | 87.7589 | 119.5532 | 119.5554 | 119.5576 | 119.5598 | 119.562 | 119.5642 | 119.5664 | 119.5687 | 119.5709 | 119.5731 | 119.5754 | 124.0117 | 218.1927 | 218.2088 | 218.225 | 218.2412 | 218.2576 | 218.274 | 218.2905 | 218.3072 | 218.3239 | 218.3407 | 218.3577
Sandy Bay | 12017 | 124.22 | 128.3426 | 129.472 | 130.6113 | 131.7607 | 132.9202 | 134.0899 | 135.2699 | 136.4603 | 137.6611 | 138.8725 | 140.0946 | 173.1769 | 174.5371 | 175.5145 | 176.4973 | 177.4857 | 178.4797 | 179.4791 | 180.4842 | 181.4949 | 182.5113 | 183.5334 | 184.5612
Sandy Bay | 12018 | 91.8672 | 94.6695 | 95.5026 | 96.3431 | 97.1909 | 98.0462 | 98.909 | 99.7794 | 100.6574 | 101.5432 | 102.4368 | 103.3382 | 146.4278 | 156.5962 | 157.4732 | 158.355 | 159.2418 | 160.1335 | 161.0303 | 161.9321 | 162.8389 | 163.7508 | 164.6678 | 165.5899
Sandy Bay | 12019 | 120.095 | 122.856 | 123.9371 | 125.0278 | 126.128 | 127.2379 | 128.3576 | 129.4872 | 130.6267 | 131.7762 | 132.9358 | 134.1056 | 190.3417 | 215.7192 | 216.9272 | 218.142 | 219.3636 | 220.5921 | 221.8274 | 223.0696 | 224.3188 | 225.575 | 226.8382 | 228.1085
Sandy Bay | 12030 | 111.4217 | 114.904 | 115.9152 | 116.9352 | 117.9643 | 119.0023 | 120.0496 | 121.106 | 122.1717 | 123.2468 | 124.3314 | 125.4255 | 141.4267 | 148.1508 | 148.9804 | 149.8147 | 150.6537 | 151.4974 | 152.3457 | 153.1989 | 154.0568 | 154.9195 | 155.7871 | 156.6595
Sandy Bay | 12031 | 149.7822 | 154.5116 | 155.8713 | 157.243 | 158.6267 | 160.0227 | 161.4309 | 162.8514 | 164.2845 | 165.7302 | 167.1887 | 168.6599 | 243.3894 | 259.647 | 261.101 | 262.5632 | 264.0335 | 265.5121 | 266.999 | 268.4942 | 269.9977 | 271.5097 | 273.0302 | 274.5592
Sandy Bay | 12032 | 82.3744 | 84.8685 | 85.6153 | 86.3688 | 87.1288 | 87.8955 | 88.669 | 89.4493 | 90.2365 | 91.0305 | 91.8316 | 92.6397 | 102.2978 | 106.5138 | 107.1103 | 107.7101 | 108.3133 | 108.9198 | 109.5298 | 110.1431 | 110.7599 | 111.3802 | 112.0039 | 112.6312
Sandy Bay | 12033 | 37.7817 | 38.7711 | 39.1123 | 39.4565 | 39.8037 | 40.154 | 40.5073 | 40.8638 | 41.2234 | 41.5861 | 41.9521 | 42.3213 | 62.2267 | 67.2257 | 67.6021 | 67.9807 | 68.3614 | 68.7442 | 69.1292 | 69.5163 | 69.9056 | 70.2971 | 70.6907 | 71.0866
Sandy Bay | 12035 | 96.41 | 99.0289 | 99.9003 | 100.7795 | 101.6663 | 102.561 | 103.4635 | 104.374 | 105.2925 | 106.2191 | 107.1538 | 108.0967 | 156.7472 | 166.0912 | 167.0213 | 167.9566 | 168.8972 | 169.843 | 170.7941 | 171.7505 | 172.7123 | 173.6795 | 174.6521 | 175.6302
Sandy Bay | 12036 | 152.3183 | 154.0222 | 155.3776 | 156.7449 | 158.1243 | 159.5158 | 160.9195 | 162.3356 | 163.7641 | 165.2053 | 166.6591 | 168.1257 | 244.595 | 246.8685 | 248.2509 | 249.6412 | 251.0391 | 252.445 | 253.8587 | 255.2803 | 256.7098 | 258.1474 | 259.593 | 261.0468
Sandy Bay | 12037 | 108.6028 | 110.0913 | 111.0601 | 112.0374 | 113.0233 | 114.018 | 115.0213 | 116.0335 | 117.0546 | 118.0847 | 119.1238 | 120.1721 | 127.4139 | 133.6016 | 134.3498 | 135.1021 | 135.8587 | 136.6195 | 137.3846 | 138.154 | 138.9276 | 139.7056 | 140.488 | 141.2747
Sandy Bay | 12038 | 97.2333 | 100.186 | 101.0677 | 101.957 | 102.8543 | 103.7594 | 104.6725 | 105.5936 | 106.5228 | 107.4602 | 108.4059 | 109.3598 | 186.7256 | 202.9542 | 204.0908 | 205.2337 | 206.383 | 207.5387 | 208.7009 | 209.8697 | 211.0449 | 212.2268 | 213.4153 | 214.6104
Sandy Bay | 12039 | 118.8472 | 119.8931 | 120.9481 | 122.0125 | 123.0862 | 124.1693 | 125.262 | 126.3643 | 127.4764 | 128.5981 | 129.7298 | 130.8714 | 184.1967 | 193.1143 | 194.1957 | 195.2832 | 196.3768 | 197.4765 | 198.5824 | 199.6944 | 200.8127 | 201.9373 | 203.0681 | 204.2053
Savage River | 95001 | 17.8261 | 18.5108 | 18.4608 | 18.4109 | 18.3612 | 18.3117 | 18.2622 | 18.2129 | 18.1637 | 18.1147 | 18.0658 | 18.017 | 31.3683 | 32.0116 | 31.9572 | 31.9029 | 31.8486 | 31.7945 | 31.7404 | 31.6865 | 31.6326 | 31.5788 | 31.5252 | 31.4716
Scottsdale | 54003 | 140.35 | 169.2235 | 170.4838 | 171.7552 | 173.038 | 174.3322 | 175.6379 | 176.9552 | 178.2842 | 179.6251 | 180.9779 | 182.3427 | 117.3444 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334 | 149.6334
Scottsdale | 54004 | 14.3333 | 14.4609 | 14.5896 | 14.7195 | 14.8505 | 14.9826 | 15.116 | 15.2505 | 15.3862 | 15.5232 | 15.6613 | 15.8007 | 15.6667 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721 | 16.1721
Scottsdale | 54005 | 99.9778 | 111.9173 | 112.8151 | 113.7208 | 114.6346 | 115.5565 | 116.4866 | 117.425 | 118.3717 | 119.3269 | 120.2905 | 121.2628 | 76.9556 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944 | 78.0944
Scottsdale | 54006 | 9.8944 | 9.9825 | 10.0714 | 10.161 | 10.2514 | 10.3427 | 10.4347 | 10.5276 | 10.6213 | 10.7158 | 10.8112 | 10.9074 | 20.7 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715 | 21.2715
Scottsdale | 54007 | 52.6333 | 53.1018 | 53.5744 | 54.0512 | 54.5322 | 55.0176 | 55.5072 | 56.0012 | 56.4997 | 57.0025 | 57.5098 | 58.0217 | 93.3778 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224 | 95.8224
Smithton | 93001 | 130.8648 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 133.9207 | 105.1871 | 105.4243 | 105.3621 | 105.3 | 105.2378 | 105.1758 | 105.1138 | 105.0518 | 104.9899 | 104.928 | 104.8661 | 104.8043
Smithton | 93002 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 174.0949 | 123.1446 | 123.2823 | 123.196 | 123.1098 | 123.0236 | 122.9375 | 122.8514 | 122.7654 | 122.6795 | 122.5936 | 122.5078 | 122.4221
Smithton | 93003 | 57.151 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 63.0203 | 86.2779 | 91.3825 | 91.3185 | 91.2546 | 91.1907 | 91.1269 | 91.0631 | 90.9993 | 90.9356 | 90.872 | 90.8084 | 90.7448
Smithton | 93004 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 87.4498 | 104.859 | 104.7856 | 104.7123 | 104.639 | 104.5657 | 104.4925 | 104.4194 | 104.3463 | 104.2732 | 104.2002 | 104.1273 | 104.0544
Smithton | 93005 | 96.2182 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 96.7583 | 141.8898 | 139.9469 | 139.8489 | 139.751 | 139.6532 | 139.5554 | 139.4578 | 139.3601 | 139.2626 | 139.1651 | 139.0677 | 138.9703
Smithton | 93006 | 60.2929 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 61.0262 | 58.1731 | 63.9957 | 63.9509 | 63.9061 | 63.8614 | 63.8167 | 63.772 | 63.7274 | 63.6827 | 63.6382 | 63.5936 | 63.5491
Sorell | 41511 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 79.3924 | 104.531 | 110.9078 | 110.7303 | 110.5532 | 110.3763 | 110.1997 | 110.0234 | 109.8473 | 109.6716 | 109.4961 | 109.3209 | 109.146
Sorell | 41512 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 97.5486 | 116.4099 | 126.6526 | 126.4499 | 126.2476 | 126.0456 | 125.8439 | 125.6426 | 125.4415 | 125.2408 | 125.0405 | 124.8404 | 124.6406
Sorell | 41513 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 90.4236 | 132.9607 | 138.7236 | 138.5017 | 138.2801 | 138.0588 | 137.8379 | 137.6174 | 137.3972 | 137.1774 | 136.9579 | 136.7387 | 136.52
Sorell | 41514 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 46.0589 | 124.1091 | 135.2043 | 134.988 | 134.772 | 134.5563 | 134.3411 | 134.1261 | 133.9115 | 133.6972 | 133.4833 | 133.2698 | 133.0565
Sorell | 41515 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 115.7732 | 120.6795 | 122.926 | 122.7293 | 122.533 | 122.3369 | 122.1412 | 121.9458 | 121.7506 | 121.5558 | 121.3613 | 121.1672 | 120.9733
Sorell | 41516 | 125.9783 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 127.7361 | 110.2439 | 113.6018 | 113.42 | 113.2386 | 113.0574 | 112.8765 | 112.6959 | 112.5156 | 112.3355 | 112.1558 | 111.9764 | 111.7972
Sorell | 41517 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 79.9171 | 29.5931 | 31.3359 | 31.2858 | 31.2357 | 31.1857 | 31.1358 | 31.086 | 31.0363 | 30.9866 | 30.937 | 30.8876 | 30.8381
Sorell | 41518 | 92.334 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 92.7986 | 113.0597 | 123.2577 | 123.0605 | 122.8636 | 122.667 | 122.4708 | 122.2748 | 122.0792 | 121.8838 | 121.6888 | 121.4941 | 121.2997
St Leonards | 66101 | 31.3183 | 31.1117 | 30.8224 | 30.5357 | 30.2517 | 29.9704 | 29.6917 | 29.4155 | 29.142 | 28.871 | 28.6025 | 28.3364 | 51.3833 | 53.8184 | 53.6839 | 53.5496 | 53.4158 | 53.2822 | 53.149 | 53.0162 | 52.8836 | 52.7514 | 52.6195 | 52.488
St Leonards | 66102 | 81.875 | 82.5375 | 81.7699 | 81.0095 | 80.2561 | 79.5097 | 78.7703 | 78.0377 | 77.3119 | 76.593 | 75.8806 | 75.1749 | 159.6933 | 170.2562 | 169.8306 | 169.406 | 168.9825 | 168.56 | 168.1386 | 167.7183 | 167.299 | 166.8807 | 166.4635 | 166.0474
St Leonards | 66103 | 86.0983 | 85.2976 | 84.5044 | 83.7185 | 82.9399 | 82.1685 | 81.4044 | 80.6473 | 79.8973 | 79.1543 | 78.4181 | 77.6888 | 162.28 | 168.8326 | 168.4105 | 167.9895 | 167.5695 | 167.1506 | 166.7327 | 166.3159 | 165.9001 | 165.4853 | 165.0716 | 164.6589
St Leonards | 66104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Leonards | 66105 | 50.485 | 50.0155 | 49.5504 | 49.0895 | 48.633 | 48.1807 | 47.7326 | 47.2887 | 46.8489 | 46.4132 | 45.9816 | 45.554 | 89.7917 | 92.8797 | 92.6475 | 92.4159 | 92.1849 | 91.9544 | 91.7245 | 91.4952 | 91.2665 | 91.0383 | 90.8107 | 90.5837
St Leonards | 66106 | 165.925 | 164.3819 | 162.8531 | 161.3386 | 159.8382 | 158.3517 | 156.879 | 155.42 | 153.9746 | 152.5427 | 151.124 | 149.7186 | 145.9989 | 149.1107 | 148.7379 | 148.3661 | 147.9952 | 147.6252 | 147.2561 | 146.888 | 146.5208 | 146.1545 | 145.7891 | 145.4246
St Leonards | 66107 | 61.2767 | 61.9633 | 61.3871 | 60.8162 | 60.2506 | 59.6903 | 59.1352 | 58.5852 | 58.0403 | 57.5006 | 56.9658 | 56.436 | 112.49 | 117.6314 | 117.3373 | 117.044 | 116.7514 | 116.4595 | 116.1684 | 115.8779 | 115.5883 | 115.2993 | 115.011 | 114.7235
St Leonards | 66108 | 2.1117 | 2.092 | 2.0726 | 2.0533 | 2.0342 | 2.0153 | 1.9965 | 1.978 | 1.9596 | 1.9414 | 1.9233 | 1.9054 | 2.7933 | 2.8016 | 2.7946 | 2.7876 | 2.7806 | 2.7737 | 2.7668 | 2.7598 | 2.7529 | 2.7461 | 2.7392 | 2.7323
St Leonards | 66109 | 29.8717 | 29.7316 | 29.4551 | 29.1812 | 28.9098 | 28.6409 | 28.3746 | 28.1107 | 27.8493 | 27.5903 | 27.3337 | 27.0795 | 48.7683 | 49.7962 | 49.6717 | 49.5475 | 49.4236 | 49.3001 | 49.1768 | 49.0539 | 48.9312 | 48.8089 | 48.6869 | 48.5652
St Leonards | 66110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St Marys | 57003 | 23.8611 | 23.7053 | 23.5133 | 23.3228 | 23.1339 | 22.9465 | 22.7606 | 22.5763 | 22.3934 | 22.212 | 22.0321 | 21.8536 | 27.9844 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681 | 28.6681
St Marys | 57004 | 123.2459 | 122.2476 | 121.2574 | 120.2752 | 119.301 | 118.3347 | 117.3761 | 116.4254 | 115.4823 | 114.5469 | 113.6191 | 112.6988 | 143.0167 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136 | 145.5136
St Marys | 57005 | 29.27 | 29.3237 | 29.0862 | 28.8506 | 28.6169 | 28.3851 | 28.1552 | 27.9271 | 27.7009 | 27.4765 | 27.254 | 27.0332 | 30.2344 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642 | 30.6642
St Marys | 57006 | 117.36 | 116.4094 | 115.4665 | 114.5312 | 113.6035 | 112.6833 | 111.7706 | 110.8652 | 109.9672 | 109.0765 | 108.193 | 107.3166 | 192.2822 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043 | 200.9043
Summerleas | 32374 | 129.4889 | 131.0206 | 130.1428 | 129.2708 | 128.4047 | 127.5444 | 126.6898 | 125.841 | 124.9979 | 124.1604 | 123.3285 | 122.5022 | 208.7889 | 227.6612 | 229.8695 | 232.0992 | 234.3506 | 236.6238 | 238.9191 | 241.2366 | 243.5766 | 245.9393 | 248.3249 | 250.7336
Summerleas | 32377 | 117.35 | 116.5638 | 115.7828 | 115.007 | 114.2365 | 113.4711 | 112.7108 | 111.9557 | 111.2056 | 110.4605 | 109.7204 | 108.9853 | 154 | 164.2936 | 165.8872 | 167.4963 | 169.1211 | 170.7615 | 172.4179 | 174.0904 | 175.779 | 177.4841 | 179.2057 | 180.944
Summerleas | 32379 | 150.8167 | 153.444 | 152.4159 | 151.3947 | 150.3804 | 149.3728 | 148.372 | 147.3779 | 146.3905 | 145.4097 | 144.4355 | 143.4677 | 237.6333 | 260.7988 | 263.3286 | 265.8829 | 268.4619 | 271.066 | 273.6954 | 276.3502 | 279.0308 | 281.7374 | 284.4703 | 287.2296
Trevallyn | 61021 | 85.6722 | 85.3467 | 85.0224 | 84.6993 | 84.3774 | 84.0568 | 83.7374 | 83.4192 | 83.1022 | 82.7864 | 82.4718 | 82.1584 | 144.85 | 150.3751 | 149.954 | 149.5342 | 149.1155 | 148.6979 | 148.2816 | 147.8664 | 147.4524 | 147.0395 | 146.6278 | 146.2172
Trevallyn | 61022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61023 | 64.3333 | 64.0889 | 63.8453 | 63.6027 | 63.361 | 63.1202 | 62.8804 | 62.6414 | 62.4034 | 62.1663 | 61.9301 | 61.6947 | 87.9278 | 89.0623 | 88.8129 | 88.5643 | 88.3163 | 88.069 | 87.8224 | 87.5765 | 87.3313 | 87.0868 | 86.8429 | 86.5998
Trevallyn | 61024 | 149.8922 | 149.3226 | 148.7552 | 148.1899 | 147.6268 | 147.0658 | 146.507 | 145.9503 | 145.3956 | 144.8431 | 144.2927 | 143.7444 | 160.0467 | 170.1647 | 169.6883 | 169.2131 | 168.7393 | 168.2669 | 167.7957 | 167.3259 | 166.8574 | 166.3902 | 165.9243 | 165.4597
Trevallyn | 61025 | 92.4556 | 92.1042 | 91.7542 | 91.4056 | 91.0582 | 90.7122 | 90.3675 | 90.0241 | 89.682 | 89.3412 | 89.0017 | 88.6635 | 151.2778 | 155.9796 | 155.5429 | 155.1074 | 154.6731 | 154.24 | 153.8081 | 153.3774 | 152.948 | 152.5197 | 152.0927 | 151.6668
Trevallyn | 61026 | 111.4389 | 112.2517 | 111.8251 | 111.4002 | 110.9768 | 110.5551 | 110.135 | 109.7165 | 109.2996 | 108.8843 | 108.4705 | 108.0583 | 107.2444 | 107.1041 | 106.8042 | 106.5051 | 106.2069 | 105.9095 | 105.613 | 105.3173 | 105.0224 | 104.7283 | 104.4351 | 104.1427
Trevallyn | 61027 | 104.9556 | 105.605 | 105.2037 | 104.8039 | 104.4057 | 104.0089 | 103.6137 | 103.22 | 102.8277 | 102.437 | 102.0477 | 101.6599 | 195.4389 | 198.2196 | 197.6646 | 197.1111 | 196.5592 | 196.0089 | 195.46 | 194.9127 | 194.367 | 193.8228 | 193.2801 | 192.7389
Trevallyn | 61028 | 85.7111 | 85.3854 | 85.0609 | 84.7377 | 84.4157 | 84.0949 | 83.7754 | 83.457 | 83.1399 | 82.8239 | 82.5092 | 82.1957 | 116.4667 | 116.4416 | 116.1156 | 115.7905 | 115.4663 | 115.143 | 114.8206 | 114.4991 | 114.1785 | 113.8588 | 113.54 | 113.2221
Trevallyn | 61029 | 56.6278 | 56.3076 | 55.9887 | 55.6709 | 55.3544 | 55.0391 | 54.725 | 54.4121 | 54.1003 | 53.7898 | 53.4804 | 53.1722 | 79.7944 | 83.0139 | 82.6268 | 82.2407 | 81.8558 | 81.4719 | 81.0891 | 80.7073 | 80.3266 | 79.947 | 79.5685 | 79.191
Trevallyn | 61030 | 0 | 19.644 | 19.5694 | 19.495 | 19.4209 | 19.3471 | 19.2736 | 19.2004 | 19.1274 | 19.0547 | 18.9823 | 18.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | 61037 | 60.4333 | 60.2037 | 59.9749 | 59.747 | 59.52 | 59.2938 | 59.0685 | 58.844 | 58.6204 | 58.3976 | 58.1757 | 57.9547 | 79.9222 | 82.0209 | 81.7912 | 81.5622 | 81.3339 | 81.1061 | 80.879 | 80.6526 | 80.4267 | 80.2015 | 79.977 | 79.753
Trevallyn | 61039 | 144.3042 | 143.7558 | 143.2095 | 142.6653 | 142.1232 | 141.5831 | 141.0451 | 140.5092 | 139.9752 | 139.4433 | 138.9134 | 138.3856 | 151.2025 | 151.7677 | 151.3428 | 150.919 | 150.4964 | 150.075 | 149.6548 | 149.2358 | 148.8179 | 148.4012 | 147.9857 | 147.5714
Trevallyn | 61040 | 141.7944 | 141.2556 | 140.7189 | 140.1841 | 139.6514 | 139.1207 | 138.5921 | 138.0654 | 137.5408 | 137.0181 | 136.4975 | 135.9788 | 172.35 | 172.6835 | 172.2 | 171.7178 | 171.237 | 170.7575 | 170.2794 | 169.8026 | 169.3272 | 168.8531 | 168.3803 | 167.9088
Trevallyn | 61041 | 80.4167 | 80.8843 | 80.5769 | 80.2707 | 79.9657 | 79.6618 | 79.3591 | 79.0576 | 78.7571 | 78.4578 | 78.1597 | 77.8627 | 131.6056 | 137.2806 | 136.8962 | 136.5129 | 136.1307 | 135.7495 | 135.3694 | 134.9904 | 134.6124 | 134.2355 | 133.8596 | 133.4848
Trevallyn | 61043 | 169.4278 | 158.0328 | 157.3903 | 156.7502 | 156.1126 | 155.4773 | 154.8445 | 154.2141 | 153.5861 | 152.9605 | 152.3373 | 151.7164 | 255.8722 | 250.9694 | 250.2125 | 249.4578 | 248.7052 | 247.9547 | 247.2062 | 246.4599 | 245.7157 | 244.9735 | 244.2335 | 243.4955
Triabunna | 43505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80761 | 0.83253 | 0.83819 | 0.84389 | 0.84963 | 0.8554 | 0.86122 | 0.86708 | 0.87297 | 0.87891 | 0.88489 | 0.8909
Triabunna | 43506 | 60.2423 | 61.1399 | 62.0509 | 62.9754 | 63.9138 | 64.8661 | 65.8326 | 66.8135 | 67.809 | 68.8194 | 69.8448 | 70.8855 | 78.2324 | 81.3197 | 81.8727 | 82.4294 | 82.9899 | 83.5543 | 84.1224 | 84.6945 | 85.2704 | 85.8502 | 86.434 | 87.0218
Triabunna | 43507 | 79.7317 | 81.2641 | 82.4749 | 83.7038 | 84.951 | 86.2168 | 87.5014 | 88.8052 | 90.1284 | 91.4713 | 92.8342 | 94.2174 | 89.0152 | 91.8737 | 92.4985 | 93.1274 | 93.7607 | 94.3983 | 95.0402 | 95.6865 | 96.3371 | 96.9922 | 97.6518 | 98.3158
Trial Harbour | 99981 | 25.5056 | 25.9067 | 25.8834 | 25.8601 | 25.8368 | 25.8136 | 25.7904 | 25.7672 | 25.744 | 25.7208 | 25.6976 | 25.6745 | 41.1444 | 44.6103 | 44.5656 | 44.5211 | 44.4766 | 44.4321 | 44.3877 | 44.3433 | 44.2989 | 44.2546 | 44.2104 | 44.1662
Trial Harbour | 99982 | 8.1222 | 8.2071 | 8.1997 | 8.1923 | 8.1849 | 8.1776 | 8.1702 | 8.1629 | 8.1555 | 8.1482 | 8.1408 | 8.1335 | 10.0556 | 10.0455 | 10.0355 | 10.0254 | 10.0154 | 10.0054 | 9.9954 | 9.9854 | 9.9754 | 9.9654 | 9.9555 | 9.9455
Trial Harbour | 99983 | 0.022222 | 0.022202 | 0.022182 | 0.022162 | 0.022142 | 0.022122 | 0.022102 | 0.022083 | 0.022063 | 0.022043 | 0.022023 | 0.022003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | 49303 | 16.2078 | 16.2758 | 16.3442 | 16.4129 | 16.4818 | 16.551 | 16.6205 | 16.6903 | 16.7604 | 16.8308 | 16.9015 | 16.9725 | 15.6067 | 15.7474 | 15.7018 | 15.6562 | 15.6108 | 15.5656 | 15.5204 | 15.4754 | 15.4305 | 15.3858 | 15.3412 | 15.2967
Tungatinah | 49304 | 14.8511 | 14.9135 | 14.9761 | 15.039 | 15.1022 | 15.1656 | 15.2293 | 15.2933 | 15.3575 | 15.422 | 15.4868 | 15.5518 | 11.4017 | 11.3686 | 11.3356 | 11.3027 | 11.27 | 11.2373 | 11.2047 | 11.1722 | 11.1398 | 11.1075 | 11.0753 | 11.0432
Tungatinah | 49307 | 0 | 8.8513 | 8.8885 | 8.9258 | 8.9633 | 9.0009 | 9.0387 | 9.0767 | 9.1148 | 9.1531 | 9.1916 | 9.2302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ulverstone | 82001 | 104.8101 | 104.3909 | 103.9733 | 103.5574 | 103.1432 | 102.7306 | 102.3197 | 101.9104 | 101.5028 | 101.0967 | 100.6924 | 100.2896 | 76.8678 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684 | 77.1684
Ulverstone | 82002 | 81.2351 | 81.1503 | 80.8257 | 80.5024 | 80.1804 | 79.8596 | 79.5402 | 79.222 | 78.9052 | 78.5895 | 78.2752 | 77.9621 | 153.9263 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016 | 159.1016
Ulverstone | 82003 | 96.9719 | 96.8527 | 96.4653 | 96.0794 | 95.6951 | 95.3123 | 94.9311 | 94.5514 | 94.1732 | 93.7965 | 93.4213 | 93.0476 | 160.9934 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896 | 167.6896
Ulverstone | 82004 | 64.8678 | 64.6083 | 64.3499 | 64.0925 | 63.8361 | 63.5808 | 63.3264 | 63.0731 | 62.8208 | 62.5696 | 62.3193 | 62.07 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974 | 46.7974
Ulverstone | 82005 | 85.3502 | 85.0088 | 84.6688 | 84.3301 | 83.9928 | 83.6568 | 83.3222 | 82.9889 | 82.6569 | 82.3263 | 81.997 | 81.669 | 150.1157 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508 | 152.0508
Ulverstone | 82006 | 181.1586 | 180.434 | 179.7122 | 178.9934 | 178.2774 | 177.5643 | 176.854 | 176.1466 | 175.442 | 174.7403 | 174.0413 | 173.3451 | 94.5581 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727 | 94.727
Ulverstone | 82007 | 52.4 | 52.1904 | 51.9816 | 51.7737 | 51.5666 | 51.3603 | 51.1549 | 50.9503 | 50.7465 | 50.5435 | 50.3413 | 50.14 | 22.1583 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144 | 23.0144
Ulverstone | 82008 | 94.0779 | 93.7016 | 93.3268 | 92.9535 | 92.5817 | 92.2113 | 91.8425 | 91.4751 | 91.1092 | 90.7448 | 90.3818 | 90.0203 | 148.7546 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323 | 158.7323
Waddamana | 49202 | 10.6733 | 11.2781 | 11.2623 | 11.2465 | 11.2308 | 11.215 | 11.1994 | 11.1837 | 11.168 | 11.1524 | 11.1368 | 11.1212 | 16.584 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442 | 17.2442
Wayatinah | 49411 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 9.9362 | 12.4424 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891 | 12.7891
Wayatinah | 49412 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 26.1058 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577 | 29.3577
Wesley Vale | 81001 | 0 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 27.6244 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333 | 193.1333
Wesley Vale | 81002 | 0 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 69.061 | 50.4867 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255 | 110.9255
Wesley Vale | 81003 | 0 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 41.4366 | 0 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732 | 82.8732
West Hobart | 13043 | 45.2722 | 46.1341 | 46.54 | 46.9496 | 47.3627 | 47.7795 | 48.2 | 48.6242 | 49.0521 | 49.4837 | 49.9192 | 50.3585 | 78.5444 | 85.0126 | 85.4887 | 85.9674 | 86.4488 | 86.9329 | 87.4197 | 87.9093 | 88.4016 | 88.8966 | 89.3945 | 89.8951
West Hobart | 13044 | 224.7056 | 226.683 | 228.6778 | 230.6901 | 232.7202 | 234.7682 | 236.8341 | 238.9183 | 241.0207 | 243.1417 | 245.2814 | 247.4398 | 224.6833 | 235.1481 | 236.465 | 237.7892 | 239.1208 | 240.4599 | 241.8065 | 243.1606 | 244.5223 | 245.8916 | 247.2686 | 248.6533
West Hobart | 13045 | 144.0056 | 149.4424 | 150.7575 | 152.0842 | 153.4225 | 154.7726 | 156.1346 | 157.5086 | 158.8947 | 160.293 | 161.7035 | 163.1265 | 214.4 | 237.582 | 238.9124 | 240.2503 | 241.5957 | 242.9487 | 244.3092 | 245.6773 | 247.0531 | 248.4366 | 249.8278 | 251.2269
West Hobart | 13046 | 56.4 | 56.8963 | 57.397 | 57.9021 | 58.4116 | 58.9257 | 59.4442 | 59.9673 | 60.495 | 61.0274 | 61.5644 | 62.1062 | 67.1889 | 67.9046 | 68.2849 | 68.6673 | 69.0518 | 69.4385 | 69.8274 | 70.2184 | 70.6116 | 71.0071 | 71.4047 | 71.8046
West Hobart | 13047 | 39.3944 | 39.7411 | 40.0908 | 40.4436 | 40.7995 | 41.1586 | 41.5208 | 41.8862 | 42.2548 | 42.6266 | 43.0017 | 43.3801 | 62.3905 | 68.081 | 68.4622 | 68.8456 | 69.2311 | 69.6188 | 70.0087 | 70.4008 | 70.795 | 71.1915 | 71.5901 | 71.991
West Hobart | 13048 | 0 | 96.6907 | 97.5415 | 98.3999 | 99.2658 | 100.1394 | 101.0206 | 101.9096 | 102.8064 | 103.7111 | 104.6237 | 105.5444 | 148.4889 | 150.2353 | 151.0766 | 151.9226 | 152.7734 | 153.6289 | 154.4893 | 155.3544 | 156.2244 | 157.0992 | 157.979 | 158.8637
West Hobart | 13049 | 86.6611 | 88.9385 | 89.7211 | 90.5107 | 91.3072 | 92.1107 | 92.9212 | 93.7389 | 94.5638 | 95.396 | 96.2355 | 97.0824 | 145.2444 | 157.4559 | 158.3377 | 159.2244 | 160.116 | 161.0127 | 161.9144 | 162.8211 | 163.7329 | 164.6498 | 165.5718 | 166.499
West Hobart | 13050 | 59.5333 | 60.1252 | 60.6543 | 61.1881 | 61.7265 | 62.2697 | 62.8177 | 63.3705 | 63.9282 | 64.4907 | 65.0583 | 65.6308 | 75.25 | 79.9012 | 80.3486 | 80.7986 | 81.2511 | 81.7061 | 82.1636 | 82.6237 | 83.0864 | 83.5517 | 84.0196 | 84.4901
West Hobart | 13052 | 177.8833 | 179.4487 | 181.0279 | 182.6209 | 184.228 | 185.8492 | 187.4846 | 189.1345 | 190.7989 | 192.4779 | 194.1717 | 195.8804 | 221.8 | 235.2074 | 236.5246 | 237.8491 | 239.1811 | 240.5205 | 241.8674 | 243.2218 | 244.5839 | 245.9536 | 247.3309 | 248.7159
West Hobart | 13053 | 89.1056 | 89.8897 | 90.6807 | 91.4787 | 92.2837 | 93.0958 | 93.9151 | 94.7415 | 95.5752 | 96.4163 | 97.2648 | 98.1207 | 135.9 | 137.3981 | 138.1675 | 138.9413 | 139.7193 | 140.5018 | 141.2886 | 142.0798 | 142.8754 | 143.6755 | 144.4801 | 145.2892
West Hobart | 13054 | 105.8611 | 139.942 | 140.8818 | 141.8298 | 142.7862 | 143.751 | 144.7243 | 145.7062 | 146.6967 | 147.6959 | 148.7039 | 149.7208 | 126.1667 | 160.4371 | 161.1499 | 161.8667 | 162.5875 | 163.3124 | 164.0413 | 164.7743 | 165.5114 | 166.2526 | 166.998 | 167.7475
West Hobart | 13055 | 103.0889 | 106.1362 | 107.0702 | 108.0124 | 108.9629 | 109.9218 | 110.8891 | 111.8649 | 112.8493 | 113.8424 | 114.8442 | 115.8548 | 213.2207 | 232.5003 | 233.8023 | 235.1116 | 236.4282 | 237.7522 | 239.0836 | 240.4225 | 241.7689 | 243.1228 | 244.4843 | 245.8534
West Hobart | 13056 | 48.7056 | 49.7643 | 50.2022 | 50.644 | 51.0897 | 51.5393 | 51.9928 | 52.4504 | 52.9119 | 53.3775 | 53.8473 | 54.3211 | 79.0611 | 84.6714 | 85.1456 | 85.6224 | 86.1019 | 86.5841 | 87.0689 | 87.5565 | 88.0468 | 88.5399 | 89.0357 | 89.5343
West Hobart | 13057 | 131.2556 | 135.3732 | 136.5644 | 137.7662 | 138.9786 | 140.2016 | 141.4353 | 142.68 | 143.9356 | 145.2022 | 146.48 | 147.769 | 147.0056 | 154.6837 | 155.5499 | 156.421 | 157.297 | 158.1778 | 159.0636 | 159.9544 | 160.8501 | 161.7509 | 162.6567 | 163.5676
West Hobart | 13058 | 68.7444 | 69.3494 | 69.9597 | 70.5753 | 71.1964 | 71.8229 | 72.4549 | 73.0926 | 73.7358 | 74.3846 | 75.0392 | 75.6996 | 65.1056 | 67.7635 | 68.143 | 68.5246 | 68.9083 | 69.2942 | 69.6822 | 70.0725 | 70.4649 | 70.8595 | 71.2563 | 71.6553

## ForecastData (hidden)
Ref. Connection point forecast data request-TasNetworks-20181203-Updated.xlsx/Rooftop PV sheet, Columns M to O.
|  |  | Summer (MVA) | [13 empty] | Winter (MVA) | [14 empty] | Embedded generation
|  | Non-peaking season | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | PF | Regional DF | 2018 (Actual) | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | PF | Regional DF |  | less than 100 kVA | Over 100 kVA
BEZ | Zs-Bellerive | Summer | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 0.999 |  | 12.53 | 12.39 | 12.25 | 12.11 | 11.98 | 11.84 | 11.7 | 11.57 | 11.44 | 11.3 | 11.17 | 11.04 | 0.9954
| Zs-CambridgeLF | Summer | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 0.999 |  | 8.3 | 8.24 | 8.18 | 8.12 | 8.06 | 8 | 7.94 | 7.89 | 7.83 | 7.77 | 7.72 | 7.66 | 0.9954
| Zs-CambridgeMT | Summer | 5.26 | 5.28 | 5.29 | 5.3 | 5.31 | 5.32 | 5.33 | 5.34 | 5.35 | 5.37 | 5.38 | 5.39 | 0.9995 |  | 6.42 | 6.46 | 6.49 | 6.53 | 6.57 | 6.61 | 6.65 | 6.69 | 6.73 | 6.77 | 6.81 | 6.85 | 0.9966
CLZ | Zs-Claremont | Summer | 12.42 | 12.53 | 12.64 | 12.76 | 12.87 | 12.98 | 13.1 | 13.21 | 13.33 | 13.44 | 13.56 | 13.68 | 0.9904 |  | 19.99 | 20.1 | 20.21 | 20.33 | 20.44 | 20.55 | 20.67 | 20.79 | 20.9 | 21.02 | 21.14 | 21.26 | 0.9827
DPZ | Zs-Derwent Park | Summer | 13.14 | 13.23 | 13.31 | 13.4 | 13.49 | 13.58 | 13.67 | 13.76 | 13.85 | 13.94 | 14.03 | 14.13 | 0.9505 |  | 21.6 | 21.72 | 21.84 | 21.96 | 22.08 | 22.2 | 22.32 | 22.45 | 22.57 | 22.69 | 22.82 | 22.94 | 0.9742
EHZ | Zs-East Hobart | Summer | 20.35 | 28.06 | 28.57 | 28.72 | 28.86 | 29 | 29.15 | 29.29 | 29.44 | 29.59 | 29.74 | 29.89 | 0.9505 |  | 25.12 | 32.65 | 33.16 | 33.31 | 33.46 | 33.61 | 33.76 | 33.91 | 34.07 | 34.22 | 34.38 | 34.53 | 0.9742
GBZ | Zs-Geilston Bay | Summer | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 11.99 | 0.999 |  | 16.94 | 16.76 | 16.59 | 16.41 | 16.24 | 16.07 | 15.9 | 15.73 | 15.56 | 15.4 | 15.23 | 15.07 | 0.9954
GRZ | Zs-Gretna | Winter | 1.46 | 1.45 | 1.45 | 1.44 | 1.44 | 1.43 | 1.43 | 1.42 | 1.42 | 1.41 | 1.41 | 1.4 | 0.9606 |  | 0.55 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.9881
HOZ | Zs-Howrah | Summer | 9.93 | 9.95 | 9.97 | 9.99 | 10.01 | 10.03 | 10.05 | 10.07 | 10.1 | 10.12 | 10.14 | 10.16 | 0.9995 |  | 17.42 | 17.52 | 17.63 | 17.73 | 17.84 | 17.94 | 18.05 | 18.15 | 18.26 | 18.37 | 18.48 | 18.59 | 0.9966
NNZ | Zs-New Norfolk zone | Summer | 5.37 | 5.35 | 5.33 | 5.32 | 5.3 | 5.28 | 5.26 | 5.24 | 5.22 | 5.2 | 5.19 | 5.17 | 0.9606 |  | 7.36 | 7.34 | 7.33 | 7.32 | 7.31 | 7.29 | 7.28 | 7.27 | 7.26 | 7.25 | 7.23 | 7.22 | 0.9881
NTZ | Zs-New Town | Summer | 14.47 | 14.56 | 14.66 | 14.76 | 14.85 | 14.95 | 15.05 | 15.15 | 15.25 | 15.35 | 15.45 | 15.55 | 0.9505 |  | 22.02 | 22.14 | 22.26 | 22.38 | 22.5 | 22.63 | 22.75 | 22.88 | 23 | 23.13 | 23.26 | 23.38 | 0.9742
RIZ | Zs-Richmond | Summer | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 0.9998 |  | 3.36 | 3.36 | 3.35 | 3.35 | 3.34 | 3.34 | 3.33 | 3.33 | 3.32 | 3.32 | 3.31 | 3.31 | 1
RPZ | Zs-Rosny Park | Summer | 10.96 | 10.97 | 10.97 | 10.98 | 10.98 | 10.99 | 10.99 | 10.99 | 11 | 11 | 11.01 | 11.01 | 0.9995 |  | 14.19 | 16.45 | 16.45 | 16.45 | 16.46 | 16.46 | 16.46 | 16.46 | 16.46 | 16.46 | 16.47 | 16.47 | 0.9966
SBZ | Zs-Sandy Bay | Summer | 24.1 | 24.31 | 24.53 | 24.74 | 24.96 | 25.18 | 25.4 | 25.62 | 25.85 | 26.08 | 26.31 | 26.54 | 0.9904 |  | 37.56 | 37.77 | 37.98 | 38.19 | 38.41 | 38.62 | 38.84 | 39.05 | 39.27 | 39.49 | 39.71 | 39.94 | 0.9827
SUZ | Zs-Summerleas | Summer | 7.07 | 7.03 | 6.98 | 6.93 | 6.89 | 6.84 | 6.79 | 6.75 | 6.7 | 6.66 | 6.61 | 6.57 | 0.9994 |  | 10.91 | 11.02 | 11.13 | 11.24 | 11.34 | 11.45 | 11.57 | 11.68 | 11.79 | 11.91 | 12.02 | 12.14 | 0.9965
THZ | Zs-Trial Harbour | Summer | 1.35 | 1.35 | 1.35 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.33 | 0.8543 |  | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.09 | 2.09 | 2.09 | 2.09 | 2.08 | 2.08 | 2.08 | 0.9298
WHZ | Zs-West Hobart | Summer | 21.82 | 22.62 | 22.81 | 23.01 | 23.21 | 23.4 | 23.6 | 23.81 | 24.01 | 24.22 | 24.43 | 24.63 | 0.9904 |  | 34.55 | 35.35 | 35.55 | 35.74 | 35.94 | 36.14 | 36.34 | 36.54 | 36.74 | 36.94 | 37.14 | 37.35 | 0.9827
CAZ | Cambridge-Total | Summer | 10.45 | 10.44 | 10.45 | 10.46 | 10.47 | 10.48 | 10.49 | 10.49 | 10.5 | 10.51 | 10.52 | 10.53 | 0.9761 |  | 14.35 | 14.26 | 14.24 | 14.22 | 14.2 | 14.19 | 14.17 | 14.16 | 14.14 | 14.13 | 14.11 | 14.09 | 0.9906
WYZ | Wayatinah | Winter | 1.3011 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 0.9109 | 0.83633 | 1.231 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 1.1078 | 0.9825 | 0.81282
AL | Arthurs Lake (DL) | Winter | 0.52463 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.56954 | 0.994 | 0.60103 | 0.049853 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.072471 | 0.5044 | 0.91568 | AL | 0 | 1.6
AV | Avoca | Winter | 7.2843 | 8.1112 | 8.0515 | 7.974 | 7.7871 | 7.7747 | 7.7762 | 7.7659 | 7.8824 | 7.9468 | 7.923 | 7.8992 | 0.9505 | 0.25754 | 6.7635 | 6.172 | 6.1465 | 6.1015 | 5.9881 | 5.9741 | 5.9503 | 5.9668 | 6.0201 | 6.083 | 6.0729 | 6.0627 | 0.9842 | 0.55044 | AV | 0.5812 | 5
BW | Bridgewater | Summer | 22.807 | 20.1928 | 19.8497 | 19.4709 | 18.8939 | 18.6993 | 18.5517 | 18.3842 | 18.5182 | 18.5268 | 18.5268 | 18.5268 | 0.9967 | 0.7349 | 33.7351 | 31.3092 | 30.9703 | 30.5356 | 29.764 | 29.491 | 29.1706 | 29.048 | 29.1023 | 29.1992 | 28.9505 | 28.7038 | 0.9977 | 0.5045 | BW | 5.0568 | 0
BU | Burnie | Summer | 41.3372 | 42.4649 | 41.7092 | 41.0582 | 39.921 | 39.3581 | 38.8646 | 38.3117 | 38.3774 | 38.1772 | 38.1772 | 38.1772 | 0.9692 | 0.93533 | 59.6283 | 57.1598 | 56.1069 | 55.1415 | 53.7989 | 53.1818 | 52.5215 | 52.2573 | 52.3493 | 52.5545 | 52.5545 | 52.5545 | 0.9945 | 0.99006 | BU | 7.5227 | 2.1353
CS | Chapel Street | Summer | 24.9778 | 24.2019 | 24.2251 | 24.2035 | 23.9033 | 23.9761 | 24.1278 | 24.2654 | 24.8115 | 25.2006 | 25.385 | 25.5708 | 0.9993 | 0.7053 | 40.0583 | 40.1729 | 40.1989 | 40.2447 | 39.9682 | 40.1886 | 40.343 | 40.7729 | 41.461 | 42.2242 | 42.4844 | 42.7462 | 0.9987 | 0.89349 | CS | 3.8869 | 1.69
CR | Creek Road | Summer | 57.5256 | 55.5878 | 55.623 | 55.5555 | 54.8499 | 55.0035 | 55.3416 | 55.649 | 56.8942 | 57.7791 | 58.2878 | 58.8009 | 0.9904 | 0.81109 | 87.1018 | 96.481 | 96.4467 | 96.4632 | 95.7252 | 96.2092 | 96.5539 | 97.5695 | 99.2027 | 101.0173 | 101.5848 | 102.1554 | 0.9827 | 0.99459 | CR | 7.2582 | 1.065
DE | Derby | Winter | 6.985 | 6.3564 | 6.3054 | 6.2405 | 6.0903 | 6.0765 | 6.0736 | 6.0615 | 6.1484 | 6.1945 | 6.1718 | 6.1491 | 0.9602 | 0.60146 | 3.4361 | 3.053 | 3.039 | 3.0154 | 2.9583 | 2.9508 | 2.9386 | 2.9466 | 2.9727 | 3.0036 | 2.9978 | 2.992 | 0.9685 | 0.37248 | DE | 0.62678 | 2.02
DB | Derwent Bridge | Summer | 0.35558 | 0.26174 | 0.25981 | 0.25731 | 0.25128 | 0.25088 | 0.25093 | 0.2506 | 0.25436 | 0.25644 | 0.25566 | 0.2549 | 0.9997 | 0.61628 | 0.42825 | 0.28709 | 0.28607 | 0.28422 | 0.27929 | 0.2791 | 0.27858 | 0.28008 | 0.28345 | 0.28744 | 0.28747 | 0.2875 | 0.9961 | 0 | DB | 0 | 0
DP | Devonport | Summer | 40.8436 | 32.2292 | 31.5206 | 30.9361 | 30.4136 | 29.9845 | 29.6511 | 29.4084 | 29.2294 | 29.088 | 29.088 | 29.088 | 0.9728 | 0.89414 | 58.2683 | 51.3107 | 50.7883 | 50.2679 | 49.7623 | 49.2856 | 48.826 | 48.3773 | 47.9286 | 47.4815 | 47.0211 | 46.5651 | 0.9922 | 0.85714 | DP | 5.2688 | 0.76689
EL | Electrona | Summer | 11.0782 | 9.7038 | 9.7925 | 9.8368 | 9.7361 | 9.7493 | 9.7558 | 9.721 | 9.8161 | 9.8155 | 9.8145 | 9.8135 | 0.9939 | 0.74268 | 15.9784 | 14.1907 | 14.09 | 13.9969 | 13.7931 | 13.7617 | 13.7076 | 13.7464 | 13.8701 | 14.0159 | 13.9931 | 13.9703 | 0.9955 | 0.89497 | EL | 4.3506 | 0.2298
EB | Emu Bay (RT) | Summer | 7.5018 | 8.02 | 7.9312 | 7.8257 | 7.6167 | 7.5861 | 7.5766 | 7.5602 | 7.669 | 7.7272 | 7.6867 | 7.6463 | 0.8935 | 0.6292 | 9.3323 | 9.4618 | 9.4135 | 9.3357 | 9.155 | 9.1294 | 9.0904 | 9.1142 | 9.1942 | 9.289 | 9.2684 | 9.2479 | 0.9528 | 0.90321 | EB | 0.39744 | 0
GT | George Town | Summer | 11.8947 | 13.1691 | 13.1523 | 13.1097 | 12.9088 | 12.8907 | 12.8953 | 12.88 | 13.075 | 13.1836 | 13.1485 | 13.1135 | 0.9809 | 0.95096 | 18.9815 | 18.7182 | 18.5854 | 18.4625 | 18.1938 | 18.1524 | 18.0811 | 18.1322 | 18.2953 | 18.4877 | 18.4576 | 18.4275 | 1 | 0.95151 | GT | 3.8522 | 0
| Gordon | Summer | 0.27247 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.31255 | 0.998 | 0.89129 | 0.41076 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.38459 | 0.9991 | 0.82088 | GO | 0 | 0
HA | Hadspen | Summer | 36.2176 | 40.4642 | 40.159 | 39.7789 | 38.9471 | 38.7331 | 38.6522 | 38.5512 | 39.0945 | 39.3806 | 39.4736 | 39.5669 | 0.9945 | 0.83984 | 53.4481 | 55.7424 | 55.3018 | 54.8924 | 54.0577 | 53.9137 | 53.6892 | 53.834 | 54.3112 | 54.876 | 54.7617 | 54.6476 | 0.9966 | 0.92938 | HA | 7.2165 | 0.4498
HR | Huon River | Summer | 1.7995 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 1.7234 | 0.853 | 0.81189 | 1.8642 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 1.7461 | 0.8735 | 0.40561 | HR | 0 | 0
KE | Kermandie | Summer | 4.9752 | 4.8323 | 4.8261 | 4.8105 | 4.7367 | 4.7301 | 4.7318 | 4.7262 | 4.7977 | 4.8376 | 4.8247 | 4.8118 | 0.9867 | 0.84888 | 7.0841 | 6.7404 | 6.7126 | 6.6634 | 6.5396 | 6.5244 | 6.4983 | 6.5163 | 6.5746 | 6.6433 | 6.6322 | 6.6211 | 0.9859 | 0.85406 | KE | 1.5525 | 0
KI11 | Kingston 11kV | Summer | 17.6007 | 14.995 | 14.8319 | 14.6418 | 14.2912 | 14.1806 | 14.1319 | 14.0838 | 14.2741 | 14.3708 | 14.2486 | 14.1274 | 1 | 0.74377 | 23.4109 | 27.187 | 26.7443 | 26.3092 | 25.6601 | 25.3249 | 24.9324 | 24.6885 | 24.5685 | 24.4558 | 24.4558 | 24.4558 | 0.9991 | 0.99028 | KI11 | 3.8754 | 0.30004
KI33 | Kingston 33kV | Summer | 7.0859 | 6.618 | 6.5668 | 6.5044 | 6.3681 | 6.3329 | 6.3196 | 6.303 | 6.3918 | 6.4385 | 6.3952 | 6.3523 | 0.9994 | 0.791 | 11.8949 | 11.8215 | 11.9045 | 11.9485 | 11.8579 | 11.9665 | 12.0574 | 12.2317 | 12.4832 | 12.7577 | 12.8815 | 13.0066 | 0.9965 | 0.94974 | KI33 | 1.4112 | 0
KR | Knights Road | Summer | 15.8717 | 14.9203 | 14.995 | 15.044 | 14.9164 | 15.0107 | 15.1437 | 15.2614 | 15.6345 | 15.9094 | 15.9895 | 16.07 | 0.9525 | 0.83927 | 19.0854 | 18.5798 | 18.4215 | 18.2735 | 17.9817 | 17.915 | 17.8189 | 17.8435 | 17.978 | 18.1408 | 18.0852 | 18.0298 | 0.9852 | 1 | KR | 3.772 | 0
LF | Lindisfarne | Summer | 22.9907 | 21.5798 | 21.3507 | 21.0822 | 20.5719 | 20.3789 | 20.2456 | 20.0958 | 20.2785 | 20.3256 | 20.3256 | 20.3256 | 0.999 | 0.78068 | 36.2695 | 38.3081 | 37.8103 | 37.3376 | 36.5812 | 36.2976 | 35.9627 | 35.8768 | 36.0111 | 36.201 | 35.9413 | 35.6834 | 0.9954 | 0.97481 | LF | 3.7019 | 0.1
MB | Meadowbank | Winter | 7.1421 | 8.8027 | 9.0127 | 9.1942 | 9.2356 | 9.471 | 9.7163 | 9.9391 | 10.3198 | 10.6294 | 10.8829 | 11.1425 | 0.9371 | 0.70588 | 6.0687 | 4.8981 | 4.9184 | 4.9226 | 4.8705 | 4.8986 | 4.9182 | 4.9712 | 5.0553 | 5.1482 | 5.1812 | 5.2145 | 0.9886 | 0.4194 | MB | 0.391 | 0.2
MT | Mornington | Summer | 27.725 | 28.5418 | 28.5676 | 28.5408 | 28.1868 | 28.2759 | 28.4615 | 28.6325 | 29.2867 | 29.7558 | 29.8184 | 29.8811 | 0.9995 | 0.69517 | 38.9974 | 41.4647 | 41.5936 | 41.5904 | 41.1211 | 41.3412 | 41.4997 | 41.9454 | 42.6566 | 43.4459 | 43.7043 | 43.9642 | 0.9966 | 0.95035 | MT | 4.5985 | 0
MY | Mowbray | Summer | 21.3137 | 22.5903 | 22.1 | 21.7183 | 21.176 | 21.0525 | 21.0832 | 21.1868 | 21.7331 | 22.229 | 22.358 | 22.4876 | 0.9662 | 0.84445 | 36.7831 | 41.1566 | 40.9295 | 40.5744 | 39.7752 | 39.6595 | 39.4919 | 39.5959 | 39.9444 | 40.3571 | 40.2606 | 40.1643 | 0.9893 | 0.97772 | MY | 3.006 | 2.2
NN | New Norfolk | Summer | 17.8863 | 12.9693 | 12.8623 | 12.727 | 12.4189 | 12.3918 | 12.3899 | 12.371 | 12.5549 | 12.6557 | 12.6109 | 12.5662 | 0.9606 | 0.68554 | 18.11 | 16.9013 | 16.8315 | 16.7082 | 16.3977 | 16.3595 | 16.2943 | 16.3394 | 16.4854 | 16.6578 | 16.6299 | 16.6021 | 0.9881 | 0.85838 | NN | 2.355 | 0.56
NT | Newton (Henty Goldmine) | Summer | 3.3412 | 3.6892 | 3.662 | 3.6267 | 3.5418 | 3.5361 | 3.5368 | 3.5321 | 3.5851 | 3.6144 | 3.6035 | 3.5927 | 0.9938 | 0.79884 | 3.7849 | 3.6526 | 3.6375 | 3.6108 | 3.5437 | 3.5355 | 3.5214 | 3.5311 | 3.5627 | 3.5999 | 3.5939 | 3.5879 | 0.9993 | 0.78302 | NT | 0 | 0
NH | North Hobart | Summer | 23.2799 | 21.9681 | 22.4522 | 22.4597 | 22.2072 | 22.2983 | 22.4601 | 22.6072 | 23.1346 | 23.516 | 23.4502 | 23.3846 | 0.9725 | 0.8015 | 35.9681 | 35.4243 | 35.9054 | 35.865 | 35.4321 | 35.6106 | 35.746 | 36.1352 | 36.7533 | 37.4397 | 37.6942 | 37.9504 | 0.977 | 0.98736 | NH | 2.5519 | 0
NW | Norwood | Summer | 16.7192 | 17.3697 | 17.2176 | 17.0337 | 16.6589 | 16.5538 | 16.5112 | 16.4634 | 16.692 | 16.8108 | 16.7242 | 16.638 | 0.9975 | 0.81347 | 27.1692 | 27.703 | 27.5359 | 27.2832 | 26.7346 | 26.6478 | 26.528 | 26.5977 | 26.8316 | 27.1088 | 27.0362 | 26.9638 | 0.9986 | 0.90791 | NW | 3.7749 | 0.58708
PM | Palmerston | Winter | 9.8118 | 9.4276 | 9.3581 | 9.268 | 9.0509 | 9.0364 | 9.0381 | 9.0261 | 9.1616 | 9.2365 | 9.2088 | 9.1811 | 0.9314 | 0.70314 | 4.517 | 3.998 | 3.9815 | 3.9524 | 3.8789 | 3.8699 | 3.8544 | 3.8651 | 3.8997 | 3.9404 | 3.9338 | 3.9273 | 0.9955 | 0.78172 | PM | 0.52636 | 0
PL | Port Latta (RT) | Winter | 7.0988 | 7.4923 | 7.4371 | 7.3655 | 7.1929 | 7.1814 | 7.1828 | 7.1732 | 7.2809 | 7.3404 | 7.3184 | 7.2964 | 0.9175 | 0.70614 | 4.1146 | 4.2084 | 4.191 | 4.1603 | 4.083 | 4.0735 | 4.0572 | 4.0685 | 4.1048 | 4.1477 | 4.1408 | 4.1339 | 0.9953 | 0.87782 | PL | 0.6376 | 0.225
QT | Queenstown | Summer | 4.2777 | 4.1059 | 4.1096 | 4.1018 | 4.0398 | 4.0301 | 4.0217 | 4.0012 | 4.0393 | 4.0437 | 4.0267 | 4.0099 | 0.9951 | 0.84249 | 5.6262 | 5.2819 | 5.2445 | 5.2098 | 5.134 | 5.1223 | 5.1022 | 5.1166 | 5.1626 | 5.2169 | 5.2084 | 5.1999 | 0.9992 | 0.91865 | QT | 0.47965 | 0
RA | Railton | Summer | 47.6664 | 49.6263 | 49.6619 | 49.5995 | 48.9364 | 48.9651 | 49.0794 | 49.1181 | 49.9602 | 50.474 | 50.4396 | 50.4051 | 0.9364 | 0.98511 | 48.2201 | 51.5036 | 51.2553 | 51.0106 | 50.3706 | 50.3398 | 50.1966 | 50.3611 | 50.7996 | 51.2817 | 51.259 | 51.2364 | 0.9742 | 0.9514 | RA | 5.4357 | 3.005
RI | Risdon 33kV | Summer | 47.8226 | 58.1168 | 58.8087 | 58.8652 | 58.223 | 58.4399 | 58.799 | 59.0928 | 60.3687 | 61.2588 | 61.6633 | 62.0704 | 0.9505 | 0.83099 | 70.2166 | 80.2304 | 80.8887 | 80.7781 | 79.7673 | 80.1017 | 80.3203 | 81.0967 | 82.3849 | 83.8217 | 84.2812 | 84.7432 | 0.9742 | 0.94845 | RI | 3.0945 | 0
RK | Rokeby | Summer | 16.0583 | 11.113 | 10.9779 | 10.8721 | 10.6726 | 10.6346 | 10.6381 | 10.6254 | 10.7861 | 10.8756 | 10.8068 | 10.7384 | 0.9987 | 0.64309 | 21.8391 | 19.6465 | 19.5653 | 19.4221 | 19.0611 | 19.0167 | 18.9409 | 18.9933 | 19.1631 | 19.3634 | 19.3311 | 19.2987 | 0.9983 | 0.85946 | RK | 3.3856 | 0
RB22 | Rosebery 22kV | Summer | 1.7876 | 2.3117 | 2.2945 | 2.2747 | 2.2396 | 2.2364 | 2.2371 | 2.2344 | 2.2682 | 2.287 | 2.2839 | 2.2809 | 0.8683 | 0.66031 | 2.6734 | 3.0902 | 3.0683 | 3.048 | 3.0037 | 2.9968 | 2.985 | 2.9935 | 3.0204 | 3.0522 | 3.0475 | 3.0427 | 0.948 | 0.94738 | RB22 | 0 | 0
RB44 | Rosebery 44kV | Winter | 16.6565 | 33.8323 | 33.6676 | 33.4775 | 33.1422 | 33.1112 | 33.1181 | 33.0923 | 33.4159 | 33.5958 | 33.5663 | 33.5369 | 0.8543 | 0.88367 | 16.3001 | 31.3841 | 31.2377 | 31.1023 | 30.8061 | 30.7605 | 30.6819 | 30.7382 | 30.918 | 31.1301 | 31.0984 | 31.0669 | 0.9298 | 0.98888 | RB44 | 0.28285 | 0
SR | Savage River DL | Summer | 0.6949 | 0.70704 | 0.70613 | 0.70383 | 0.69304 | 0.69207 | 0.69231 | 0.69148 | 0.70195 | 0.70778 | 0.70589 | 0.704 | 1 | 0.76872 | 1.2828 | 1.2508 | 1.2456 | 1.2365 | 1.2135 | 1.2107 | 1.2058 | 1.2092 | 1.22 | 1.2327 | 1.2307 | 1.2286 | 0.9999 | 0.82261 | SR | 0.10927 | 0
SD | Scottsdale | Summer | 10.3534 | 11.7817 | 11.6516 | 11.4964 | 11.1852 | 11.1254 | 11.0857 | 11.0292 | 11.1523 | 11.2007 | 11.3 | 11.4001 | 0.9629 | 0.87342 | 11.2992 | 12.7398 | 12.5177 | 12.3041 | 11.996 | 11.84 | 11.6653 | 11.5698 | 11.5442 | 11.5345 | 11.5345 | 11.5345 | 0.9952 | 0.96449 | SD | 2.4685 | 0
ST | Smithton | Winter | 20.9918 | 24.0776 | 23.322 | 22.5555 | 21.6477 | 21.0626 | 20.5216 | 19.9534 | 19.7051 | 19.3138 | 19.3138 | 19.3138 | 0.9323 | 0.80269 | 20.3218 | 24.8733 | 24.7541 | 24.557 | 24.0876 | 24.0239 | 23.9236 | 23.9873 | 24.199 | 24.4497 | 24.4337 | 24.4177 | 0.9719 | 0.87959 | ST | 1.7015 | 0.825
SO | Sorell | Summer | 25.6095 | 19.493 | 19.3257 | 19.1213 | 18.6915 | 18.5359 | 18.4205 | 18.2813 | 18.4408 | 18.4758 | 18.4758 | 18.4758 | 0.9998 | 0.79597 | 33.284 | 31.0316 | 30.8114 | 30.6077 | 30.1622 | 30.0936 | 29.9753 | 30.06 | 30.3305 | 30.6494 | 30.5995 | 30.5497 | 1 | 0.87334 | SO | 6.178 | 0
SL | St Leonards | Summer | 18.1923 | 14.1884 | 14.0248 | 13.8358 | 13.495 | 13.3804 | 13.3236 | 13.267 | 13.4347 | 13.5139 | 13.3889 | 13.265 | 0.9954 | 0.84329 | 28.7196 | 27.6765 | 27.5217 | 27.2809 | 26.742 | 26.6608 | 26.5434 | 26.6105 | 26.842 | 27.1169 | 27.0494 | 26.982 | 0.9978 | 0.95408 | SL | 2.8082 | 0
SM | St Marys | Summer | 10.9361 | 9.9194 | 9.7874 | 9.635 | 9.3548 | 9.2913 | 9.2506 | 9.1996 | 9.2998 | 9.3379 | 9.2626 | 9.1879 | 0.9927 | 0.93022 | 15.5825 | 12.4823 | 12.3059 | 12.0918 | 11.7455 | 11.5967 | 11.4296 | 11.34 | 11.3191 | 11.3138 | 11.3138 | 11.3138 | 0.9894 | 0.62287 | SM | 2.8842 | 0
TR | Trevallyn | Summer | 38.4303 | 35.5358 | 35.2277 | 34.8544 | 34.09 | 33.8769 | 33.7909 | 33.6937 | 34.1619 | 34.4057 | 34.2743 | 34.1434 | 0.9984 | 0.78742 | 65.6323 | 64.7757 | 64.1852 | 63.6339 | 62.6038 | 62.4002 | 62.1187 | 62.2738 | 62.8134 | 63.4554 | 63.28 | 63.1051 | 0.9983 | 0.97409 | TR | 10.0376 | 2.5
TB | Triabunna (RT) | Winter | 7.9684 | 5.7957 | 5.8573 | 5.9041 | 5.8672 | 5.9605 | 6.0659 | 6.1628 | 6.3623 | 6.5221 | 6.6191 | 6.7176 | 0.971 | 0 | 6.8388 | 7.0468 | 7.0784 | 7.0868 | 7.0142 | 7.0569 | 7.0875 | 7.1661 | 7.2896 | 7.4259 | 7.476 | 7.5265 | 0.9978 | 0.79273 | TB | 1.2688 | 0
TU | Tungatinah | Summer | 0.90258 | 0.74669 | 0.74939 | 0.7521 | 0.75494 | 0.75809 | 0.76158 | 0.76527 | 0.76904 | 0.77282 | 0.7761 | 0.77939 | 0.9735 | 0.49749 | 0.90427 | 1.101 | 1.0955 | 1.0906 | 1.0864 | 1.083 | 1.0804 | 1.0788 | 1.0781 | 1.0783 | 1.0752 | 1.0721 | 0.978 | 0.3929 | TU | 0.03491 | 0
UL | Ulverstone | Summer | 22.1067 | 20.9293 | 20.7541 | 20.5333 | 20.0317 | 19.9793 | 19.9626 | 19.9158 | 20.194 | 20.3381 | 20.2564 | 20.1749 | 0.9782 | 0.95321 | 32.4622 | 27.3626 | 26.808 | 26.1734 | 25.2568 | 24.7687 | 24.2425 | 23.8809 | 23.6618 | 23.4722 | 23.4722 | 23.4722 | 0.9955 | 0.84008 | UL | 5.2517 | 8.805
WA | Waddamana | Summer | 0.47748 | 0.34433 | 0.34359 | 0.34287 | 0.34221 | 0.34174 | 0.34146 | 0.3413 | 0.34118 | 0.34107 | 0.3406 | 0.34013 | 0.9884 | 0 | 0.73039 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.58277 | 0.9975 | 0.56808 | WA | 0.14125 | 0
WV | Wesley Vale | Summer | 0.068435 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 8.8623 | 0.8863 | 0.11482 | 10.5244 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 12.0753 | 0.9999 | 0.95585 | WV | 1.9107 | 0.265
[31 empty] | WY | 0.00152 | 0